## Assumptions
FDRE Bid Financial Model — Assumptions
NHPC FDRE Tranche-II · 200 MW · Rajasthan portfolio · All cells in BLUE are inputs; YELLOW cells are the solver levers.
LEGEND & HOW TO USE
Blue text = hardcoded input · Black = formula · Green = link to another sheet · Yellow fill = key lever.
To re-derive the bid tariff after changing any assumption: Data ▸ What-If Analysis ▸ Goal Seek —
set 'Financial Model'!C68 (Equity IRR) to 0.14 by changing Assumptions!C11 (Bid tariff).
Then verify 'Financial Model'!C70 Min DSCR ≥ 1.10 (if it binds instead, Goal Seek on C70).
A. OPTIMIZED BID CONFIGURATION (optimizer output — engine run, seed 42)
Solar capacity (AC) | 288.8 | MW | Optimizer result
Wind capacity | 40.9 | MW | Optimizer result
BESS power | 180 | MW | Optimizer result
BESS energy | 540 | MWh | Optimizer result
Contracted (bid) capacity | 200 | MW | Selected bid capacity
Bid tariff (levelized) | 5.9113 | Rs/kWh | REQUIRED TARIFF at declared-value delivery (CUF 40%, availability 90%): lowest tariff meeting IRR & DSCR targets — re-derive via Goal Seek (see legend)
B. TENDER RULES (NHPC FDRE Tranche-II RfS)
Declared annual CUF | 40% |  | RfS: bid declaration, min 40%
Annual CUF lower tolerance | 15% |  | RfS: -15% on declared CUF
Annual CUF upper multiplier | 1.1 | x | RfS: NHPC offtake capped at +10%
PPA offtake target (x declared CUF) | 1 | x | SCENARIO LEVER: 1.00 = deliver at declared CUF (this case); 1.10 = deliver at the +10% offtake cap (gives Rs 5.58)
Hours per year (CUF convention) | 8766 | h | RfS LD illustration uses 8,766 h
Peak availability floor (monthly) | 90% |  | RfS: 90% of contracted capacity in peak hours
Peak hours per day | 4 | h | 2 morning (05-10) + 2 evening (18-23), buyer-scheduled
Liquidated damages multiplier | 1.5 | x tariff | Applies to monthly-peak and annual-CUF shortfall
PSM charge | 0.02 | Rs/kWh | Netted from tariff in revenue
PPA term | 25 | years
C. RESOURCE & DELIVERED YIELD
Solar net CUF (P50, base) | 27.5% |  | PVsyst — TOPCon bifacial, 1.5 DC/AC
Wind net CUF (P50, base) | 34% |  | Project configuration; measured Bikaner data
Measured-yield calibration factor | 1.1911 | x | Calibrates synthetic base CUFs to the measured-trace optimizer run that produced the bid (engine seed 42). Change only with new yield studies.
Delivery efficiency to POI | 90% |  | BESS cycling losses + spill in firming the peak blocks
Solar degradation | 0.5% | /yr
Wind degradation | 0.2% | /yr
Merchant capture of surplus | 60% |  | Curtailment haircut and solar-hour price factor on surplus sales
D. CAPEX UNIT RATES (Rs cr)
Solar EPC | 3.1 | cr/MWac | Project configuration
Wind EPC | 6.5 | cr/MW
BESS energy | 1.1 | cr/MWh
BESS PCS | 0.3 | cr/MW
Land & development — lump sum | 90 | cr | Project configuration
Land — solar | 0.45 | cr/MWac
Land — wind | 0.08 | cr/MW
Land — BESS | 0.02 | cr/MWh
Transmission — lump sum | 180 | cr | Project configuration
Transmission — per MW (evacuation basis) | 1 | cr/MW
Interconnection limit (3 nodes) | 280 | MW | Fatehgarh 30 + Bikaner III 150 + Bikaner II 100
Owner's costs — lump sum | 60 | cr
Owner's costs — per MW (all assets) | 0.12 | cr/MW
Success charge | 1 | lakh/MW +18% GST | On contracted capacity
Processing fee (100–250 MW slab) | 10 | lakh +18% GST | RfS slab
Contingency | 3% | of base capex
E. O&M AND OTHER OPEX
Solar O&M | 5.5 | lakh/MW/yr
Wind O&M | 11 | lakh/MW/yr
BESS O&M | 1.2 | lakh/MWh/yr
Admin — fixed | 5 | cr/yr
Admin — per MW (all assets) | 0.75 | lakh/MW/yr
Transmission O&M (evacuation basis) | 2 | lakh/MW/yr
Insurance | 0.35% | of hard capex/yr
O&M escalation | 3.5% | /yr
Transmission loss | 0.5% | of PPA revenue
F. FINANCING
Debt fraction | 75% | of project cost
Interest rate (long-term debt) | 8.75% | /yr
Debt tenor | 18 | years | Sculpted repayment (constant DSCR)
Sculpting DSCR constant | 1.4782 | x | Sets debt service = CFADS / this constant. Re-solve by Goal Seek: Capex!G31 (closing debt yr-18) to 0 by changing this cell.
Construction period | 24 | months
Drawdown — year 1 | 45%
Drawdown — year 2 | 55%
Target equity IRR | 14% |  | Bid solve criterion
Minimum DSCR floor | 1.1 | x | Bid solve criterion
Equity discount rate (NPV) | 10%
Receivable days | 60 | days | Working capital
Working-capital interest rate | 9.5% | /yr
G. TAX & DEPRECIATION
Corporate tax rate (Sec 115BAA) | 25.17% |  | Incl. surcharge & cess
Tax WDV depreciation rate | 40% | /yr | On eligible block
Eligible block fraction | 95% | of project cost | Balance on straight line
Book depreciation life | 25 | years | SLM
Residual value | 5%
H. BESS AUGMENTATION & MERCHANT
Augmentation year | 11 |  | Full energy replacement per BESS spec
Energy replacement fraction | 100%
Augmentation cost | 0.75 | cr/MWh | Future cell price
Merchant price — year 1 | 3.25 | Rs/kWh
Merchant escalation | 2% | /yr
Sources: RFS.pdf, PROJECT CONFIGURATION_FDRE 2.docx, project_config_fdre2.json, engine fdre_enterprise_engine.py (v1.x, seed 42).

## Capex
Capex Build-Up & Financing (Rs cr)
Component | Rs cr | Basis | IDC schedule
Solar EPC | 895.28 | Solar MW x EPC rate | Month | Debt drawn (cum) | Interest
Wind EPC | 265.85 | Wind MW x EPC rate | 1 | 76.0952 | 0.53378
BESS energy | 594 | MWh x rate | 2 | 152.1905 | 1.0676
BESS PCS | 54 | MW x rate | 3 | 228.2857 | 1.6013
Land & development | 234.032 | Lump + per-asset land | 4 | 304.3809 | 2.1351
Transmission & connectivity | 460 | Lump + evacuation MW x rate | 5 | 380.4761 | 2.6689
Owner's costs | 121.164 | Lump + all-asset MW x rate | 6 | 456.5714 | 3.2027
Success charge | 2.36 | Contracted MW x 1 lakh x GST | 7 | 532.6666 | 3.7364
Processing fee | 0.118 | Slab fee x GST | 8 | 608.7618 | 4.2702
Base capex | 2626.804 |  | 9 | 684.8571 | 4.804
Contingency | 78.8041 |  | 10 | 760.9523 | 5.3378
HARD CAPEX | 2705.6081 |  | 11 | 837.0475 | 5.8716
Evacuation basis (MW) | 280 | min(max(contracted, RE MW, BESS MW), interconnection) | 12 | 913.1427 | 6.4053
|  |  | 13 | 1006.148 | 7.0577
Monthly interest rate | 0.7015% |  | 14 | 1099.1533 | 7.7101
Debt base for IDC (hard x debt%) | 2029.2061 |  | 15 | 1192.1586 | 8.3625
IDC (capitalized) | 169.3857 |  | 16 | 1285.1639 | 9.0149
TOTAL PROJECT COST | 2874.9938 |  | 17 | 1378.1691 | 9.6673
Debt | 2156.2454 |  | 18 | 1471.1744 | 10.3197
Equity | 718.7485 |  | 19 | 1564.1797 | 10.9721
|  |  | 20 | 1657.185 | 11.6245
EMD (capped Rs 10 cr) | 10 | Rs 9.28/12.64/14.64 lakh per MW (solar/wind/ESS) | 21 | 1750.1903 | 12.2769
PBG | 145.806 | Rs 23.20/31.60/36.60 lakh per MW | 22 | 1843.1955 | 12.9293
|  |  | 23 | 1936.2008 | 13.5817
BESS augmentation capex (year 11) | 405 |  | 24 | 2029.2061 | 14.2341
|  |  | CHECK: debt fully repaid by yr-18 (closing balance, cr) | 0
Goal Seek this to 0 by changing Assumptions sculpting DSCR if assumptions change.

## Dispatch 25Y
25-Year Dispatch & Annual Compliance (MWh)
PPA cap =
Year | Solar gen | Wind gen | RE total | Delivered at POI | PPA target | PPA energy | Annual CUF | Surplus | Merchant sold | CUF floor ok | CUF cap ok | Spill
1 | 829267.9623 | 145200.205 | 974468.1673 | 877021.3506 | 701280 | 701280 | 40% | 175741.3506 | 105444.8104 | PASS | PASS | 70296.5402
2 | 825121.6225 | 144909.8046 | 970031.4271 | 873028.2844 | 701280 | 701280 | 40% | 171748.2844 | 103048.9706 | PASS | PASS | 68699.3138
3 | 820996.0144 | 144619.985 | 965615.9994 | 869054.3995 | 701280 | 701280 | 40% | 167774.3995 | 100664.6397 | PASS | PASS | 67109.7598
4 | 816891.0343 | 144330.745 | 961221.7794 | 865099.6014 | 701280 | 701280 | 40% | 163819.6014 | 98291.7609 | PASS | PASS | 65527.8406
5 | 812806.5791 | 144042.0836 | 956848.6627 | 861163.7964 | 701280 | 701280 | 40% | 159883.7964 | 95930.2779 | PASS | PASS | 63953.5186
6 | 808742.5462 | 143753.9994 | 952496.5456 | 857246.8911 | 701280 | 701280 | 40% | 155966.8911 | 93580.1346 | PASS | PASS | 62386.7564
7 | 804698.8335 | 143466.4914 | 948165.3249 | 853348.7924 | 701280 | 701280 | 40% | 152068.7924 | 91241.2755 | PASS | PASS | 60827.517
8 | 800675.3394 | 143179.5584 | 943854.8978 | 849469.408 | 701280 | 701280 | 40% | 148189.408 | 88913.6448 | PASS | PASS | 59275.7632
9 | 796671.9627 | 142893.1993 | 939565.1619 | 845608.6457 | 701280 | 701280 | 40% | 144328.6457 | 86597.1874 | PASS | PASS | 57731.4583
10 | 792688.6028 | 142607.4129 | 935296.0157 | 841766.4142 | 701280 | 701280 | 40% | 140486.4142 | 84291.8485 | PASS | PASS | 56194.5657
11 | 788725.1598 | 142322.1981 | 931047.3579 | 837942.6221 | 701280 | 701280 | 40% | 136662.6221 | 81997.5733 | PASS | PASS | 54665.0488
12 | 784781.534 | 142037.5537 | 926819.0877 | 834137.1789 | 701280 | 701280 | 40% | 132857.1789 | 79714.3074 | PASS | PASS | 53142.8716
13 | 780857.6264 | 141753.4786 | 922611.1049 | 830349.9944 | 701280 | 701280 | 40% | 129069.9944 | 77441.9967 | PASS | PASS | 51627.9978
14 | 776953.3382 | 141469.9716 | 918423.3098 | 826580.9788 | 701280 | 701280 | 40% | 125300.9788 | 75180.5873 | PASS | PASS | 50120.3915
15 | 773068.5715 | 141187.0317 | 914255.6032 | 822830.0429 | 701280 | 701280 | 40% | 121550.0429 | 72930.0257 | PASS | PASS | 48620.0172
16 | 769203.2287 | 140904.6576 | 910107.8863 | 819097.0976 | 701280 | 701280 | 40% | 117817.0976 | 70690.2586 | PASS | PASS | 47126.8391
17 | 765357.2125 | 140622.8483 | 905980.0608 | 815382.0547 | 701280 | 701280 | 40% | 114102.0547 | 68461.2328 | PASS | PASS | 45640.8219
18 | 761530.4265 | 140341.6026 | 901872.0291 | 811684.8262 | 701280 | 701280 | 40% | 110404.8262 | 66242.8957 | PASS | PASS | 44161.9305
19 | 757722.7743 | 140060.9194 | 897783.6937 | 808005.3243 | 701280 | 701280 | 40% | 106725.3243 | 64035.1946 | PASS | PASS | 42690.1297
20 | 753934.1605 | 139780.7975 | 893714.958 | 804343.4622 | 701280 | 701280 | 40% | 103063.4622 | 61838.0773 | PASS | PASS | 41225.3849
21 | 750164.4897 | 139501.2359 | 889665.7256 | 800699.1531 | 701280 | 701280 | 40% | 99419.1531 | 59651.4918 | PASS | PASS | 39767.6612
22 | 746413.6672 | 139222.2335 | 885635.9007 | 797072.3106 | 701280 | 701280 | 40% | 95792.3106 | 57475.3864 | PASS | PASS | 38316.9242
23 | 742681.5989 | 138943.789 | 881625.3879 | 793462.8491 | 701280 | 701280 | 40% | 92182.8491 | 55309.7095 | PASS | PASS | 36873.1396
24 | 738968.1909 | 138665.9014 | 877634.0923 | 789870.6831 | 701280 | 701280 | 40% | 88590.6831 | 53154.4099 | PASS | PASS | 35436.2732
25 | 735273.3499 | 138388.5696 | 873661.9196 | 786295.7276 | 701280 | 701280 | 40% | 85015.7276 | 51009.4366 | PASS | PASS | 34006.291
Scenario: PPA delivery held at the DECLARED CUF (40%) in all 25 years — inside the -15%/+10% band throughout. Surplus RE above the target is sold merchant at the capture factor. Set the offtake lever to 1.10 to model delivery at the +10% cap.

## Monthly Y1
Year-1 Monthly Dispatch & Peak Compliance
Month | Days | Peak hours | Peak obligation MWh | Availability % | Peak delivered MWh | Floor (90%) MWh | Shortfall MWh | LD Rs cr | Compliant | PPA energy MWh | Monthly CUF
Jan | 31 | 124 | 24800 | 90% | 22320 | 22320 | 0 | 0 | PASS | 59560.7671 | 40.03%
Feb | 28 | 112 | 22400 | 90% | 20160 | 20160 | 0 | 0 | PASS | 53796.8219 | 40.03%
Mar | 31 | 124 | 24800 | 90% | 22320 | 22320 | 0 | 0 | PASS | 59560.7671 | 40.03%
Apr | 30 | 120 | 24000 | 90% | 21600 | 21600 | 0 | 0 | PASS | 57639.4521 | 40.03%
May | 31 | 124 | 24800 | 90% | 22320 | 22320 | 0 | 0 | PASS | 59560.7671 | 40.03%
Jun | 30 | 120 | 24000 | 90% | 21600 | 21600 | 0 | 0 | PASS | 57639.4521 | 40.03%
Jul | 31 | 124 | 24800 | 90% | 22320 | 22320 | 0 | 0 | PASS | 59560.7671 | 40.03%
Aug | 31 | 124 | 24800 | 90% | 22320 | 22320 | 0 | 0 | PASS | 59560.7671 | 40.03%
Sep | 30 | 120 | 24000 | 90% | 21600 | 21600 | 0 | 0 | PASS | 57639.4521 | 40.03%
Oct | 31 | 124 | 24800 | 90% | 22320 | 22320 | 0 | 0 | PASS | 59560.7671 | 40.03%
Nov | 30 | 120 | 24000 | 90% | 21600 | 21600 | 0 | 0 | PASS | 57639.4521 | 40.03%
Dec | 31 | 124 | 24800 | 90% | 22320 | 22320 | 0 | 0 | PASS | 59560.7671 | 40.03%
TOTAL / MIN | 365 |  | 292000 | 90% |  |  | 0 | 0 | ALL PASS | 701280
Scenario: availability held at the 90% RfS floor in every month (blue inputs) — exactly compliant, zero liquidated damages. Replace with monthly dispatch output when re-running the engine.

## Financial Model
25-Year Financial Model (Rs cr unless noted)
Year | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
ENERGY
PPA energy (MWh) | 701280 | 701280 | 701280 | 701280 | 701280 | 701280 | 701280 | 701280 | 701280 | 701280 | 701280 | 701280 | 701280 | 701280 | 701280 | 701280 | 701280 | 701280 | 701280 | 701280 | 701280 | 701280 | 701280 | 701280 | 701280
Merchant energy (MWh) | 105444.8104 | 103048.9706 | 100664.6397 | 98291.7609 | 95930.2779 | 93580.1346 | 91241.2755 | 88913.6448 | 86597.1874 | 84291.8485 | 81997.5733 | 79714.3074 | 77441.9967 | 75180.5873 | 72930.0257 | 70690.2586 | 68461.2328 | 66242.8957 | 64035.1946 | 61838.0773 | 59651.4918 | 57475.3864 | 55309.7095 | 53154.4099 | 51009.4366
REVENUE
Net PPA tariff (Rs/kWh, tariff - PSM) | 5.8913 | 5.8913 | 5.8913 | 5.8913 | 5.8913 | 5.8913 | 5.8913 | 5.8913 | 5.8913 | 5.8913 | 5.8913 | 5.8913 | 5.8913 | 5.8913 | 5.8913 | 5.8913 | 5.8913 | 5.8913 | 5.8913 | 5.8913 | 5.8913 | 5.8913 | 5.8913 | 5.8913 | 5.8913
PPA revenue | 413.1451 | 413.1451 | 413.1451 | 413.1451 | 413.1451 | 413.1451 | 413.1451 | 413.1451 | 413.1451 | 413.1451 | 413.1451 | 413.1451 | 413.1451 | 413.1451 | 413.1451 | 413.1451 | 413.1451 | 413.1451 | 413.1451 | 413.1451 | 413.1451 | 413.1451 | 413.1451 | 413.1451 | 413.1451
Merchant price (Rs/kWh) | 3.25 | 3.315 | 3.3813 | 3.4489 | 3.5179 | 3.5883 | 3.66 | 3.7332 | 3.8079 | 3.8841 | 3.9617 | 4.041 | 4.1218 | 4.2042 | 4.2883 | 4.3741 | 4.4616 | 4.5508 | 4.6418 | 4.7346 | 4.8293 | 4.9259 | 5.0244 | 5.1249 | 5.2274
Merchant revenue | 34.2696 | 34.1607 | 34.0377 | 33.9001 | 33.7474 | 33.579 | 33.3946 | 33.1935 | 32.9753 | 32.7394 | 32.4852 | 32.2123 | 31.9199 | 31.6076 | 31.2746 | 30.9204 | 30.5443 | 30.1457 | 29.7239 | 29.2781 | 28.8077 | 28.3119 | 27.79 | 27.2412 | 26.6648
Total revenue | 447.4146 | 447.3058 | 447.1828 | 447.0452 | 446.8924 | 446.7241 | 446.5396 | 446.3386 | 446.1204 | 445.8845 | 445.6303 | 445.3574 | 445.065 | 444.7527 | 444.4197 | 444.0655 | 443.6894 | 443.2908 | 442.8689 | 442.4232 | 441.9528 | 441.457 | 440.9351 | 440.3863 | 439.8099
OPERATING EXPENSES
Generation + BESS O&M (escalated) | 26.863 | 27.8032 | 28.7763 | 29.7835 | 30.8259 | 31.9048 | 33.0215 | 34.1772 | 35.3734 | 36.6115 | 37.8929 | 39.2192 | 40.5918 | 42.0126 | 43.483 | 45.0049 | 46.5801 | 48.2104 | 49.8977 | 51.6442 | 53.4517 | 55.3225 | 57.2588 | 59.2629 | 61.3371
Admin (escalated) | 8.8227 | 9.1315 | 9.4512 | 9.7819 | 10.1243 | 10.4787 | 10.8454 | 11.225 | 11.6179 | 12.0245 | 12.4454 | 12.8809 | 13.3318 | 13.7984 | 14.2813 | 14.7812 | 15.2985 | 15.834 | 16.3882 | 16.9617 | 17.5554 | 18.1698 | 18.8058 | 19.464 | 20.1452
Transmission O&M (escalated) | 5.6 | 5.796 | 5.9989 | 6.2088 | 6.4261 | 6.651 | 6.8838 | 7.1248 | 7.3741 | 7.6322 | 7.8994 | 8.1758 | 8.462 | 8.7582 | 9.0647 | 9.382 | 9.7103 | 10.0502 | 10.4019 | 10.766 | 11.1428 | 11.5328 | 11.9365 | 12.3542 | 12.7866
Insurance (on hard capex) | 9.4696 | 9.4696 | 9.4696 | 9.4696 | 9.4696 | 9.4696 | 9.4696 | 9.4696 | 9.4696 | 9.4696 | 9.4696 | 9.4696 | 9.4696 | 9.4696 | 9.4696 | 9.4696 | 9.4696 | 9.4696 | 9.4696 | 9.4696 | 9.4696 | 9.4696 | 9.4696 | 9.4696 | 9.4696
Working-capital interest | 6.987 | 6.9853 | 6.9834 | 6.9813 | 6.9789 | 6.9762 | 6.9734 | 6.9702 | 6.9668 | 6.9631 | 6.9592 | 6.9549 | 6.9503 | 6.9455 | 6.9403 | 6.9347 | 6.9288 | 6.9226 | 6.916 | 6.9091 | 6.9017 | 6.894 | 6.8858 | 6.8773 | 6.8683
Transmission losses (on PPA revenue) | 2.0657 | 2.0657 | 2.0657 | 2.0657 | 2.0657 | 2.0657 | 2.0657 | 2.0657 | 2.0657 | 2.0657 | 2.0657 | 2.0657 | 2.0657 | 2.0657 | 2.0657 | 2.0657 | 2.0657 | 2.0657 | 2.0657 | 2.0657 | 2.0657 | 2.0657 | 2.0657 | 2.0657 | 2.0657
Total opex | 59.8081 | 61.2514 | 62.7451 | 64.2909 | 65.8906 | 67.5461 | 69.2594 | 71.0326 | 72.8676 | 74.7667 | 76.7321 | 78.7662 | 80.8713 | 83.0499 | 85.3046 | 87.6381 | 90.0531 | 92.5525 | 95.1392 | 97.8163 | 100.587 | 103.4545 | 106.4222 | 109.4937 | 112.6725
EBITDA | 387.6065 | 386.0544 | 384.4377 | 382.7543 | 381.0019 | 379.178 | 377.2802 | 375.306 | 373.2528 | 371.1177 | 368.8982 | 366.5912 | 364.1937 | 361.7028 | 359.1151 | 356.4274 | 353.6363 | 350.7383 | 347.7297 | 344.6068 | 341.3657 | 338.0025 | 334.5128 | 330.8926 | 327.1373
TAX COMPUTATION (Sec 115BAA, WDV + loss carry-forward)
WDV block — opening | 2731.2441 | 1638.7465 | 983.2479 | 589.9487 | 353.9692 | 212.3815 | 127.4289 | 76.4574 | 45.8744 | 27.5246 | 16.5148 | 240.7589 | 144.4553 | 86.6732 | 52.0039 | 31.2023 | 18.7214 | 11.2328 | 6.7397 | 4.0438 | 2.4263 | 1.4558 | 0.87347 | 0.52408 | 0.31445
Addition (augmentation x eligible) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 384.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WDV depreciation (40%) | 1092.4977 | 655.4986 | 393.2992 | 235.9795 | 141.5877 | 84.9526 | 50.9716 | 30.5829 | 18.3498 | 11.0099 | 160.5059 | 96.3035 | 57.7821 | 34.6693 | 20.8016 | 12.4809 | 7.4886 | 4.4931 | 2.6959 | 1.6175 | 0.97052 | 0.58231 | 0.34939 | 0.20963 | 0.12578
WDV block — closing | 1638.7465 | 983.2479 | 589.9487 | 353.9692 | 212.3815 | 127.4289 | 76.4574 | 45.8744 | 27.5246 | 16.5148 | 240.7589 | 144.4553 | 86.6732 | 52.0039 | 31.2023 | 18.7214 | 11.2328 | 6.7397 | 4.0438 | 2.4263 | 1.4558 | 0.87347 | 0.52408 | 0.31445 | 0.18867
SLM on non-eligible 5% | 5.75 | 5.75 | 5.75 | 5.75 | 5.75 | 5.75 | 5.75 | 5.75 | 5.75 | 5.75 | 5.75 | 5.75 | 5.75 | 5.75 | 5.75 | 5.75 | 5.75 | 5.75 | 5.75 | 5.75 | 5.75 | 5.75 | 5.75 | 5.75 | 5.75
Total tax depreciation | 1098.2476 | 661.2486 | 399.0491 | 241.7295 | 147.3377 | 90.7026 | 56.7216 | 36.3329 | 24.0998 | 16.7598 | 166.2559 | 102.0535 | 63.5321 | 40.4193 | 26.5516 | 18.2309 | 13.2386 | 10.2431 | 8.4459 | 7.3675 | 6.7205 | 6.3323 | 6.0994 | 5.9596 | 5.8758
Taxable income (EBITDA - interest - tax dep) | -899.3126 | -461.7843 | -194.6754 | -32.0375 | 68.1167 | 130.9966 | 171.7468 | 199.4744 | 219.6656 | 235.6365 | 95.5026 | 169.8619 | 219.4041 | 254.4765 | 278.6863 | 296.7136 | 311.9662 | 325.8648 | 339.2839 | 337.2393 | 334.6452 | 331.6702 | 328.4135 | 324.933 | 321.2616
Loss brought forward | 0 | 899.3126 | 1361.0969 | 1555.7723 | 1587.8097 | 1519.6931 | 1388.6965 | 1216.9496 | 1017.4753 | 797.8097 | 562.1732 | 466.6706 | 296.8087 | 77.4046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taxable after loss set-off | -899.3126 | -1361.0969 | -1555.7723 | -1587.8097 | -1519.6931 | -1388.6965 | -1216.9496 | -1017.4753 | -797.8097 | -562.1732 | -466.6706 | -296.8087 | -77.4046 | 177.0719 | 278.6863 | 296.7136 | 311.9662 | 325.8648 | 339.2839 | 337.2393 | 334.6452 | 331.6702 | 328.4135 | 324.933 | 321.2616
Tax payable | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.5655 | 70.1398 | 74.6769 | 78.5157 | 82.0136 | 85.391 | 84.8764 | 84.2235 | 83.4747 | 82.6551 | 81.7791 | 80.8551
Loss carried forward | 899.3126 | 1361.0969 | 1555.7723 | 1587.8097 | 1519.6931 | 1388.6965 | 1216.9496 | 1017.4753 | 797.8097 | 562.1732 | 466.6706 | 296.8087 | 77.4046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PROFIT & LOSS
Book depreciation (SLM to 5% residual) | 109.2498 | 109.2498 | 109.2498 | 109.2498 | 109.2498 | 109.2498 | 109.2498 | 109.2498 | 109.2498 | 109.2498 | 134.8998 | 134.8998 | 134.8998 | 134.8998 | 134.8998 | 134.8998 | 134.8998 | 134.8998 | 134.8998 | 134.8998 | 134.8998 | 134.8998 | 134.8998 | 134.8998 | 134.8998
EBIT | 278.3568 | 276.8046 | 275.188 | 273.5046 | 271.7521 | 269.9282 | 268.0304 | 266.0562 | 264.003 | 261.868 | 233.9984 | 231.6914 | 229.294 | 226.803 | 224.2153 | 221.5276 | 218.7366 | 215.8385 | 212.83 | 209.7071 | 206.466 | 203.1027 | 199.6131 | 195.9928 | 192.2376
Interest on term debt | 188.6715 | 186.5901 | 180.064 | 173.0623 | 165.5475 | 157.4788 | 148.8118 | 139.4987 | 129.4874 | 118.7214 | 107.1397 | 94.6757 | 81.2575 | 66.807 | 53.8772 | 41.4829 | 28.4315 | 14.6304 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Profit before tax | 89.6853 | 90.2145 | 95.124 | 100.4423 | 106.2046 | 112.4494 | 119.2186 | 126.5575 | 134.5156 | 143.1465 | 126.8587 | 137.0157 | 148.0364 | 159.996 | 170.3381 | 180.0447 | 190.305 | 201.2081 | 212.83 | 209.7071 | 206.466 | 203.1027 | 199.6131 | 195.9928 | 192.2376
PAT | 89.6853 | 90.2145 | 95.124 | 100.4423 | 106.2046 | 112.4494 | 119.2186 | 126.5575 | 134.5156 | 143.1465 | 126.8587 | 137.0157 | 148.0364 | 115.4306 | 100.1983 | 105.3679 | 111.7893 | 119.1945 | 127.439 | 124.8307 | 122.2425 | 119.628 | 116.958 | 114.2137 | 111.3824
DEBT SCHEDULE (sculpted, constant DSCR)
Debt — opening | 2156.2454 | 2132.4585 | 2057.8738 | 1977.855 | 1891.9717 | 1799.7575 | 1700.7067 | 1594.271 | 1479.8558 | 1356.8164 | 1224.4534 | 1082.0082 | 928.6575 | 763.5084 | 615.7398 | 474.0905 | 324.932 | 167.2048 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Interest | 188.6715 | 186.5901 | 180.064 | 173.0623 | 165.5475 | 157.4788 | 148.8118 | 139.4987 | 129.4874 | 118.7214 | 107.1397 | 94.6757 | 81.2575 | 66.807 | 53.8772 | 41.4829 | 28.4315 | 14.6304 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sculpted debt service target (CFADS/DSCR) | 212.4584 | 261.1748 | 260.0827 | 258.9456 | 257.7617 | 256.5296 | 255.2476 | 253.9139 | 252.5268 | 251.0844 | 249.5849 | 248.0264 | 246.4067 | 214.5756 | 195.5265 | 190.6414 | 186.1588 | 181.8344 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Principal repayment | 23.7869 | 74.5847 | 80.0188 | 85.8833 | 92.2142 | 99.0508 | 106.4357 | 114.4152 | 123.0394 | 132.363 | 142.4453 | 153.3507 | 165.1491 | 147.7686 | 141.6493 | 149.1585 | 157.7272 | 167.2048 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Debt service | 212.4584 | 261.1748 | 260.0827 | 258.9456 | 257.7617 | 256.5296 | 255.2476 | 253.9139 | 252.5268 | 251.0844 | 249.5849 | 248.0264 | 246.4067 | 214.5756 | 195.5265 | 190.6414 | 186.1588 | 181.8352 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Debt — closing | 2132.4585 | 2057.8738 | 1977.855 | 1891.9717 | 1799.7575 | 1700.7067 | 1594.271 | 1479.8558 | 1356.8164 | 1224.4534 | 1082.0082 | 928.6575 | 763.5084 | 615.7398 | 474.0905 | 324.932 | 167.2048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CASH FLOW
Receivables (60 days) / change in WC | 73.5476 | 73.5297 | 73.5095 | 73.4869 | 73.4618 | 73.4341 | 73.4038 | 73.3707 | 73.3349 | 73.2961 | 73.2543 | 73.2094 | 73.1614 | 73.11 | 73.0553 | 72.9971 | 72.9352 | 72.8697 | 72.8004 | 72.7271 | 72.6498 | 72.5683 | 72.4825 | 72.3923 | 72.2975
CFADS (EBITDA - tax - change in WC) | 314.0589 | 386.0723 | 384.458 | 382.777 | 381.027 | 379.2057 | 377.3105 | 375.3391 | 373.2886 | 371.1565 | 368.94 | 366.636 | 364.2418 | 317.1886 | 289.0301 | 281.8088 | 275.1825 | 268.7902 | 262.4081 | 259.8037 | 257.2196 | 254.6092 | 251.9435 | 249.2037 | 246.377
BESS augmentation capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FCFE (CFADS - debt service - augmentation) | 101.6006 | 124.8975 | 124.3752 | 123.8314 | 123.2653 | 122.676 | 122.063 | 121.4252 | 120.7618 | 120.0721 | -285.645 | 118.6097 | 117.8351 | 102.6131 | 93.5035 | 91.1674 | 89.0237 | 86.955 | 262.4081 | 259.8037 | 257.2196 | 254.6092 | 251.9435 | 249.2037 | 246.377
DSCR (x) | 1.4782 | 1.4782 | 1.4782 | 1.4782 | 1.4782 | 1.4782 | 1.4782 | 1.4782 | 1.4782 | 1.4782 | 1.4782 | 1.4782 | 1.4782 | 1.4782 | 1.4782 | 1.4782 | 1.4782 | 1.4782
Post-augmentation DSCR (x) | 1.4782 | 1.4782 | 1.4782 | 1.4782 | 1.4782 | 1.4782 | 1.4782 | 1.4782 | 1.4782 | 1.4782 | -0.14448 | 1.4782 | 1.4782 | 1.4782 | 1.4782 | 1.4782 | 1.4782 | 1.4782
EQUITY & PROJECT CASH FLOWS (t0, t1 = construction years)
Equity cash flow | -323.4368 | -395.3117 | 101.6006 | 124.8975 | 124.3752 | 123.8314 | 123.2653 | 122.676 | 122.063 | 121.4252 | 120.7618 | 120.0721 | -285.645 | 118.6097 | 117.8351 | 102.6131 | 93.5035 | 91.1674 | 89.0237 | 86.955 | 262.4081 | 259.8037 | 257.2196 | 254.6092 | 251.9435 | 249.2037 | 246.377
Project cash flow | -1293.7472 | -1581.2466 | 314.0589 | 386.0723 | 384.458 | 382.777 | 381.027 | 379.2057 | 377.3105 | 375.3391 | 373.2886 | 371.1565 | -36.06 | 366.636 | 364.2418 | 317.1886 | 289.0301 | 281.8088 | 275.1825 | 268.7902 | 262.4081 | 259.8037 | 257.2196 | 254.6092 | 251.9435 | 249.2037 | 246.377
RESULTS
Bid tariff (Rs/kWh) | 5.9113
Project IRR (pre-financing, post-tax) | 10.1%
EQUITY IRR | 14%
Equity NPV @ discount rate | 257.397
Min DSCR (debt years) | 1.4782
Average DSCR (debt years) | 1.4782
IRR target met (>= 14%)? | PASS
DSCR floor met (>= 1.10x)? | PASS
Bid tariff is the LOWEST tariff meeting both -> re-derive with Goal Seek (see Assumptions legend).

## Tender Compliance
Hard Tender Conditions & Optimized Output Validation
HARD TENDER CONDITIONS (NHPC FDRE T-II) | Model value | Requirement | Status | Reference
Monthly peak availability — minimum month (year 1) | 90% | 90% | PASS | RfS: 90% of contracted capacity across 4 daily peak hours, tested monthly
All 12 months compliant (year 1) | ALL PASS | "ALL PASS" | PASS | Both peak and annual LDs can apply in the same year
Annual CUF — minimum year | 40% | 0.34 | PASS | Floor: declared CUF - 15% (34%)
Annual CUF — maximum year (offtake cap) | 40% | 0.44 | PASS | Cap: 110% of declared CUF (44%) — NHPC purchase limit
Liquidated damages — total (year 1) | 0 | 0 | PASS | 1.5x tariff on shortfall energy
Bid capacity >= minimum project size | 200 | 50 MW | PASS | RfS minimum 50 MW
Bid capacity multiple of 10 MW | 0 | 0 | PASS
Bid capacity <= bidder cap | 200 | 600 MW | PASS | RfS maximum 600 MW per bidder
BESS charging source | "RE only" | "RE only" | "PASS" | By construction: BESS charges only from co-located RE (no grid/fossil)
Declared CUF >= 40% | 40% | 40% | PASS | RfS minimum declaration
OPTIMIZED OUTPUT VALIDATION (model vs optimizer result) | Optimizer | This model | Match
Solar capacity (MW) | 288.8 | 288.8 | MATCH
Wind capacity (MW) | 40.9 | 40.9 | MATCH
BESS power (MW) | 180 | 180 | MATCH
BESS energy (MWh) | 540 | 540 | MATCH
Selected bid capacity (MW) | 200 | 200 | MATCH
Required tariff (Rs/kWh) — declared CUF 40% / 90% availability | 5.9113 | 5.9113 | MATCH
Equity IRR at bid tariff | 14% | 14% | MATCH
Min DSCR at bid tariff (>= floor) | 1.1 | 1.4782 | PASS

## Validation
Validation — Excel formulas vs dispatch engine (calibrated reference run)
Engine: fdre_enterprise_engine.py, seed 42, capacities as bid, delivery at declared CUF 40% / availability 90% (compliant, zero LD), tariff Rs 5.9113.
Metric | Engine | This model | Delta % | Status
Hard capex (cr) | 2705.6081 | 2705.6081 | 0% | PASS
IDC (cr) | 169.3857 | 169.3857 | -1.33e-07% | PASS
Total project cost (cr) | 2874.9938 | 2874.9938 | -7.838e-09% | PASS
Debt (cr) | 2156.2454 | 2156.2454 | 1.535e-08% | PASS
Equity (cr) | 718.7485 | 718.7485 | 6.173e-08% | PASS
EMD (cr) | 10 | 10 | 0% | PASS
PBG (cr) | 145.806 | 145.806 | 0% | PASS
Year-1 PPA energy (MWh) | 701280 | 701280 | 0% | PASS
Year-1 merchant energy (MWh) | 105444.8104 | 105444.8104 | -2.438e-10% | PASS
Year-1 total revenue (cr) | 447.4146 | 447.4146 | -5.151e-08% | PASS
Year-1 total opex (cr) | 59.8081 | 59.8081 | 2.504e-07% | PASS
Year-1 EBITDA (cr) | 387.6065 | 387.6065 | -9.81e-08% | PASS
Year-1 CFADS (cr) | 314.0589 | 314.0589 | -1.305e-08% | PASS
Year-1 FCFE (cr) | 101.6005 | 101.6006 | 1.86e-05% | PASS
Year-14 tax (first tax-paying year, cr) | 44.5655 | 44.5655 | -0.000148% | PASS
Year-11 augmentation (cr) | 405 | 405 | 0% | PASS
Year-25 EBITDA (cr) | 327.1373 | 327.1373 | 2.552e-08% | PASS
Equity IRR | 14% | 14% | -9.999e-05% | PASS
Project IRR | 10.1% | 10.1% | -0.0004305% | PASS
Min DSCR (x) | 1.4782 | 1.4782 | -0.0004277% | PASS
Equity NPV @10% (cr) | 257.3969 | 257.397 | 1.736e-05% | PASS
PASS = within 0.5%. Engine values are hardcoded reference outputs from the calibrated run; model values are live formulas.

## Profiles 8760
Hourly capacity-factor profiles (engine seed 42, measured-yield calibrated x1.1911, mean-preserving clip). Values.
Hour | Month | Day | HourOfDay | PeakFlag | SolarCF | WindCF | RemPeakOblMWh
1 | 1 | 1 | 0 | 0 | 0 | 0.20912 | 292000
2 | 1 | 1 | 1 | 0 | 0 | 0.25758 | 292000
3 | 1 | 1 | 2 | 0 | 0 | 0.2741 | 292000
4 | 1 | 1 | 3 | 0 | 0 | 0.36883 | 292000
5 | 1 | 1 | 4 | 0 | 0 | 0.29228 | 292000
6 | 1 | 1 | 5 | 0 | 0 | 0.1936 | 292000
7 | 1 | 1 | 6 | 0 | 0 | 0.15759 | 292000
8 | 1 | 1 | 7 | 1 | 0.06852 | 0.20751 | 291800
9 | 1 | 1 | 8 | 1 | 0.3592 | 0.34747 | 291600
10 | 1 | 1 | 9 | 0 | 0.69059 | 0.29144 | 291600
11 | 1 | 1 | 10 | 0 | 0.9839 | 0.30514 | 291600
12 | 1 | 1 | 11 | 0 | 1 | 0.30696 | 291600
13 | 1 | 1 | 12 | 0 | 1 | 0.49278 | 291600
14 | 1 | 1 | 13 | 0 | 1 | 0.50808 | 291600
15 | 1 | 1 | 14 | 0 | 0.9839 | 0.48747 | 291600
16 | 1 | 1 | 15 | 0 | 0.69059 | 0.42084 | 291600
17 | 1 | 1 | 16 | 0 | 0.3592 | 0.49704 | 291600
18 | 1 | 1 | 17 | 0 | 0.06852 | 0.33241 | 291600
19 | 1 | 1 | 18 | 0 | 0 | 0.2532 | 291600
20 | 1 | 1 | 19 | 1 | 0 | 0.31906 | 291400
21 | 1 | 1 | 20 | 1 | 0 | 0.20144 | 291200
22 | 1 | 1 | 21 | 0 | 0 | 0.16257 | 291200
23 | 1 | 1 | 22 | 0 | 0 | 0.092644 | 291200
24 | 1 | 1 | 23 | 0 | 0 | 0.063263 | 291200
25 | 1 | 2 | 0 | 0 | 0 | 0.073818 | 291200
26 | 1 | 2 | 1 | 0 | 0 | 0.059784 | 291200
27 | 1 | 2 | 2 | 0 | 0 | 0.052314 | 291200
28 | 1 | 2 | 3 | 0 | 0 | 0.053166 | 291200
29 | 1 | 2 | 4 | 0 | 0 | 0.060345 | 291200
30 | 1 | 2 | 5 | 0 | 0 | 0.062616 | 291200
31 | 1 | 2 | 6 | 0 | 0 | 0.10278 | 291200
32 | 1 | 2 | 7 | 1 | 0.063687 | 0.10952 | 291000
33 | 1 | 2 | 8 | 1 | 0.33386 | 0.077773 | 290800
34 | 1 | 2 | 9 | 0 | 0.64188 | 0.049638 | 290800
35 | 1 | 2 | 10 | 0 | 0.9145 | 0.076102 | 290800
36 | 1 | 2 | 11 | 0 | 1 | 0.080285 | 290800
37 | 1 | 2 | 12 | 0 | 1 | 0.10496 | 290800
38 | 1 | 2 | 13 | 0 | 1 | 0.12122 | 290800
39 | 1 | 2 | 14 | 0 | 0.9145 | 0.11806 | 290800
40 | 1 | 2 | 15 | 0 | 0.64188 | 0.10212 | 290800
41 | 1 | 2 | 16 | 0 | 0.33386 | 0.12391 | 290800
42 | 1 | 2 | 17 | 0 | 0.063687 | 0.11653 | 290800
43 | 1 | 2 | 18 | 0 | 0 | 0.14041 | 290800
44 | 1 | 2 | 19 | 1 | 0 | 0.11957 | 290600
45 | 1 | 2 | 20 | 1 | 0 | 0.1327 | 290400
46 | 1 | 2 | 21 | 0 | 0 | 0.13877 | 290400
47 | 1 | 2 | 22 | 0 | 0 | 0.12178 | 290400
48 | 1 | 2 | 23 | 0 | 0 | 0.098675 | 290400
49 | 1 | 3 | 0 | 0 | 0 | 0.081514 | 290400
50 | 1 | 3 | 1 | 0 | 0 | 0.08203 | 290400
51 | 1 | 3 | 2 | 0 | 0 | 0.10307 | 290400
52 | 1 | 3 | 3 | 0 | 0 | 0.081672 | 290400
53 | 1 | 3 | 4 | 0 | 0 | 0.10234 | 290400
54 | 1 | 3 | 5 | 0 | 0 | 0.099462 | 290400
55 | 1 | 3 | 6 | 0 | 0 | 0.092949 | 290400
56 | 1 | 3 | 7 | 1 | 0.073744 | 0.15113 | 290200
57 | 1 | 3 | 8 | 1 | 0.38658 | 0.10248 | 290000
58 | 1 | 3 | 9 | 0 | 0.74324 | 0.10133 | 290000
59 | 1 | 3 | 10 | 0 | 1 | 0.088836 | 290000
60 | 1 | 3 | 11 | 0 | 1 | 0.13721 | 290000
61 | 1 | 3 | 12 | 0 | 1 | 0.13067 | 290000
62 | 1 | 3 | 13 | 0 | 1 | 0.1828 | 290000
63 | 1 | 3 | 14 | 0 | 1 | 0.15624 | 290000
64 | 1 | 3 | 15 | 0 | 0.74324 | 0.10882 | 290000
65 | 1 | 3 | 16 | 0 | 0.38658 | 0.075816 | 290000
66 | 1 | 3 | 17 | 0 | 0.073744 | 0.057936 | 290000
67 | 1 | 3 | 18 | 0 | 0 | 0.055017 | 290000
68 | 1 | 3 | 19 | 1 | 0 | 0.061255 | 289800
69 | 1 | 3 | 20 | 1 | 0 | 0.07735 | 289600
70 | 1 | 3 | 21 | 0 | 0 | 0.064554 | 289600
71 | 1 | 3 | 22 | 0 | 0 | 0.054754 | 289600
72 | 1 | 3 | 23 | 0 | 0 | 0.058559 | 289600
73 | 1 | 4 | 0 | 0 | 0 | 0.085639 | 289600
74 | 1 | 4 | 1 | 0 | 0 | 0.069102 | 289600
75 | 1 | 4 | 2 | 0 | 0 | 0.13126 | 289600
76 | 1 | 4 | 3 | 0 | 0 | 0.16451 | 289600
77 | 1 | 4 | 4 | 0 | 0 | 0.14173 | 289600
78 | 1 | 4 | 5 | 0 | 0 | 0.097928 | 289600
79 | 1 | 4 | 6 | 0 | 0 | 0.10806 | 289600
80 | 1 | 4 | 7 | 1 | 0.060581 | 0.1318 | 289400
81 | 1 | 4 | 8 | 1 | 0.31758 | 0.11686 | 289200
82 | 1 | 4 | 9 | 0 | 0.61057 | 0.10551 | 289200
83 | 1 | 4 | 10 | 0 | 0.86989 | 0.11338 | 289200
84 | 1 | 4 | 11 | 0 | 1 | 0.1277 | 289200
85 | 1 | 4 | 12 | 0 | 1 | 0.15649 | 289200
86 | 1 | 4 | 13 | 0 | 1 | 0.14027 | 289200
87 | 1 | 4 | 14 | 0 | 0.86989 | 0.12754 | 289200
88 | 1 | 4 | 15 | 0 | 0.61057 | 0.11178 | 289200
89 | 1 | 4 | 16 | 0 | 0.31758 | 0.16136 | 289200
90 | 1 | 4 | 17 | 0 | 0.060581 | 0.1453 | 289200
91 | 1 | 4 | 18 | 0 | 0 | 0.15119 | 289200
92 | 1 | 4 | 19 | 1 | 0 | 0.14401 | 289000
93 | 1 | 4 | 20 | 1 | 0 | 0.17249 | 288800
94 | 1 | 4 | 21 | 0 | 0 | 0.17181 | 288800
95 | 1 | 4 | 22 | 0 | 0 | 0.14578 | 288800
96 | 1 | 4 | 23 | 0 | 0 | 0.15439 | 288800
97 | 1 | 5 | 0 | 0 | 0 | 0.16487 | 288800
98 | 1 | 5 | 1 | 0 | 0 | 0.31706 | 288800
99 | 1 | 5 | 2 | 0 | 0 | 0.23361 | 288800
100 | 1 | 5 | 3 | 0 | 0 | 0.26 | 288800
101 | 1 | 5 | 4 | 0 | 0 | 0.22125 | 288800
102 | 1 | 5 | 5 | 0 | 0 | 0.25858 | 288800
103 | 1 | 5 | 6 | 0 | 0 | 0.35301 | 288800
104 | 1 | 5 | 7 | 1 | 0.068012 | 0.43665 | 288600
105 | 1 | 5 | 8 | 1 | 0.35654 | 0.5624 | 288400
106 | 1 | 5 | 9 | 0 | 0.68547 | 0.55143 | 288400
107 | 1 | 5 | 10 | 0 | 0.97661 | 0.52821 | 288400
108 | 1 | 5 | 11 | 0 | 1 | 0.32378 | 288400
109 | 1 | 5 | 12 | 0 | 1 | 0.34473 | 288400
110 | 1 | 5 | 13 | 0 | 1 | 0.3692 | 288400
111 | 1 | 5 | 14 | 0 | 0.97661 | 0.40466 | 288400
112 | 1 | 5 | 15 | 0 | 0.68547 | 0.42448 | 288400
113 | 1 | 5 | 16 | 0 | 0.35654 | 0.7223 | 288400
114 | 1 | 5 | 17 | 0 | 0.068012 | 0.51668 | 288400
115 | 1 | 5 | 18 | 0 | 0 | 0.39184 | 288400
116 | 1 | 5 | 19 | 1 | 0 | 0.28721 | 288200
117 | 1 | 5 | 20 | 1 | 0 | 0.48003 | 288000
118 | 1 | 5 | 21 | 0 | 0 | 0.51072 | 288000
119 | 1 | 5 | 22 | 0 | 0 | 0.40887 | 288000
120 | 1 | 5 | 23 | 0 | 0 | 0.35703 | 288000
121 | 1 | 6 | 0 | 0 | 0 | 0.36582 | 288000
122 | 1 | 6 | 1 | 0 | 0 | 0.36 | 288000
123 | 1 | 6 | 2 | 0 | 0 | 0.34817 | 288000
124 | 1 | 6 | 3 | 0 | 0 | 0.3159 | 288000
125 | 1 | 6 | 4 | 0 | 0 | 0.32531 | 288000
126 | 1 | 6 | 5 | 0 | 0 | 0.28956 | 288000
127 | 1 | 6 | 6 | 0 | 0 | 0.36933 | 288000
128 | 1 | 6 | 7 | 1 | 0.070155 | 0.54188 | 287800
129 | 1 | 6 | 8 | 1 | 0.36777 | 0.37265 | 287600
130 | 1 | 6 | 9 | 0 | 0.70707 | 0.24128 | 287600
131 | 1 | 6 | 10 | 0 | 1 | 0.16837 | 287600
132 | 1 | 6 | 11 | 0 | 1 | 0.18144 | 287600
133 | 1 | 6 | 12 | 0 | 1 | 0.23378 | 287600
134 | 1 | 6 | 13 | 0 | 1 | 0.35331 | 287600
135 | 1 | 6 | 14 | 0 | 1 | 0.164 | 287600
136 | 1 | 6 | 15 | 0 | 0.70707 | 0.1124 | 287600
137 | 1 | 6 | 16 | 0 | 0.36777 | 0.11934 | 287600
138 | 1 | 6 | 17 | 0 | 0.070155 | 0.10483 | 287600
139 | 1 | 6 | 18 | 0 | 0 | 0.13971 | 287600
140 | 1 | 6 | 19 | 1 | 0 | 0.12531 | 287400
141 | 1 | 6 | 20 | 1 | 0 | 0.19037 | 287200
142 | 1 | 6 | 21 | 0 | 0 | 0.17192 | 287200
143 | 1 | 6 | 22 | 0 | 0 | 0.1525 | 287200
144 | 1 | 6 | 23 | 0 | 0 | 0.08038 | 287200
145 | 1 | 7 | 0 | 0 | 0 | 0.15282 | 287200
146 | 1 | 7 | 1 | 0 | 0 | 0.14298 | 287200
147 | 1 | 7 | 2 | 0 | 0 | 0.13876 | 287200
148 | 1 | 7 | 3 | 0 | 0 | 0.12431 | 287200
149 | 1 | 7 | 4 | 0 | 0 | 0.14117 | 287200
150 | 1 | 7 | 5 | 0 | 0 | 0.17033 | 287200
151 | 1 | 7 | 6 | 0 | 0 | 0.18613 | 287200
152 | 1 | 7 | 7 | 1 | 0.070027 | 0.20562 | 287000
153 | 1 | 7 | 8 | 1 | 0.3671 | 0.18722 | 286800
154 | 1 | 7 | 9 | 0 | 0.70578 | 0.25102 | 286800
155 | 1 | 7 | 10 | 0 | 1 | 0.18001 | 286800
156 | 1 | 7 | 11 | 0 | 1 | 0.29399 | 286800
157 | 1 | 7 | 12 | 0 | 1 | 0.35726 | 286800
158 | 1 | 7 | 13 | 0 | 1 | 0.43879 | 286800
159 | 1 | 7 | 14 | 0 | 1 | 0.74728 | 286800
160 | 1 | 7 | 15 | 0 | 0.70578 | 0.46832 | 286800
161 | 1 | 7 | 16 | 0 | 0.3671 | 0.38363 | 286800
162 | 1 | 7 | 17 | 0 | 0.070027 | 0.29725 | 286800
163 | 1 | 7 | 18 | 0 | 0 | 0.30254 | 286800
164 | 1 | 7 | 19 | 1 | 0 | 0.22073 | 286600
165 | 1 | 7 | 20 | 1 | 0 | 0.18366 | 286400
166 | 1 | 7 | 21 | 0 | 0 | 0.11926 | 286400
167 | 1 | 7 | 22 | 0 | 0 | 0.13641 | 286400
168 | 1 | 7 | 23 | 0 | 0 | 0.077229 | 286400
169 | 1 | 8 | 0 | 0 | 0 | 0.079571 | 286400
170 | 1 | 8 | 1 | 0 | 0 | 0.094036 | 286400
171 | 1 | 8 | 2 | 0 | 0 | 0.18655 | 286400
172 | 1 | 8 | 3 | 0 | 0 | 0.17437 | 286400
173 | 1 | 8 | 4 | 0 | 0 | 0.1837 | 286400
174 | 1 | 8 | 5 | 0 | 0 | 0.16262 | 286400
175 | 1 | 8 | 6 | 0 | 0 | 0.18756 | 286400
176 | 1 | 8 | 7 | 1 | 0.074872 | 0.1349 | 286200
177 | 1 | 8 | 8 | 1 | 0.3925 | 0.15883 | 286000
178 | 1 | 8 | 9 | 0 | 0.75461 | 0.19381 | 286000
179 | 1 | 8 | 10 | 0 | 1 | 0.20247 | 286000
180 | 1 | 8 | 11 | 0 | 1 | 0.18782 | 286000
181 | 1 | 8 | 12 | 0 | 1 | 0.17899 | 286000
182 | 1 | 8 | 13 | 0 | 1 | 0.14974 | 286000
183 | 1 | 8 | 14 | 0 | 1 | 0.15885 | 286000
184 | 1 | 8 | 15 | 0 | 0.75461 | 0.13814 | 286000
185 | 1 | 8 | 16 | 0 | 0.3925 | 0.136 | 286000
186 | 1 | 8 | 17 | 0 | 0.074872 | 0.17307 | 286000
187 | 1 | 8 | 18 | 0 | 0 | 0.1634 | 286000
188 | 1 | 8 | 19 | 1 | 0 | 0.22064 | 285800
189 | 1 | 8 | 20 | 1 | 0 | 0.22491 | 285600
190 | 1 | 8 | 21 | 0 | 0 | 0.1726 | 285600
191 | 1 | 8 | 22 | 0 | 0 | 0.21505 | 285600
192 | 1 | 8 | 23 | 0 | 0 | 0.20361 | 285600
193 | 1 | 9 | 0 | 0 | 0 | 0.20289 | 285600
194 | 1 | 9 | 1 | 0 | 0 | 0.30118 | 285600
195 | 1 | 9 | 2 | 0 | 0 | 0.27349 | 285600
196 | 1 | 9 | 3 | 0 | 0 | 0.25787 | 285600
197 | 1 | 9 | 4 | 0 | 0 | 0.26526 | 285600
198 | 1 | 9 | 5 | 0 | 0 | 0.28565 | 285600
199 | 1 | 9 | 6 | 0 | 0 | 0.20209 | 285600
200 | 1 | 9 | 7 | 1 | 0.077571 | 0.22433 | 285400
201 | 1 | 9 | 8 | 1 | 0.40665 | 0.12948 | 285200
202 | 1 | 9 | 9 | 0 | 0.78182 | 0.12031 | 285200
203 | 1 | 9 | 10 | 0 | 1 | 0.14123 | 285200
204 | 1 | 9 | 11 | 0 | 1 | 0.13556 | 285200
205 | 1 | 9 | 12 | 0 | 1 | 0.10484 | 285200
206 | 1 | 9 | 13 | 0 | 1 | 0.11274 | 285200
207 | 1 | 9 | 14 | 0 | 1 | 0.12424 | 285200
208 | 1 | 9 | 15 | 0 | 0.78182 | 0.14552 | 285200
209 | 1 | 9 | 16 | 0 | 0.40665 | 0.11869 | 285200
210 | 1 | 9 | 17 | 0 | 0.077571 | 0.12423 | 285200
211 | 1 | 9 | 18 | 0 | 0 | 0.13035 | 285200
212 | 1 | 9 | 19 | 1 | 0 | 0.11569 | 285000
213 | 1 | 9 | 20 | 1 | 0 | 0.14288 | 284800
214 | 1 | 9 | 21 | 0 | 0 | 0.10556 | 284800
215 | 1 | 9 | 22 | 0 | 0 | 0.11871 | 284800
216 | 1 | 9 | 23 | 0 | 0 | 0.16006 | 284800
217 | 1 | 10 | 0 | 0 | 0 | 0.2982 | 284800
218 | 1 | 10 | 1 | 0 | 0 | 0.25864 | 284800
219 | 1 | 10 | 2 | 0 | 0 | 0.28506 | 284800
220 | 1 | 10 | 3 | 0 | 0 | 0.34726 | 284800
221 | 1 | 10 | 4 | 0 | 0 | 0.35564 | 284800
222 | 1 | 10 | 5 | 0 | 0 | 0.2916 | 284800
223 | 1 | 10 | 6 | 0 | 0 | 0.40126 | 284800
224 | 1 | 10 | 7 | 1 | 0.064139 | 0.49262 | 284600
225 | 1 | 10 | 8 | 1 | 0.33624 | 0.41637 | 284400
226 | 1 | 10 | 9 | 0 | 0.64644 | 0.55287 | 284400
227 | 1 | 10 | 10 | 0 | 0.92099 | 0.34199 | 284400
228 | 1 | 10 | 11 | 0 | 1 | 0.43657 | 284400
229 | 1 | 10 | 12 | 0 | 1 | 0.40784 | 284400
230 | 1 | 10 | 13 | 0 | 1 | 0.41356 | 284400
231 | 1 | 10 | 14 | 0 | 0.92099 | 0.46241 | 284400
232 | 1 | 10 | 15 | 0 | 0.64644 | 0.42963 | 284400
233 | 1 | 10 | 16 | 0 | 0.33624 | 0.31187 | 284400
234 | 1 | 10 | 17 | 0 | 0.064139 | 0.25495 | 284400
235 | 1 | 10 | 18 | 0 | 0 | 0.20843 | 284400
236 | 1 | 10 | 19 | 1 | 0 | 0.22939 | 284200
237 | 1 | 10 | 20 | 1 | 0 | 0.1668 | 284000
238 | 1 | 10 | 21 | 0 | 0 | 0.12068 | 284000
239 | 1 | 10 | 22 | 0 | 0 | 0.097817 | 284000
240 | 1 | 10 | 23 | 0 | 0 | 0.064717 | 284000
241 | 1 | 11 | 0 | 0 | 0 | 0.093353 | 284000
242 | 1 | 11 | 1 | 0 | 0 | 0.10057 | 284000
243 | 1 | 11 | 2 | 0 | 0 | 0.1395 | 284000
244 | 1 | 11 | 3 | 0 | 0 | 0.11911 | 284000
245 | 1 | 11 | 4 | 0 | 0 | 0.095534 | 284000
246 | 1 | 11 | 5 | 0 | 0 | 0.16616 | 284000
247 | 1 | 11 | 6 | 0 | 0 | 0.17681 | 284000
248 | 1 | 11 | 7 | 1 | 0.064296 | 0.15851 | 283800
249 | 1 | 11 | 8 | 1 | 0.33705 | 0.15128 | 283600
250 | 1 | 11 | 9 | 0 | 0.64802 | 0.14451 | 283600
251 | 1 | 11 | 10 | 0 | 0.92324 | 0.12261 | 283600
252 | 1 | 11 | 11 | 0 | 1 | 0.10038 | 283600
253 | 1 | 11 | 12 | 0 | 1 | 0.10443 | 283600
254 | 1 | 11 | 13 | 0 | 1 | 0.065506 | 283600
255 | 1 | 11 | 14 | 0 | 0.92324 | 0.057244 | 283600
256 | 1 | 11 | 15 | 0 | 0.64802 | 0.058509 | 283600
257 | 1 | 11 | 16 | 0 | 0.33705 | 0.095894 | 283600
258 | 1 | 11 | 17 | 0 | 0.064296 | 0.082966 | 283600
259 | 1 | 11 | 18 | 0 | 0 | 0.063839 | 283600
260 | 1 | 11 | 19 | 1 | 0 | 0.084924 | 283400
261 | 1 | 11 | 20 | 1 | 0 | 0.077845 | 283200
262 | 1 | 11 | 21 | 0 | 0 | 0.080505 | 283200
263 | 1 | 11 | 22 | 0 | 0 | 0.10303 | 283200
264 | 1 | 11 | 23 | 0 | 0 | 0.10531 | 283200
265 | 1 | 12 | 0 | 0 | 0 | 0.12678 | 283200
266 | 1 | 12 | 1 | 0 | 0 | 0.16161 | 283200
267 | 1 | 12 | 2 | 0 | 0 | 0.13865 | 283200
268 | 1 | 12 | 3 | 0 | 0 | 0.1522 | 283200
269 | 1 | 12 | 4 | 0 | 0 | 0.17899 | 283200
270 | 1 | 12 | 5 | 0 | 0 | 0.23905 | 283200
271 | 1 | 12 | 6 | 0 | 0 | 0.30418 | 283200
272 | 1 | 12 | 7 | 1 | 0.068931 | 0.28765 | 283000
273 | 1 | 12 | 8 | 1 | 0.36135 | 0.42283 | 282800
274 | 1 | 12 | 9 | 0 | 0.69473 | 0.41757 | 282800
275 | 1 | 12 | 10 | 0 | 0.98979 | 0.45341 | 282800
276 | 1 | 12 | 11 | 0 | 1 | 0.40932 | 282800
277 | 1 | 12 | 12 | 0 | 1 | 0.43666 | 282800
278 | 1 | 12 | 13 | 0 | 1 | 0.47127 | 282800
279 | 1 | 12 | 14 | 0 | 0.98979 | 0.37801 | 282800
280 | 1 | 12 | 15 | 0 | 0.69473 | 0.30614 | 282800
281 | 1 | 12 | 16 | 0 | 0.36135 | 0.35951 | 282800
282 | 1 | 12 | 17 | 0 | 0.068931 | 0.34448 | 282800
283 | 1 | 12 | 18 | 0 | 0 | 0.42611 | 282800
284 | 1 | 12 | 19 | 1 | 0 | 0.54307 | 282600
285 | 1 | 12 | 20 | 1 | 0 | 0.41805 | 282400
286 | 1 | 12 | 21 | 0 | 0 | 0.45891 | 282400
287 | 1 | 12 | 22 | 0 | 0 | 0.35218 | 282400
288 | 1 | 12 | 23 | 0 | 0 | 0.34512 | 282400
289 | 1 | 13 | 0 | 0 | 0 | 0.36236 | 282400
290 | 1 | 13 | 1 | 0 | 0 | 0.26271 | 282400
291 | 1 | 13 | 2 | 0 | 0 | 0.29619 | 282400
292 | 1 | 13 | 3 | 0 | 0 | 0.37792 | 282400
293 | 1 | 13 | 4 | 0 | 0 | 0.32461 | 282400
294 | 1 | 13 | 5 | 0 | 0 | 0.26443 | 282400
295 | 1 | 13 | 6 | 0 | 0 | 0.27627 | 282400
296 | 1 | 13 | 7 | 1 | 0.069828 | 0.29478 | 282200
297 | 1 | 13 | 8 | 1 | 0.36605 | 0.18943 | 282000
298 | 1 | 13 | 9 | 0 | 0.70377 | 0.21844 | 282000
299 | 1 | 13 | 10 | 0 | 1 | 0.34929 | 282000
300 | 1 | 13 | 11 | 0 | 1 | 0.29868 | 282000
301 | 1 | 13 | 12 | 0 | 1 | 0.37883 | 282000
302 | 1 | 13 | 13 | 0 | 1 | 0.20182 | 282000
303 | 1 | 13 | 14 | 0 | 1 | 0.292 | 282000
304 | 1 | 13 | 15 | 0 | 0.70377 | 0.29608 | 282000
305 | 1 | 13 | 16 | 0 | 0.36605 | 0.24562 | 282000
306 | 1 | 13 | 17 | 0 | 0.069828 | 0.35411 | 282000
307 | 1 | 13 | 18 | 0 | 0 | 0.28681 | 282000
308 | 1 | 13 | 19 | 1 | 0 | 0.25184 | 281800
309 | 1 | 13 | 20 | 1 | 0 | 0.31663 | 281600
310 | 1 | 13 | 21 | 0 | 0 | 0.33657 | 281600
311 | 1 | 13 | 22 | 0 | 0 | 0.25208 | 281600
312 | 1 | 13 | 23 | 0 | 0 | 0.2678 | 281600
313 | 1 | 14 | 0 | 0 | 0 | 0.17561 | 281600
314 | 1 | 14 | 1 | 0 | 0 | 0.19782 | 281600
315 | 1 | 14 | 2 | 0 | 0 | 0.12129 | 281600
316 | 1 | 14 | 3 | 0 | 0 | 0.11347 | 281600
317 | 1 | 14 | 4 | 0 | 0 | 0.11697 | 281600
318 | 1 | 14 | 5 | 0 | 0 | 0.1206 | 281600
319 | 1 | 14 | 6 | 0 | 0 | 0.082422 | 281600
320 | 1 | 14 | 7 | 1 | 0.070068 | 0.044803 | 281400
321 | 1 | 14 | 8 | 1 | 0.36732 | 0.090204 | 281200
322 | 1 | 14 | 9 | 0 | 0.70619 | 0.099098 | 281200
323 | 1 | 14 | 10 | 0 | 1 | 0.11712 | 281200
324 | 1 | 14 | 11 | 0 | 1 | 0.073552 | 281200
325 | 1 | 14 | 12 | 0 | 1 | 0.11209 | 281200
326 | 1 | 14 | 13 | 0 | 1 | 0.094031 | 281200
327 | 1 | 14 | 14 | 0 | 1 | 0.097692 | 281200
328 | 1 | 14 | 15 | 0 | 0.70619 | 0.089633 | 281200
329 | 1 | 14 | 16 | 0 | 0.36732 | 0.097496 | 281200
330 | 1 | 14 | 17 | 0 | 0.070068 | 0.12671 | 281200
331 | 1 | 14 | 18 | 0 | 0 | 0.11192 | 281200
332 | 1 | 14 | 19 | 1 | 0 | 0.1576 | 281000
333 | 1 | 14 | 20 | 1 | 0 | 0.11252 | 280800
334 | 1 | 14 | 21 | 0 | 0 | 0.094772 | 280800
335 | 1 | 14 | 22 | 0 | 0 | 0.13118 | 280800
336 | 1 | 14 | 23 | 0 | 0 | 0.091592 | 280800
337 | 1 | 15 | 0 | 0 | 0 | 0.099778 | 280800
338 | 1 | 15 | 1 | 0 | 0 | 0.093175 | 280800
339 | 1 | 15 | 2 | 0 | 0 | 0.058883 | 280800
340 | 1 | 15 | 3 | 0 | 0 | 0.054819 | 280800
341 | 1 | 15 | 4 | 0 | 0 | 0.042322 | 280800
342 | 1 | 15 | 5 | 0 | 0 | 0.044167 | 280800
343 | 1 | 15 | 6 | 0 | 0 | 0.043905 | 280800
344 | 1 | 15 | 7 | 1 | 0.056982 | 0.04886 | 280600
345 | 1 | 15 | 8 | 1 | 0.29872 | 0.039039 | 280400
346 | 1 | 15 | 9 | 0 | 0.57431 | 0.05766 | 280400
347 | 1 | 15 | 10 | 0 | 0.81822 | 0.046518 | 280400
348 | 1 | 15 | 11 | 0 | 0.98421 | 0.047762 | 280400
349 | 1 | 15 | 12 | 0 | 1 | 0.070158 | 280400
350 | 1 | 15 | 13 | 0 | 0.98421 | 0.089387 | 280400
351 | 1 | 15 | 14 | 0 | 0.81822 | 0.095571 | 280400
352 | 1 | 15 | 15 | 0 | 0.57431 | 0.086816 | 280400
353 | 1 | 15 | 16 | 0 | 0.29872 | 0.10906 | 280400
354 | 1 | 15 | 17 | 0 | 0.056982 | 0.090772 | 280400
355 | 1 | 15 | 18 | 0 | 0 | 0.061738 | 280400
356 | 1 | 15 | 19 | 1 | 0 | 0.095819 | 280200
357 | 1 | 15 | 20 | 1 | 0 | 0.09046 | 280000
358 | 1 | 15 | 21 | 0 | 0 | 0.088916 | 280000
359 | 1 | 15 | 22 | 0 | 0 | 0.088965 | 280000
360 | 1 | 15 | 23 | 0 | 0 | 0.076083 | 280000
361 | 1 | 16 | 0 | 0 | 0 | 0.076552 | 280000
362 | 1 | 16 | 1 | 0 | 0 | 0.071772 | 280000
363 | 1 | 16 | 2 | 0 | 0 | 0.05185 | 280000
364 | 1 | 16 | 3 | 0 | 0 | 0.073075 | 280000
365 | 1 | 16 | 4 | 0 | 0 | 0.088517 | 280000
366 | 1 | 16 | 5 | 0 | 0 | 0.092293 | 280000
367 | 1 | 16 | 6 | 0 | 0 | 0.098391 | 280000
368 | 1 | 16 | 7 | 1 | 0.074729 | 0.14041 | 279800
369 | 1 | 16 | 8 | 1 | 0.39175 | 0.14823 | 279600
370 | 1 | 16 | 9 | 0 | 0.75317 | 0.21393 | 279600
371 | 1 | 16 | 10 | 0 | 1 | 0.2227 | 279600
372 | 1 | 16 | 11 | 0 | 1 | 0.16146 | 279600
373 | 1 | 16 | 12 | 0 | 1 | 0.2576 | 279600
374 | 1 | 16 | 13 | 0 | 1 | 0.20073 | 279600
375 | 1 | 16 | 14 | 0 | 1 | 0.30743 | 279600
376 | 1 | 16 | 15 | 0 | 0.75317 | 0.36574 | 279600
377 | 1 | 16 | 16 | 0 | 0.39175 | 0.30246 | 279600
378 | 1 | 16 | 17 | 0 | 0.074729 | 0.31159 | 279600
379 | 1 | 16 | 18 | 0 | 0 | 0.24192 | 279600
380 | 1 | 16 | 19 | 1 | 0 | 0.30302 | 279400
381 | 1 | 16 | 20 | 1 | 0 | 0.33533 | 279200
382 | 1 | 16 | 21 | 0 | 0 | 0.35012 | 279200
383 | 1 | 16 | 22 | 0 | 0 | 0.36772 | 279200
384 | 1 | 16 | 23 | 0 | 0 | 0.328 | 279200
385 | 1 | 17 | 0 | 0 | 0 | 0.30001 | 279200
386 | 1 | 17 | 1 | 0 | 0 | 0.2964 | 279200
387 | 1 | 17 | 2 | 0 | 0 | 0.34253 | 279200
388 | 1 | 17 | 3 | 0 | 0 | 0.23658 | 279200
389 | 1 | 17 | 4 | 0 | 0 | 0.21863 | 279200
390 | 1 | 17 | 5 | 0 | 0 | 0.18004 | 279200
391 | 1 | 17 | 6 | 0 | 0 | 0.10318 | 279200
392 | 1 | 17 | 7 | 1 | 0.07419 | 0.1345 | 279000
393 | 1 | 17 | 8 | 1 | 0.38892 | 0.17534 | 278800
394 | 1 | 17 | 9 | 0 | 0.74774 | 0.13695 | 278800
395 | 1 | 17 | 10 | 0 | 1 | 0.14884 | 278800
396 | 1 | 17 | 11 | 0 | 1 | 0.15163 | 278800
397 | 1 | 17 | 12 | 0 | 1 | 0.14271 | 278800
398 | 1 | 17 | 13 | 0 | 1 | 0.10367 | 278800
399 | 1 | 17 | 14 | 0 | 1 | 0.11511 | 278800
400 | 1 | 17 | 15 | 0 | 0.74774 | 0.13573 | 278800
401 | 1 | 17 | 16 | 0 | 0.38892 | 0.15001 | 278800
402 | 1 | 17 | 17 | 0 | 0.07419 | 0.14707 | 278800
403 | 1 | 17 | 18 | 0 | 0 | 0.16584 | 278800
404 | 1 | 17 | 19 | 1 | 0 | 0.15299 | 278600
405 | 1 | 17 | 20 | 1 | 0 | 0.1758 | 278400
406 | 1 | 17 | 21 | 0 | 0 | 0.20337 | 278400
407 | 1 | 17 | 22 | 0 | 0 | 0.25461 | 278400
408 | 1 | 17 | 23 | 0 | 0 | 0.24121 | 278400
409 | 1 | 18 | 0 | 0 | 0 | 0.19678 | 278400
410 | 1 | 18 | 1 | 0 | 0 | 0.19997 | 278400
411 | 1 | 18 | 2 | 0 | 0 | 0.18407 | 278400
412 | 1 | 18 | 3 | 0 | 0 | 0.11474 | 278400
413 | 1 | 18 | 4 | 0 | 0 | 0.11978 | 278400
414 | 1 | 18 | 5 | 0 | 0 | 0.094292 | 278400
415 | 1 | 18 | 6 | 0 | 0 | 0.12277 | 278400
416 | 1 | 18 | 7 | 1 | 0.079353 | 0.13192 | 278200
417 | 1 | 18 | 8 | 1 | 0.41599 | 0.11194 | 278000
418 | 1 | 18 | 9 | 0 | 0.79978 | 0.12604 | 278000
419 | 1 | 18 | 10 | 0 | 1 | 0.15585 | 278000
420 | 1 | 18 | 11 | 0 | 1 | 0.18807 | 278000
421 | 1 | 18 | 12 | 0 | 1 | 0.15105 | 278000
422 | 1 | 18 | 13 | 0 | 1 | 0.13663 | 278000
423 | 1 | 18 | 14 | 0 | 1 | 0.12432 | 278000
424 | 1 | 18 | 15 | 0 | 0.79978 | 0.099266 | 278000
425 | 1 | 18 | 16 | 0 | 0.41599 | 0.088424 | 278000
426 | 1 | 18 | 17 | 0 | 0.079353 | 0.1188 | 278000
427 | 1 | 18 | 18 | 0 | 0 | 0.12695 | 278000
428 | 1 | 18 | 19 | 1 | 0 | 0.11224 | 277800
429 | 1 | 18 | 20 | 1 | 0 | 0.10473 | 277600
430 | 1 | 18 | 21 | 0 | 0 | 0.093044 | 277600
431 | 1 | 18 | 22 | 0 | 0 | 0.074738 | 277600
432 | 1 | 18 | 23 | 0 | 0 | 0.064234 | 277600
433 | 1 | 19 | 0 | 0 | 0 | 0.058036 | 277600
434 | 1 | 19 | 1 | 0 | 0 | 0.075183 | 277600
435 | 1 | 19 | 2 | 0 | 0 | 0.085871 | 277600
436 | 1 | 19 | 3 | 0 | 0 | 0.095468 | 277600
437 | 1 | 19 | 4 | 0 | 0 | 0.14338 | 277600
438 | 1 | 19 | 5 | 0 | 0 | 0.17817 | 277600
439 | 1 | 19 | 6 | 0 | 0 | 0.22283 | 277600
440 | 1 | 19 | 7 | 1 | 0.065066 | 0.1726 | 277400
441 | 1 | 19 | 8 | 1 | 0.34109 | 0.20576 | 277200
442 | 1 | 19 | 9 | 0 | 0.65578 | 0.33872 | 277200
443 | 1 | 19 | 10 | 0 | 0.93429 | 0.39138 | 277200
444 | 1 | 19 | 11 | 0 | 1 | 0.22695 | 277200
445 | 1 | 19 | 12 | 0 | 1 | 0.15963 | 277200
446 | 1 | 19 | 13 | 0 | 1 | 0.21 | 277200
447 | 1 | 19 | 14 | 0 | 0.93429 | 0.31692 | 277200
448 | 1 | 19 | 15 | 0 | 0.65578 | 0.4407 | 277200
449 | 1 | 19 | 16 | 0 | 0.34109 | 0.29404 | 277200
450 | 1 | 19 | 17 | 0 | 0.065066 | 0.25442 | 277200
451 | 1 | 19 | 18 | 0 | 0 | 0.23135 | 277200
452 | 1 | 19 | 19 | 1 | 0 | 0.11757 | 277000
453 | 1 | 19 | 20 | 1 | 0 | 0.10834 | 276800
454 | 1 | 19 | 21 | 0 | 0 | 0.10148 | 276800
455 | 1 | 19 | 22 | 0 | 0 | 0.12718 | 276800
456 | 1 | 19 | 23 | 0 | 0 | 0.1355 | 276800
457 | 1 | 20 | 0 | 0 | 0 | 0.095073 | 276800
458 | 1 | 20 | 1 | 0 | 0 | 0.074406 | 276800
459 | 1 | 20 | 2 | 0 | 0 | 0.11065 | 276800
460 | 1 | 20 | 3 | 0 | 0 | 0.090249 | 276800
461 | 1 | 20 | 4 | 0 | 0 | 0.10906 | 276800
462 | 1 | 20 | 5 | 0 | 0 | 0.098419 | 276800
463 | 1 | 20 | 6 | 0 | 0 | 0.11445 | 276800
464 | 1 | 20 | 7 | 1 | 0.065477 | 0.13977 | 276600
465 | 1 | 20 | 8 | 1 | 0.34325 | 0.19198 | 276400
466 | 1 | 20 | 9 | 0 | 0.65992 | 0.20434 | 276400
467 | 1 | 20 | 10 | 0 | 0.9402 | 0.3032 | 276400
468 | 1 | 20 | 11 | 0 | 1 | 0.42595 | 276400
469 | 1 | 20 | 12 | 0 | 1 | 0.5768 | 276400
470 | 1 | 20 | 13 | 0 | 1 | 0.69369 | 276400
471 | 1 | 20 | 14 | 0 | 0.9402 | 0.54958 | 276400
472 | 1 | 20 | 15 | 0 | 0.65992 | 1 | 276400
473 | 1 | 20 | 16 | 0 | 0.34325 | 0.84836 | 276400
474 | 1 | 20 | 17 | 0 | 0.065477 | 0.37539 | 276400
475 | 1 | 20 | 18 | 0 | 0 | 0.26581 | 276400
476 | 1 | 20 | 19 | 1 | 0 | 0.23798 | 276200
477 | 1 | 20 | 20 | 1 | 0 | 0.24145 | 276000
478 | 1 | 20 | 21 | 0 | 0 | 0.16172 | 276000
479 | 1 | 20 | 22 | 0 | 0 | 0.21086 | 276000
480 | 1 | 20 | 23 | 0 | 0 | 0.1772 | 276000
481 | 1 | 21 | 0 | 0 | 0 | 0.14415 | 276000
482 | 1 | 21 | 1 | 0 | 0 | 0.13178 | 276000
483 | 1 | 21 | 2 | 0 | 0 | 0.18311 | 276000
484 | 1 | 21 | 3 | 0 | 0 | 0.14827 | 276000
485 | 1 | 21 | 4 | 0 | 0 | 0.16354 | 276000
486 | 1 | 21 | 5 | 0 | 0 | 0.32094 | 276000
487 | 1 | 21 | 6 | 0 | 0 | 0.22681 | 276000
488 | 1 | 21 | 7 | 1 | 0.069937 | 0.16966 | 275800
489 | 1 | 21 | 8 | 1 | 0.36663 | 0.15832 | 275600
490 | 1 | 21 | 9 | 0 | 0.70488 | 0.14898 | 275600
491 | 1 | 21 | 10 | 0 | 1 | 0.19624 | 275600
492 | 1 | 21 | 11 | 0 | 1 | 0.17336 | 275600
493 | 1 | 21 | 12 | 0 | 1 | 0.2031 | 275600
494 | 1 | 21 | 13 | 0 | 1 | 0.19266 | 275600
495 | 1 | 21 | 14 | 0 | 1 | 0.16381 | 275600
496 | 1 | 21 | 15 | 0 | 0.70488 | 0.18642 | 275600
497 | 1 | 21 | 16 | 0 | 0.36663 | 0.19301 | 275600
498 | 1 | 21 | 17 | 0 | 0.069937 | 0.27209 | 275600
499 | 1 | 21 | 18 | 0 | 0 | 0.19451 | 275600
500 | 1 | 21 | 19 | 1 | 0 | 0.20881 | 275400
501 | 1 | 21 | 20 | 1 | 0 | 0.26183 | 275200
502 | 1 | 21 | 21 | 0 | 0 | 0.16991 | 275200
503 | 1 | 21 | 22 | 0 | 0 | 0.16523 | 275200
504 | 1 | 21 | 23 | 0 | 0 | 0.18227 | 275200
505 | 1 | 22 | 0 | 0 | 0 | 0.15967 | 275200
506 | 1 | 22 | 1 | 0 | 0 | 0.26395 | 275200
507 | 1 | 22 | 2 | 0 | 0 | 0.37632 | 275200
508 | 1 | 22 | 3 | 0 | 0 | 0.2979 | 275200
509 | 1 | 22 | 4 | 0 | 0 | 0.25395 | 275200
510 | 1 | 22 | 5 | 0 | 0 | 0.17731 | 275200
511 | 1 | 22 | 6 | 0 | 0 | 0.14779 | 275200
512 | 1 | 22 | 7 | 1 | 0.065556 | 0.16554 | 275000
513 | 1 | 22 | 8 | 1 | 0.34366 | 0.27527 | 274800
514 | 1 | 22 | 9 | 0 | 0.66072 | 0.26108 | 274800
515 | 1 | 22 | 10 | 0 | 0.94133 | 0.38838 | 274800
516 | 1 | 22 | 11 | 0 | 1 | 0.37921 | 274800
517 | 1 | 22 | 12 | 0 | 1 | 0.4015 | 274800
518 | 1 | 22 | 13 | 0 | 1 | 0.2679 | 274800
519 | 1 | 22 | 14 | 0 | 0.94133 | 0.34069 | 274800
520 | 1 | 22 | 15 | 0 | 0.66072 | 0.29552 | 274800
521 | 1 | 22 | 16 | 0 | 0.34366 | 0.44691 | 274800
522 | 1 | 22 | 17 | 0 | 0.065556 | 0.42096 | 274800
523 | 1 | 22 | 18 | 0 | 0 | 0.33714 | 274800
524 | 1 | 22 | 19 | 1 | 0 | 0.25669 | 274600
525 | 1 | 22 | 20 | 1 | 0 | 0.28058 | 274400
526 | 1 | 22 | 21 | 0 | 0 | 0.37686 | 274400
527 | 1 | 22 | 22 | 0 | 0 | 0.30432 | 274400
528 | 1 | 22 | 23 | 0 | 0 | 0.32446 | 274400
529 | 1 | 23 | 0 | 0 | 0 | 0.35255 | 274400
530 | 1 | 23 | 1 | 0 | 0 | 0.33431 | 274400
531 | 1 | 23 | 2 | 0 | 0 | 0.34461 | 274400
532 | 1 | 23 | 3 | 0 | 0 | 0.39155 | 274400
533 | 1 | 23 | 4 | 0 | 0 | 0.53004 | 274400
534 | 1 | 23 | 5 | 0 | 0 | 0.49321 | 274400
535 | 1 | 23 | 6 | 0 | 0 | 0.61459 | 274400
536 | 1 | 23 | 7 | 1 | 0.063027 | 0.59895 | 274200
537 | 1 | 23 | 8 | 1 | 0.33041 | 0.58812 | 274000
538 | 1 | 23 | 9 | 0 | 0.63523 | 0.60454 | 274000
539 | 1 | 23 | 10 | 0 | 0.90502 | 0.46227 | 274000
540 | 1 | 23 | 11 | 0 | 1 | 0.29633 | 274000
541 | 1 | 23 | 12 | 0 | 1 | 0.28268 | 274000
542 | 1 | 23 | 13 | 0 | 1 | 0.22923 | 274000
543 | 1 | 23 | 14 | 0 | 0.90502 | 0.31191 | 274000
544 | 1 | 23 | 15 | 0 | 0.63523 | 0.26641 | 274000
545 | 1 | 23 | 16 | 0 | 0.33041 | 0.33068 | 274000
546 | 1 | 23 | 17 | 0 | 0.063027 | 0.28922 | 274000
547 | 1 | 23 | 18 | 0 | 0 | 0.33298 | 274000
548 | 1 | 23 | 19 | 1 | 0 | 0.27284 | 273800
549 | 1 | 23 | 20 | 1 | 0 | 0.18441 | 273600
550 | 1 | 23 | 21 | 0 | 0 | 0.22513 | 273600
551 | 1 | 23 | 22 | 0 | 0 | 0.28459 | 273600
552 | 1 | 23 | 23 | 0 | 0 | 0.30608 | 273600
553 | 1 | 24 | 0 | 0 | 0 | 0.38348 | 273600
554 | 1 | 24 | 1 | 0 | 0 | 0.38794 | 273600
555 | 1 | 24 | 2 | 0 | 0 | 0.49287 | 273600
556 | 1 | 24 | 3 | 0 | 0 | 0.56144 | 273600
557 | 1 | 24 | 4 | 0 | 0 | 0.50369 | 273600
558 | 1 | 24 | 5 | 0 | 0 | 0.35796 | 273600
559 | 1 | 24 | 6 | 0 | 0 | 0.27278 | 273600
560 | 1 | 24 | 7 | 1 | 0.064005 | 0.16932 | 273400
561 | 1 | 24 | 8 | 1 | 0.33553 | 0.19601 | 273200
562 | 1 | 24 | 9 | 0 | 0.64509 | 0.23363 | 273200
563 | 1 | 24 | 10 | 0 | 0.91907 | 0.20997 | 273200
564 | 1 | 24 | 11 | 0 | 1 | 0.26925 | 273200
565 | 1 | 24 | 12 | 0 | 1 | 0.31356 | 273200
566 | 1 | 24 | 13 | 0 | 1 | 0.45096 | 273200
567 | 1 | 24 | 14 | 0 | 0.91907 | 0.46473 | 273200
568 | 1 | 24 | 15 | 0 | 0.64509 | 0.24255 | 273200
569 | 1 | 24 | 16 | 0 | 0.33553 | 0.2087 | 273200
570 | 1 | 24 | 17 | 0 | 0.064005 | 0.20504 | 273200
571 | 1 | 24 | 18 | 0 | 0 | 0.27143 | 273200
572 | 1 | 24 | 19 | 1 | 0 | 0.17769 | 273000
573 | 1 | 24 | 20 | 1 | 0 | 0.098934 | 272800
574 | 1 | 24 | 21 | 0 | 0 | 0.14322 | 272800
575 | 1 | 24 | 22 | 0 | 0 | 0.16402 | 272800
576 | 1 | 24 | 23 | 0 | 0 | 0.13384 | 272800
577 | 1 | 25 | 0 | 0 | 0 | 0.22099 | 272800
578 | 1 | 25 | 1 | 0 | 0 | 0.17323 | 272800
579 | 1 | 25 | 2 | 0 | 0 | 0.22604 | 272800
580 | 1 | 25 | 3 | 0 | 0 | 0.23728 | 272800
581 | 1 | 25 | 4 | 0 | 0 | 0.34233 | 272800
582 | 1 | 25 | 5 | 0 | 0 | 0.45872 | 272800
583 | 1 | 25 | 6 | 0 | 0 | 0.43958 | 272800
584 | 1 | 25 | 7 | 1 | 0.063188 | 0.45205 | 272600
585 | 1 | 25 | 8 | 1 | 0.33125 | 0.34022 | 272400
586 | 1 | 25 | 9 | 0 | 0.63685 | 0.32821 | 272400
587 | 1 | 25 | 10 | 0 | 0.90733 | 0.31002 | 272400
588 | 1 | 25 | 11 | 0 | 1 | 0.40596 | 272400
589 | 1 | 25 | 12 | 0 | 1 | 0.26971 | 272400
590 | 1 | 25 | 13 | 0 | 1 | 0.27223 | 272400
591 | 1 | 25 | 14 | 0 | 0.90733 | 0.29009 | 272400
592 | 1 | 25 | 15 | 0 | 0.63685 | 0.29522 | 272400
593 | 1 | 25 | 16 | 0 | 0.33125 | 0.25846 | 272400
594 | 1 | 25 | 17 | 0 | 0.063188 | 0.21269 | 272400
595 | 1 | 25 | 18 | 0 | 0 | 0.18884 | 272400
596 | 1 | 25 | 19 | 1 | 0 | 0.25453 | 272200
597 | 1 | 25 | 20 | 1 | 0 | 0.27571 | 272000
598 | 1 | 25 | 21 | 0 | 0 | 0.30907 | 272000
599 | 1 | 25 | 22 | 0 | 0 | 0.37029 | 272000
600 | 1 | 25 | 23 | 0 | 0 | 0.30286 | 272000
601 | 1 | 26 | 0 | 0 | 0 | 0.20866 | 272000
602 | 1 | 26 | 1 | 0 | 0 | 0.20701 | 272000
603 | 1 | 26 | 2 | 0 | 0 | 0.29022 | 272000
604 | 1 | 26 | 3 | 0 | 0 | 0.28451 | 272000
605 | 1 | 26 | 4 | 0 | 0 | 0.3187 | 272000
606 | 1 | 26 | 5 | 0 | 0 | 0.23491 | 272000
607 | 1 | 26 | 6 | 0 | 0 | 0.22864 | 272000
608 | 1 | 26 | 7 | 1 | 0.061826 | 0.27855 | 271800
609 | 1 | 26 | 8 | 1 | 0.32411 | 0.26926 | 271600
610 | 1 | 26 | 9 | 0 | 0.62313 | 0.27675 | 271600
611 | 1 | 26 | 10 | 0 | 0.88778 | 0.28147 | 271600
612 | 1 | 26 | 11 | 0 | 1 | 0.43867 | 271600
613 | 1 | 26 | 12 | 0 | 1 | 0.49386 | 271600
614 | 1 | 26 | 13 | 0 | 1 | 0.4603 | 271600
615 | 1 | 26 | 14 | 0 | 0.88778 | 0.55168 | 271600
616 | 1 | 26 | 15 | 0 | 0.62313 | 0.51488 | 271600
617 | 1 | 26 | 16 | 0 | 0.32411 | 0.48348 | 271600
618 | 1 | 26 | 17 | 0 | 0.061826 | 0.44971 | 271600
619 | 1 | 26 | 18 | 0 | 0 | 0.32952 | 271600
620 | 1 | 26 | 19 | 1 | 0 | 0.42823 | 271400
621 | 1 | 26 | 20 | 1 | 0 | 0.23736 | 271200
622 | 1 | 26 | 21 | 0 | 0 | 0.28027 | 271200
623 | 1 | 26 | 22 | 0 | 0 | 0.24644 | 271200
624 | 1 | 26 | 23 | 0 | 0 | 0.16135 | 271200
625 | 1 | 27 | 0 | 0 | 0 | 0.1715 | 271200
626 | 1 | 27 | 1 | 0 | 0 | 0.1062 | 271200
627 | 1 | 27 | 2 | 0 | 0 | 0.13802 | 271200
628 | 1 | 27 | 3 | 0 | 0 | 0.12721 | 271200
629 | 1 | 27 | 4 | 0 | 0 | 0.1459 | 271200
630 | 1 | 27 | 5 | 0 | 0 | 0.19482 | 271200
631 | 1 | 27 | 6 | 0 | 0 | 0.14562 | 271200
632 | 1 | 27 | 7 | 1 | 0.064478 | 0.10022 | 271000
633 | 1 | 27 | 8 | 1 | 0.33801 | 0.09579 | 270800
634 | 1 | 27 | 9 | 0 | 0.64985 | 0.089637 | 270800
635 | 1 | 27 | 10 | 0 | 0.92585 | 0.084644 | 270800
636 | 1 | 27 | 11 | 0 | 1 | 0.09891 | 270800
637 | 1 | 27 | 12 | 0 | 1 | 0.10208 | 270800
638 | 1 | 27 | 13 | 0 | 1 | 0.096954 | 270800
639 | 1 | 27 | 14 | 0 | 0.92585 | 0.10465 | 270800
640 | 1 | 27 | 15 | 0 | 0.64985 | 0.11155 | 270800
641 | 1 | 27 | 16 | 0 | 0.33801 | 0.083956 | 270800
642 | 1 | 27 | 17 | 0 | 0.064478 | 0.11124 | 270800
643 | 1 | 27 | 18 | 0 | 0 | 0.1072 | 270800
644 | 1 | 27 | 19 | 1 | 0 | 0.07766 | 270600
645 | 1 | 27 | 20 | 1 | 0 | 0.089281 | 270400
646 | 1 | 27 | 21 | 0 | 0 | 0.095244 | 270400
647 | 1 | 27 | 22 | 0 | 0 | 0.06816 | 270400
648 | 1 | 27 | 23 | 0 | 0 | 0.076806 | 270400
649 | 1 | 28 | 0 | 0 | 0 | 0.057739 | 270400
650 | 1 | 28 | 1 | 0 | 0 | 0.053212 | 270400
651 | 1 | 28 | 2 | 0 | 0 | 0.073323 | 270400
652 | 1 | 28 | 3 | 0 | 0 | 0.087236 | 270400
653 | 1 | 28 | 4 | 0 | 0 | 0.12937 | 270400
654 | 1 | 28 | 5 | 0 | 0 | 0.11659 | 270400
655 | 1 | 28 | 6 | 0 | 0 | 0.091646 | 270400
656 | 1 | 28 | 7 | 1 | 0.05973 | 0.12205 | 270200
657 | 1 | 28 | 8 | 1 | 0.31312 | 0.12942 | 270000
658 | 1 | 28 | 9 | 0 | 0.602 | 0.13056 | 270000
659 | 1 | 28 | 10 | 0 | 0.85768 | 0.19536 | 270000
660 | 1 | 28 | 11 | 0 | 1 | 0.17779 | 270000
661 | 1 | 28 | 12 | 0 | 1 | 0.17292 | 270000
662 | 1 | 28 | 13 | 0 | 1 | 0.15678 | 270000
663 | 1 | 28 | 14 | 0 | 0.85768 | 0.17362 | 270000
664 | 1 | 28 | 15 | 0 | 0.602 | 0.16746 | 270000
665 | 1 | 28 | 16 | 0 | 0.31312 | 0.14917 | 270000
666 | 1 | 28 | 17 | 0 | 0.05973 | 0.15974 | 270000
667 | 1 | 28 | 18 | 0 | 0 | 0.23667 | 270000
668 | 1 | 28 | 19 | 1 | 0 | 0.15385 | 269800
669 | 1 | 28 | 20 | 1 | 0 | 0.13523 | 269600
670 | 1 | 28 | 21 | 0 | 0 | 0.12254 | 269600
671 | 1 | 28 | 22 | 0 | 0 | 0.072461 | 269600
672 | 1 | 28 | 23 | 0 | 0 | 0.11133 | 269600
673 | 1 | 29 | 0 | 0 | 0 | 0.11386 | 269600
674 | 1 | 29 | 1 | 0 | 0 | 0.12718 | 269600
675 | 1 | 29 | 2 | 0 | 0 | 0.16676 | 269600
676 | 1 | 29 | 3 | 0 | 0 | 0.17387 | 269600
677 | 1 | 29 | 4 | 0 | 0 | 0.25121 | 269600
678 | 1 | 29 | 5 | 0 | 0 | 0.20423 | 269600
679 | 1 | 29 | 6 | 0 | 0 | 0.23009 | 269600
680 | 1 | 29 | 7 | 1 | 0.062363 | 0.33428 | 269400
681 | 1 | 29 | 8 | 1 | 0.32693 | 0.3271 | 269200
682 | 1 | 29 | 9 | 0 | 0.62854 | 0.25566 | 269200
683 | 1 | 29 | 10 | 0 | 0.89549 | 0.31147 | 269200
684 | 1 | 29 | 11 | 0 | 1 | 0.28284 | 269200
685 | 1 | 29 | 12 | 0 | 1 | 0.22047 | 269200
686 | 1 | 29 | 13 | 0 | 1 | 0.22386 | 269200
687 | 1 | 29 | 14 | 0 | 0.89549 | 0.37275 | 269200
688 | 1 | 29 | 15 | 0 | 0.62854 | 0.59899 | 269200
689 | 1 | 29 | 16 | 0 | 0.32693 | 0.62133 | 269200
690 | 1 | 29 | 17 | 0 | 0.062363 | 0.96329 | 269200
691 | 1 | 29 | 18 | 0 | 0 | 0.43224 | 269200
692 | 1 | 29 | 19 | 1 | 0 | 0.3614 | 269000
693 | 1 | 29 | 20 | 1 | 0 | 0.4506 | 268800
694 | 1 | 29 | 21 | 0 | 0 | 0.45665 | 268800
695 | 1 | 29 | 22 | 0 | 0 | 0.43221 | 268800
696 | 1 | 29 | 23 | 0 | 0 | 0.40458 | 268800
697 | 1 | 30 | 0 | 0 | 0 | 0.2983 | 268800
698 | 1 | 30 | 1 | 0 | 0 | 0.2196 | 268800
699 | 1 | 30 | 2 | 0 | 0 | 0.32487 | 268800
700 | 1 | 30 | 3 | 0 | 0 | 0.29948 | 268800
701 | 1 | 30 | 4 | 0 | 0 | 0.31636 | 268800
702 | 1 | 30 | 5 | 0 | 0 | 0.20456 | 268800
703 | 1 | 30 | 6 | 0 | 0 | 0.24004 | 268800
704 | 1 | 30 | 7 | 1 | 0.065221 | 0.23413 | 268600
705 | 1 | 30 | 8 | 1 | 0.34191 | 0.22545 | 268400
706 | 1 | 30 | 9 | 0 | 0.65734 | 0.31522 | 268400
707 | 1 | 30 | 10 | 0 | 0.93653 | 0.45406 | 268400
708 | 1 | 30 | 11 | 0 | 1 | 0.51303 | 268400
709 | 1 | 30 | 12 | 0 | 1 | 0.4951 | 268400
710 | 1 | 30 | 13 | 0 | 1 | 0.27737 | 268400
711 | 1 | 30 | 14 | 0 | 0.93653 | 0.38904 | 268400
712 | 1 | 30 | 15 | 0 | 0.65734 | 0.69904 | 268400
713 | 1 | 30 | 16 | 0 | 0.34191 | 0.69283 | 268400
714 | 1 | 30 | 17 | 0 | 0.065221 | 0.66405 | 268400
715 | 1 | 30 | 18 | 0 | 0 | 0.65357 | 268400
716 | 1 | 30 | 19 | 1 | 0 | 0.66808 | 268200
717 | 1 | 30 | 20 | 1 | 0 | 0.68797 | 268000
718 | 1 | 30 | 21 | 0 | 0 | 0.83296 | 268000
719 | 1 | 30 | 22 | 0 | 0 | 0.73847 | 268000
720 | 1 | 30 | 23 | 0 | 0 | 0.46659 | 268000
721 | 1 | 31 | 0 | 0 | 0 | 0.5836 | 268000
722 | 1 | 31 | 1 | 0 | 0 | 0.32635 | 268000
723 | 1 | 31 | 2 | 0 | 0 | 0.26461 | 268000
724 | 1 | 31 | 3 | 0 | 0 | 0.36761 | 268000
725 | 1 | 31 | 4 | 0 | 0 | 0.20954 | 268000
726 | 1 | 31 | 5 | 0 | 0 | 0.16385 | 268000
727 | 1 | 31 | 6 | 0 | 0 | 0.1528 | 268000
728 | 1 | 31 | 7 | 1 | 0.073678 | 0.13934 | 267800
729 | 1 | 31 | 8 | 1 | 0.38624 | 0.1367 | 267600
730 | 1 | 31 | 9 | 0 | 0.74258 | 0.12791 | 267600
731 | 1 | 31 | 10 | 0 | 1 | 0.12547 | 267600
732 | 1 | 31 | 11 | 0 | 1 | 0.12705 | 267600
733 | 1 | 31 | 12 | 0 | 1 | 0.12114 | 267600
734 | 1 | 31 | 13 | 0 | 1 | 0.15749 | 267600
735 | 1 | 31 | 14 | 0 | 1 | 0.18107 | 267600
736 | 1 | 31 | 15 | 0 | 0.74258 | 0.18049 | 267600
737 | 1 | 31 | 16 | 0 | 0.38624 | 0.12436 | 267600
738 | 1 | 31 | 17 | 0 | 0.073678 | 0.10977 | 267600
739 | 1 | 31 | 18 | 0 | 0 | 0.099774 | 267600
740 | 1 | 31 | 19 | 1 | 0 | 0.11112 | 267400
741 | 1 | 31 | 20 | 1 | 0 | 0.10784 | 267200
742 | 1 | 31 | 21 | 0 | 0 | 0.092034 | 267200
743 | 1 | 31 | 22 | 0 | 0 | 0.12437 | 267200
744 | 1 | 31 | 23 | 0 | 0 | 0.08377 | 267200
745 | 2 | 32 | 0 | 0 | 0 | 0.12216 | 267200
746 | 2 | 32 | 1 | 0 | 0 | 0.14484 | 267200
747 | 2 | 32 | 2 | 0 | 0 | 0.11342 | 267200
748 | 2 | 32 | 3 | 0 | 0 | 0.1432 | 267200
749 | 2 | 32 | 4 | 0 | 0 | 0.12882 | 267200
750 | 2 | 32 | 5 | 0 | 0 | 0.12436 | 267200
751 | 2 | 32 | 6 | 0 | 0 | 0.083123 | 267200
752 | 2 | 32 | 7 | 1 | 0.12018 | 0.082983 | 267000
753 | 2 | 32 | 8 | 1 | 0.40596 | 0.080053 | 266800
754 | 2 | 32 | 9 | 0 | 0.71275 | 0.1792 | 266800
755 | 2 | 32 | 10 | 0 | 0.97805 | 0.16123 | 266800
756 | 2 | 32 | 11 | 0 | 1 | 0.15419 | 266800
757 | 2 | 32 | 12 | 0 | 1 | 0.14053 | 266800
758 | 2 | 32 | 13 | 0 | 1 | 0.12345 | 266800
759 | 2 | 32 | 14 | 0 | 0.97805 | 0.14597 | 266800
760 | 2 | 32 | 15 | 0 | 0.71275 | 0.1665 | 266800
761 | 2 | 32 | 16 | 0 | 0.40596 | 0.1579 | 266800
762 | 2 | 32 | 17 | 0 | 0.12018 | 0.1806 | 266800
763 | 2 | 32 | 18 | 0 | 0 | 0.19544 | 266800
764 | 2 | 32 | 19 | 1 | 0 | 0.23635 | 266600
765 | 2 | 32 | 20 | 1 | 0 | 0.27064 | 266400
766 | 2 | 32 | 21 | 0 | 0 | 0.21073 | 266400
767 | 2 | 32 | 22 | 0 | 0 | 0.23698 | 266400
768 | 2 | 32 | 23 | 0 | 0 | 0.10884 | 266400
769 | 2 | 33 | 0 | 0 | 0 | 0.10917 | 266400
770 | 2 | 33 | 1 | 0 | 0 | 0.17378 | 266400
771 | 2 | 33 | 2 | 0 | 0 | 0.19392 | 266400
772 | 2 | 33 | 3 | 0 | 0 | 0.25042 | 266400
773 | 2 | 33 | 4 | 0 | 0 | 0.29464 | 266400
774 | 2 | 33 | 5 | 0 | 0 | 0.15758 | 266400
775 | 2 | 33 | 6 | 0 | 0 | 0.12283 | 266400
776 | 2 | 33 | 7 | 1 | 0.1596 | 0.19471 | 266200
777 | 2 | 33 | 8 | 1 | 0.53914 | 0.20403 | 266000
778 | 2 | 33 | 9 | 0 | 0.94657 | 0.23896 | 266000
779 | 2 | 33 | 10 | 0 | 1 | 0.24695 | 266000
780 | 2 | 33 | 11 | 0 | 1 | 0.19361 | 266000
781 | 2 | 33 | 12 | 0 | 1 | 0.2516 | 266000
782 | 2 | 33 | 13 | 0 | 1 | 0.21853 | 266000
783 | 2 | 33 | 14 | 0 | 1 | 0.17453 | 266000
784 | 2 | 33 | 15 | 0 | 0.94657 | 0.1782 | 266000
785 | 2 | 33 | 16 | 0 | 0.53914 | 0.19916 | 266000
786 | 2 | 33 | 17 | 0 | 0.1596 | 0.26346 | 266000
787 | 2 | 33 | 18 | 0 | 0 | 0.17739 | 266000
788 | 2 | 33 | 19 | 1 | 0 | 0.14461 | 265800
789 | 2 | 33 | 20 | 1 | 0 | 0.17631 | 265600
790 | 2 | 33 | 21 | 0 | 0 | 0.16101 | 265600
791 | 2 | 33 | 22 | 0 | 0 | 0.12044 | 265600
792 | 2 | 33 | 23 | 0 | 0 | 0.13498 | 265600
793 | 2 | 34 | 0 | 0 | 0 | 0.15066 | 265600
794 | 2 | 34 | 1 | 0 | 0 | 0.19994 | 265600
795 | 2 | 34 | 2 | 0 | 0 | 0.20885 | 265600
796 | 2 | 34 | 3 | 0 | 0 | 0.22211 | 265600
797 | 2 | 34 | 4 | 0 | 0 | 0.21694 | 265600
798 | 2 | 34 | 5 | 0 | 0 | 0.20295 | 265600
799 | 2 | 34 | 6 | 0 | 0 | 0.17462 | 265600
800 | 2 | 34 | 7 | 1 | 0.11848 | 0.099631 | 265400
801 | 2 | 34 | 8 | 1 | 0.40022 | 0.12595 | 265200
802 | 2 | 34 | 9 | 0 | 0.70268 | 0.17374 | 265200
803 | 2 | 34 | 10 | 0 | 0.96424 | 0.28184 | 265200
804 | 2 | 34 | 11 | 0 | 1 | 0.28343 | 265200
805 | 2 | 34 | 12 | 0 | 1 | 0.22949 | 265200
806 | 2 | 34 | 13 | 0 | 1 | 0.16114 | 265200
807 | 2 | 34 | 14 | 0 | 0.96424 | 0.20561 | 265200
808 | 2 | 34 | 15 | 0 | 0.70268 | 0.19465 | 265200
809 | 2 | 34 | 16 | 0 | 0.40022 | 0.27529 | 265200
810 | 2 | 34 | 17 | 0 | 0.11848 | 0.23895 | 265200
811 | 2 | 34 | 18 | 0 | 0 | 0.23681 | 265200
812 | 2 | 34 | 19 | 1 | 0 | 0.16221 | 265000
813 | 2 | 34 | 20 | 1 | 0 | 0.18733 | 264800
814 | 2 | 34 | 21 | 0 | 0 | 0.18909 | 264800
815 | 2 | 34 | 22 | 0 | 0 | 0.086325 | 264800
816 | 2 | 34 | 23 | 0 | 0 | 0.10587 | 264800
817 | 2 | 35 | 0 | 0 | 0 | 0.096006 | 264800
818 | 2 | 35 | 1 | 0 | 0 | 0.11332 | 264800
819 | 2 | 35 | 2 | 0 | 0 | 0.10711 | 264800
820 | 2 | 35 | 3 | 0 | 0 | 0.11039 | 264800
821 | 2 | 35 | 4 | 0 | 0 | 0.13046 | 264800
822 | 2 | 35 | 5 | 0 | 0 | 0.13161 | 264800
823 | 2 | 35 | 6 | 0 | 0 | 0.17084 | 264800
824 | 2 | 35 | 7 | 1 | 0.13637 | 0.2215 | 264600
825 | 2 | 35 | 8 | 1 | 0.46066 | 0.1956 | 264400
826 | 2 | 35 | 9 | 0 | 0.80878 | 0.21304 | 264400
827 | 2 | 35 | 10 | 0 | 1 | 0.13089 | 264400
828 | 2 | 35 | 11 | 0 | 1 | 0.19751 | 264400
829 | 2 | 35 | 12 | 0 | 1 | 0.14009 | 264400
830 | 2 | 35 | 13 | 0 | 1 | 0.15231 | 264400
831 | 2 | 35 | 14 | 0 | 1 | 0.17195 | 264400
832 | 2 | 35 | 15 | 0 | 0.80878 | 0.1646 | 264400
833 | 2 | 35 | 16 | 0 | 0.46066 | 0.24415 | 264400
834 | 2 | 35 | 17 | 0 | 0.13637 | 0.18841 | 264400
835 | 2 | 35 | 18 | 0 | 0 | 0.12001 | 264400
836 | 2 | 35 | 19 | 1 | 0 | 0.12535 | 264200
837 | 2 | 35 | 20 | 1 | 0 | 0.23281 | 264000
838 | 2 | 35 | 21 | 0 | 0 | 0.21916 | 264000
839 | 2 | 35 | 22 | 0 | 0 | 0.26282 | 264000
840 | 2 | 35 | 23 | 0 | 0 | 0.27763 | 264000
841 | 2 | 36 | 0 | 0 | 0 | 0.35964 | 264000
842 | 2 | 36 | 1 | 0 | 0 | 0.298 | 264000
843 | 2 | 36 | 2 | 0 | 0 | 0.35522 | 264000
844 | 2 | 36 | 3 | 0 | 0 | 0.37958 | 264000
845 | 2 | 36 | 4 | 0 | 0 | 0.40196 | 264000
846 | 2 | 36 | 5 | 0 | 0 | 0.4048 | 264000
847 | 2 | 36 | 6 | 0 | 0 | 0.43042 | 264000
848 | 2 | 36 | 7 | 1 | 0.13971 | 0.35015 | 263800
849 | 2 | 36 | 8 | 1 | 0.47193 | 0.26352 | 263600
850 | 2 | 36 | 9 | 0 | 0.82858 | 0.30748 | 263600
851 | 2 | 36 | 10 | 0 | 1 | 0.45263 | 263600
852 | 2 | 36 | 11 | 0 | 1 | 0.31325 | 263600
853 | 2 | 36 | 12 | 0 | 1 | 0.21338 | 263600
854 | 2 | 36 | 13 | 0 | 1 | 0.15619 | 263600
855 | 2 | 36 | 14 | 0 | 1 | 0.18973 | 263600
856 | 2 | 36 | 15 | 0 | 0.82858 | 0.31833 | 263600
857 | 2 | 36 | 16 | 0 | 0.47193 | 0.39125 | 263600
858 | 2 | 36 | 17 | 0 | 0.13971 | 0.51494 | 263600
859 | 2 | 36 | 18 | 0 | 0 | 0.30064 | 263600
860 | 2 | 36 | 19 | 1 | 0 | 0.35424 | 263400
861 | 2 | 36 | 20 | 1 | 0 | 0.34311 | 263200
862 | 2 | 36 | 21 | 0 | 0 | 0.38895 | 263200
863 | 2 | 36 | 22 | 0 | 0 | 0.44073 | 263200
864 | 2 | 36 | 23 | 0 | 0 | 0.4726 | 263200
865 | 2 | 37 | 0 | 0 | 0 | 0.56684 | 263200
866 | 2 | 37 | 1 | 0 | 0 | 0.42173 | 263200
867 | 2 | 37 | 2 | 0 | 0 | 0.32353 | 263200
868 | 2 | 37 | 3 | 0 | 0 | 0.20874 | 263200
869 | 2 | 37 | 4 | 0 | 0 | 0.17534 | 263200
870 | 2 | 37 | 5 | 0 | 0 | 0.26333 | 263200
871 | 2 | 37 | 6 | 0 | 0 | 0.34081 | 263200
872 | 2 | 37 | 7 | 1 | 0.13961 | 0.47449 | 263000
873 | 2 | 37 | 8 | 1 | 0.4716 | 0.43753 | 262800
874 | 2 | 37 | 9 | 0 | 0.828 | 0.36623 | 262800
875 | 2 | 37 | 10 | 0 | 1 | 0.35195 | 262800
876 | 2 | 37 | 11 | 0 | 1 | 0.35929 | 262800
877 | 2 | 37 | 12 | 0 | 1 | 0.35485 | 262800
878 | 2 | 37 | 13 | 0 | 1 | 0.33773 | 262800
879 | 2 | 37 | 14 | 0 | 1 | 0.36565 | 262800
880 | 2 | 37 | 15 | 0 | 0.828 | 0.39576 | 262800
881 | 2 | 37 | 16 | 0 | 0.4716 | 0.37027 | 262800
882 | 2 | 37 | 17 | 0 | 0.13961 | 0.35958 | 262800
883 | 2 | 37 | 18 | 0 | 0 | 0.40701 | 262800
884 | 2 | 37 | 19 | 1 | 0 | 0.25953 | 262600
885 | 2 | 37 | 20 | 1 | 0 | 0.25279 | 262400
886 | 2 | 37 | 21 | 0 | 0 | 0.33402 | 262400
887 | 2 | 37 | 22 | 0 | 0 | 0.30243 | 262400
888 | 2 | 37 | 23 | 0 | 0 | 0.39251 | 262400
889 | 2 | 38 | 0 | 0 | 0 | 0.41514 | 262400
890 | 2 | 38 | 1 | 0 | 0 | 0.6763 | 262400
891 | 2 | 38 | 2 | 0 | 0 | 0.49054 | 262400
892 | 2 | 38 | 3 | 0 | 0 | 0.46776 | 262400
893 | 2 | 38 | 4 | 0 | 0 | 0.50121 | 262400
894 | 2 | 38 | 5 | 0 | 0 | 0.49909 | 262400
895 | 2 | 38 | 6 | 0 | 0 | 0.66277 | 262400
896 | 2 | 38 | 7 | 1 | 0.13867 | 0.67163 | 262200
897 | 2 | 38 | 8 | 1 | 0.46842 | 0.60436 | 262000
898 | 2 | 38 | 9 | 0 | 0.82242 | 0.86946 | 262000
899 | 2 | 38 | 10 | 0 | 1 | 0.57459 | 262000
900 | 2 | 38 | 11 | 0 | 1 | 0.47934 | 262000
901 | 2 | 38 | 12 | 0 | 1 | 0.31116 | 262000
902 | 2 | 38 | 13 | 0 | 1 | 0.2826 | 262000
903 | 2 | 38 | 14 | 0 | 1 | 0.28161 | 262000
904 | 2 | 38 | 15 | 0 | 0.82242 | 0.22493 | 262000
905 | 2 | 38 | 16 | 0 | 0.46842 | 0.39293 | 262000
906 | 2 | 38 | 17 | 0 | 0.13867 | 0.24722 | 262000
907 | 2 | 38 | 18 | 0 | 0 | 0.29236 | 262000
908 | 2 | 38 | 19 | 1 | 0 | 0.3917 | 261800
909 | 2 | 38 | 20 | 1 | 0 | 0.30064 | 261600
910 | 2 | 38 | 21 | 0 | 0 | 0.446 | 261600
911 | 2 | 38 | 22 | 0 | 0 | 0.41408 | 261600
912 | 2 | 38 | 23 | 0 | 0 | 0.293 | 261600
913 | 2 | 39 | 0 | 0 | 0 | 0.27229 | 261600
914 | 2 | 39 | 1 | 0 | 0 | 0.32236 | 261600
915 | 2 | 39 | 2 | 0 | 0 | 0.2814 | 261600
916 | 2 | 39 | 3 | 0 | 0 | 0.33382 | 261600
917 | 2 | 39 | 4 | 0 | 0 | 0.42013 | 261600
918 | 2 | 39 | 5 | 0 | 0 | 0.41472 | 261600
919 | 2 | 39 | 6 | 0 | 0 | 0.38087 | 261600
920 | 2 | 39 | 7 | 1 | 0.13956 | 0.28023 | 261400
921 | 2 | 39 | 8 | 1 | 0.47144 | 0.25911 | 261200
922 | 2 | 39 | 9 | 0 | 0.82771 | 0.21481 | 261200
923 | 2 | 39 | 10 | 0 | 1 | 0.2441 | 261200
924 | 2 | 39 | 11 | 0 | 1 | 0.18276 | 261200
925 | 2 | 39 | 12 | 0 | 1 | 0.20427 | 261200
926 | 2 | 39 | 13 | 0 | 1 | 0.23093 | 261200
927 | 2 | 39 | 14 | 0 | 1 | 0.16102 | 261200
928 | 2 | 39 | 15 | 0 | 0.82771 | 0.14892 | 261200
929 | 2 | 39 | 16 | 0 | 0.47144 | 0.11126 | 261200
930 | 2 | 39 | 17 | 0 | 0.13956 | 0.13965 | 261200
931 | 2 | 39 | 18 | 0 | 0 | 0.13067 | 261200
932 | 2 | 39 | 19 | 1 | 0 | 0.16771 | 261000
933 | 2 | 39 | 20 | 1 | 0 | 0.17318 | 260800
934 | 2 | 39 | 21 | 0 | 0 | 0.13784 | 260800
935 | 2 | 39 | 22 | 0 | 0 | 0.094527 | 260800
936 | 2 | 39 | 23 | 0 | 0 | 0.11281 | 260800
937 | 2 | 40 | 0 | 0 | 0 | 0.11683 | 260800
938 | 2 | 40 | 1 | 0 | 0 | 0.090819 | 260800
939 | 2 | 40 | 2 | 0 | 0 | 0.092093 | 260800
940 | 2 | 40 | 3 | 0 | 0 | 0.16129 | 260800
941 | 2 | 40 | 4 | 0 | 0 | 0.16677 | 260800
942 | 2 | 40 | 5 | 0 | 0 | 0.25844 | 260800
943 | 2 | 40 | 6 | 0 | 0 | 0.23517 | 260800
944 | 2 | 40 | 7 | 1 | 0.13835 | 0.29627 | 260600
945 | 2 | 40 | 8 | 1 | 0.46735 | 0.25882 | 260400
946 | 2 | 40 | 9 | 0 | 0.82053 | 0.23671 | 260400
947 | 2 | 40 | 10 | 0 | 1 | 0.21723 | 260400
948 | 2 | 40 | 11 | 0 | 1 | 0.17908 | 260400
949 | 2 | 40 | 12 | 0 | 1 | 0.21638 | 260400
950 | 2 | 40 | 13 | 0 | 1 | 0.19397 | 260400
951 | 2 | 40 | 14 | 0 | 1 | 0.16097 | 260400
952 | 2 | 40 | 15 | 0 | 0.82053 | 0.149 | 260400
953 | 2 | 40 | 16 | 0 | 0.46735 | 0.20043 | 260400
954 | 2 | 40 | 17 | 0 | 0.13835 | 0.2218 | 260400
955 | 2 | 40 | 18 | 0 | 0 | 0.15529 | 260400
956 | 2 | 40 | 19 | 1 | 0 | 0.16996 | 260200
957 | 2 | 40 | 20 | 1 | 0 | 0.15746 | 260000
958 | 2 | 40 | 21 | 0 | 0 | 0.10328 | 260000
959 | 2 | 40 | 22 | 0 | 0 | 0.14693 | 260000
960 | 2 | 40 | 23 | 0 | 0 | 0.15251 | 260000
961 | 2 | 41 | 0 | 0 | 0 | 0.10193 | 260000
962 | 2 | 41 | 1 | 0 | 0 | 0.16893 | 260000
963 | 2 | 41 | 2 | 0 | 0 | 0.27892 | 260000
964 | 2 | 41 | 3 | 0 | 0 | 0.31246 | 260000
965 | 2 | 41 | 4 | 0 | 0 | 0.26102 | 260000
966 | 2 | 41 | 5 | 0 | 0 | 0.19076 | 260000
967 | 2 | 41 | 6 | 0 | 0 | 0.1528 | 260000
968 | 2 | 41 | 7 | 1 | 0.15555 | 0.13634 | 259800
969 | 2 | 41 | 8 | 1 | 0.52544 | 0.0987 | 259600
970 | 2 | 41 | 9 | 0 | 0.92252 | 0.10759 | 259600
971 | 2 | 41 | 10 | 0 | 1 | 0.11483 | 259600
972 | 2 | 41 | 11 | 0 | 1 | 0.15975 | 259600
973 | 2 | 41 | 12 | 0 | 1 | 0.12486 | 259600
974 | 2 | 41 | 13 | 0 | 1 | 0.12927 | 259600
975 | 2 | 41 | 14 | 0 | 1 | 0.10122 | 259600
976 | 2 | 41 | 15 | 0 | 0.92252 | 0.14852 | 259600
977 | 2 | 41 | 16 | 0 | 0.52544 | 0.12391 | 259600
978 | 2 | 41 | 17 | 0 | 0.15555 | 0.12211 | 259600
979 | 2 | 41 | 18 | 0 | 0 | 0.21074 | 259600
980 | 2 | 41 | 19 | 1 | 0 | 0.31125 | 259400
981 | 2 | 41 | 20 | 1 | 0 | 0.38092 | 259200
982 | 2 | 41 | 21 | 0 | 0 | 0.40991 | 259200
983 | 2 | 41 | 22 | 0 | 0 | 0.52984 | 259200
984 | 2 | 41 | 23 | 0 | 0 | 0.55792 | 259200
985 | 2 | 42 | 0 | 0 | 0 | 0.79417 | 259200
986 | 2 | 42 | 1 | 0 | 0 | 0.83292 | 259200
987 | 2 | 42 | 2 | 0 | 0 | 0.69002 | 259200
988 | 2 | 42 | 3 | 0 | 0 | 0.64441 | 259200
989 | 2 | 42 | 4 | 0 | 0 | 0.76766 | 259200
990 | 2 | 42 | 5 | 0 | 0 | 0.92854 | 259200
991 | 2 | 42 | 6 | 0 | 0 | 0.63634 | 259200
992 | 2 | 42 | 7 | 1 | 0.10295 | 0.44108 | 259000
993 | 2 | 42 | 8 | 1 | 0.34776 | 0.39442 | 258800
994 | 2 | 42 | 9 | 0 | 0.61057 | 0.44546 | 258800
995 | 2 | 42 | 10 | 0 | 0.83784 | 0.42419 | 258800
996 | 2 | 42 | 11 | 0 | 0.99068 | 0.65463 | 258800
997 | 2 | 42 | 12 | 0 | 1 | 0.38714 | 258800
998 | 2 | 42 | 13 | 0 | 0.99068 | 0.26256 | 258800
999 | 2 | 42 | 14 | 0 | 0.83784 | 0.25943 | 258800
1000 | 2 | 42 | 15 | 0 | 0.61057 | 0.29062 | 258800
1001 | 2 | 42 | 16 | 0 | 0.34776 | 0.24155 | 258800
1002 | 2 | 42 | 17 | 0 | 0.10295 | 0.23413 | 258800
1003 | 2 | 42 | 18 | 0 | 0 | 0.15165 | 258800
1004 | 2 | 42 | 19 | 1 | 0 | 0.10565 | 258600
1005 | 2 | 42 | 20 | 1 | 0 | 0.11704 | 258400
1006 | 2 | 42 | 21 | 0 | 0 | 0.076147 | 258400
1007 | 2 | 42 | 22 | 0 | 0 | 0.072663 | 258400
1008 | 2 | 42 | 23 | 0 | 0 | 0.082019 | 258400
1009 | 2 | 43 | 0 | 0 | 0 | 0.099124 | 258400
1010 | 2 | 43 | 1 | 0 | 0 | 0.10648 | 258400
1011 | 2 | 43 | 2 | 0 | 0 | 0.07709 | 258400
1012 | 2 | 43 | 3 | 0 | 0 | 0.068287 | 258400
1013 | 2 | 43 | 4 | 0 | 0 | 0.083624 | 258400
1014 | 2 | 43 | 5 | 0 | 0 | 0.091493 | 258400
1015 | 2 | 43 | 6 | 0 | 0 | 0.048946 | 258400
1016 | 2 | 43 | 7 | 1 | 0.124 | 0.039901 | 258200
1017 | 2 | 43 | 8 | 1 | 0.41887 | 0.040576 | 258000
1018 | 2 | 43 | 9 | 0 | 0.73542 | 0.041706 | 258000
1019 | 2 | 43 | 10 | 0 | 1 | 0.03391 | 258000
1020 | 2 | 43 | 11 | 0 | 1 | 0.055178 | 258000
1021 | 2 | 43 | 12 | 0 | 1 | 0.070497 | 258000
1022 | 2 | 43 | 13 | 0 | 1 | 0.066962 | 258000
1023 | 2 | 43 | 14 | 0 | 1 | 0.10387 | 258000
1024 | 2 | 43 | 15 | 0 | 0.73542 | 0.13924 | 258000
1025 | 2 | 43 | 16 | 0 | 0.41887 | 0.10307 | 258000
1026 | 2 | 43 | 17 | 0 | 0.124 | 0.14301 | 258000
1027 | 2 | 43 | 18 | 0 | 0 | 0.094168 | 258000
1028 | 2 | 43 | 19 | 1 | 0 | 0.090505 | 257800
1029 | 2 | 43 | 20 | 1 | 0 | 0.0737 | 257600
1030 | 2 | 43 | 21 | 0 | 0 | 0.070869 | 257600
1031 | 2 | 43 | 22 | 0 | 0 | 0.083392 | 257600
1032 | 2 | 43 | 23 | 0 | 0 | 0.10907 | 257600
1033 | 2 | 44 | 0 | 0 | 0 | 0.095599 | 257600
1034 | 2 | 44 | 1 | 0 | 0 | 0.090398 | 257600
1035 | 2 | 44 | 2 | 0 | 0 | 0.1309 | 257600
1036 | 2 | 44 | 3 | 0 | 0 | 0.11654 | 257600
1037 | 2 | 44 | 4 | 0 | 0 | 0.16526 | 257600
1038 | 2 | 44 | 5 | 0 | 0 | 0.18326 | 257600
1039 | 2 | 44 | 6 | 0 | 0 | 0.23511 | 257600
1040 | 2 | 44 | 7 | 1 | 0.14618 | 0.237 | 257400
1041 | 2 | 44 | 8 | 1 | 0.4938 | 0.17821 | 257200
1042 | 2 | 44 | 9 | 0 | 0.86697 | 0.21004 | 257200
1043 | 2 | 44 | 10 | 0 | 1 | 0.23865 | 257200
1044 | 2 | 44 | 11 | 0 | 1 | 0.26046 | 257200
1045 | 2 | 44 | 12 | 0 | 1 | 0.25007 | 257200
1046 | 2 | 44 | 13 | 0 | 1 | 0.32178 | 257200
1047 | 2 | 44 | 14 | 0 | 1 | 0.30647 | 257200
1048 | 2 | 44 | 15 | 0 | 0.86697 | 0.34166 | 257200
1049 | 2 | 44 | 16 | 0 | 0.4938 | 0.22745 | 257200
1050 | 2 | 44 | 17 | 0 | 0.14618 | 0.207 | 257200
1051 | 2 | 44 | 18 | 0 | 0 | 0.24614 | 257200
1052 | 2 | 44 | 19 | 1 | 0 | 0.18546 | 257000
1053 | 2 | 44 | 20 | 1 | 0 | 0.20369 | 256800
1054 | 2 | 44 | 21 | 0 | 0 | 0.23991 | 256800
1055 | 2 | 44 | 22 | 0 | 0 | 0.1958 | 256800
1056 | 2 | 44 | 23 | 0 | 0 | 0.12884 | 256800
1057 | 2 | 45 | 0 | 0 | 0 | 0.13334 | 256800
1058 | 2 | 45 | 1 | 0 | 0 | 0.17229 | 256800
1059 | 2 | 45 | 2 | 0 | 0 | 0.19198 | 256800
1060 | 2 | 45 | 3 | 0 | 0 | 0.23705 | 256800
1061 | 2 | 45 | 4 | 0 | 0 | 0.34011 | 256800
1062 | 2 | 45 | 5 | 0 | 0 | 0.46321 | 256800
1063 | 2 | 45 | 6 | 0 | 0 | 0.72526 | 256800
1064 | 2 | 45 | 7 | 1 | 0.14294 | 0.51803 | 256600
1065 | 2 | 45 | 8 | 1 | 0.48283 | 0.58156 | 256400
1066 | 2 | 45 | 9 | 0 | 0.84771 | 0.8177 | 256400
1067 | 2 | 45 | 10 | 0 | 1 | 0.74291 | 256400
1068 | 2 | 45 | 11 | 0 | 1 | 0.76276 | 256400
1069 | 2 | 45 | 12 | 0 | 1 | 0.70059 | 256400
1070 | 2 | 45 | 13 | 0 | 1 | 0.38241 | 256400
1071 | 2 | 45 | 14 | 0 | 1 | 0.44456 | 256400
1072 | 2 | 45 | 15 | 0 | 0.84771 | 0.32526 | 256400
1073 | 2 | 45 | 16 | 0 | 0.48283 | 0.43403 | 256400
1074 | 2 | 45 | 17 | 0 | 0.14294 | 0.45411 | 256400
1075 | 2 | 45 | 18 | 0 | 0 | 0.60798 | 256400
1076 | 2 | 45 | 19 | 1 | 0 | 0.75145 | 256200
1077 | 2 | 45 | 20 | 1 | 0 | 0.39798 | 256000
1078 | 2 | 45 | 21 | 0 | 0 | 0.37304 | 256000
1079 | 2 | 45 | 22 | 0 | 0 | 0.36638 | 256000
1080 | 2 | 45 | 23 | 0 | 0 | 0.32556 | 256000
1081 | 2 | 46 | 0 | 0 | 0 | 0.27627 | 256000
1082 | 2 | 46 | 1 | 0 | 0 | 0.25711 | 256000
1083 | 2 | 46 | 2 | 0 | 0 | 0.17369 | 256000
1084 | 2 | 46 | 3 | 0 | 0 | 0.13947 | 256000
1085 | 2 | 46 | 4 | 0 | 0 | 0.10577 | 256000
1086 | 2 | 46 | 5 | 0 | 0 | 0.1701 | 256000
1087 | 2 | 46 | 6 | 0 | 0 | 0.22618 | 256000
1088 | 2 | 46 | 7 | 1 | 0.14792 | 0.18174 | 255800
1089 | 2 | 46 | 8 | 1 | 0.49968 | 0.26844 | 255600
1090 | 2 | 46 | 9 | 0 | 0.87729 | 0.36027 | 255600
1091 | 2 | 46 | 10 | 0 | 1 | 0.44778 | 255600
1092 | 2 | 46 | 11 | 0 | 1 | 0.29565 | 255600
1093 | 2 | 46 | 12 | 0 | 1 | 0.34353 | 255600
1094 | 2 | 46 | 13 | 0 | 1 | 0.3836 | 255600
1095 | 2 | 46 | 14 | 0 | 1 | 0.34824 | 255600
1096 | 2 | 46 | 15 | 0 | 0.87729 | 0.47542 | 255600
1097 | 2 | 46 | 16 | 0 | 0.49968 | 0.52365 | 255600
1098 | 2 | 46 | 17 | 0 | 0.14792 | 0.51456 | 255600
1099 | 2 | 46 | 18 | 0 | 0 | 0.49331 | 255600
1100 | 2 | 46 | 19 | 1 | 0 | 0.37609 | 255400
1101 | 2 | 46 | 20 | 1 | 0 | 0.38243 | 255200
1102 | 2 | 46 | 21 | 0 | 0 | 0.29476 | 255200
1103 | 2 | 46 | 22 | 0 | 0 | 0.24824 | 255200
1104 | 2 | 46 | 23 | 0 | 0 | 0.24962 | 255200
1105 | 2 | 47 | 0 | 0 | 0 | 0.18362 | 255200
1106 | 2 | 47 | 1 | 0 | 0 | 0.2603 | 255200
1107 | 2 | 47 | 2 | 0 | 0 | 0.24955 | 255200
1108 | 2 | 47 | 3 | 0 | 0 | 0.15806 | 255200
1109 | 2 | 47 | 4 | 0 | 0 | 0.21509 | 255200
1110 | 2 | 47 | 5 | 0 | 0 | 0.32129 | 255200
1111 | 2 | 47 | 6 | 0 | 0 | 0.3361 | 255200
1112 | 2 | 47 | 7 | 1 | 0.11111 | 0.18141 | 255000
1113 | 2 | 47 | 8 | 1 | 0.37532 | 0.10869 | 254800
1114 | 2 | 47 | 9 | 0 | 0.65895 | 0.1624 | 254800
1115 | 2 | 47 | 10 | 0 | 0.90424 | 0.18641 | 254800
1116 | 2 | 47 | 11 | 0 | 1 | 0.17082 | 254800
1117 | 2 | 47 | 12 | 0 | 1 | 0.18801 | 254800
1118 | 2 | 47 | 13 | 0 | 1 | 0.17155 | 254800
1119 | 2 | 47 | 14 | 0 | 0.90424 | 0.11926 | 254800
1120 | 2 | 47 | 15 | 0 | 0.65895 | 0.11111 | 254800
1121 | 2 | 47 | 16 | 0 | 0.37532 | 0.099626 | 254800
1122 | 2 | 47 | 17 | 0 | 0.11111 | 0.1319 | 254800
1123 | 2 | 47 | 18 | 0 | 0 | 0.1879 | 254800
1124 | 2 | 47 | 19 | 1 | 0 | 0.2561 | 254600
1125 | 2 | 47 | 20 | 1 | 0 | 0.3514 | 254400
1126 | 2 | 47 | 21 | 0 | 0 | 0.4415 | 254400
1127 | 2 | 47 | 22 | 0 | 0 | 0.27931 | 254400
1128 | 2 | 47 | 23 | 0 | 0 | 0.45262 | 254400
1129 | 2 | 48 | 0 | 0 | 0 | 0.38144 | 254400
1130 | 2 | 48 | 1 | 0 | 0 | 0.36456 | 254400
1131 | 2 | 48 | 2 | 0 | 0 | 0.41717 | 254400
1132 | 2 | 48 | 3 | 0 | 0 | 0.63537 | 254400
1133 | 2 | 48 | 4 | 0 | 0 | 0.66546 | 254400
1134 | 2 | 48 | 5 | 0 | 0 | 0.99314 | 254400
1135 | 2 | 48 | 6 | 0 | 0 | 1 | 254400
1136 | 2 | 48 | 7 | 1 | 0.12347 | 0.71849 | 254200
1137 | 2 | 48 | 8 | 1 | 0.41707 | 0.63684 | 254000
1138 | 2 | 48 | 9 | 0 | 0.73225 | 0.44903 | 254000
1139 | 2 | 48 | 10 | 0 | 1 | 0.37311 | 254000
1140 | 2 | 48 | 11 | 0 | 1 | 0.36161 | 254000
1141 | 2 | 48 | 12 | 0 | 1 | 0.3195 | 254000
1142 | 2 | 48 | 13 | 0 | 1 | 0.4264 | 254000
1143 | 2 | 48 | 14 | 0 | 1 | 0.61441 | 254000
1144 | 2 | 48 | 15 | 0 | 0.73225 | 0.56748 | 254000
1145 | 2 | 48 | 16 | 0 | 0.41707 | 0.59881 | 254000
1146 | 2 | 48 | 17 | 0 | 0.12347 | 0.52179 | 254000
1147 | 2 | 48 | 18 | 0 | 0 | 0.44076 | 254000
1148 | 2 | 48 | 19 | 1 | 0 | 0.34486 | 253800
1149 | 2 | 48 | 20 | 1 | 0 | 0.28366 | 253600
1150 | 2 | 48 | 21 | 0 | 0 | 0.30692 | 253600
1151 | 2 | 48 | 22 | 0 | 0 | 0.2695 | 253600
1152 | 2 | 48 | 23 | 0 | 0 | 0.22408 | 253600
1153 | 2 | 49 | 0 | 0 | 0 | 0.17764 | 253600
1154 | 2 | 49 | 1 | 0 | 0 | 0.1307 | 253600
1155 | 2 | 49 | 2 | 0 | 0 | 0.12377 | 253600
1156 | 2 | 49 | 3 | 0 | 0 | 0.127 | 253600
1157 | 2 | 49 | 4 | 0 | 0 | 0.12696 | 253600
1158 | 2 | 49 | 5 | 0 | 0 | 0.17339 | 253600
1159 | 2 | 49 | 6 | 0 | 0 | 0.19325 | 253600
1160 | 2 | 49 | 7 | 1 | 0.14106 | 0.31293 | 253400
1161 | 2 | 49 | 8 | 1 | 0.4765 | 0.17636 | 253200
1162 | 2 | 49 | 9 | 0 | 0.8366 | 0.14118 | 253200
1163 | 2 | 49 | 10 | 0 | 1 | 0.12718 | 253200
1164 | 2 | 49 | 11 | 0 | 1 | 0.10087 | 253200
1165 | 2 | 49 | 12 | 0 | 1 | 0.16645 | 253200
1166 | 2 | 49 | 13 | 0 | 1 | 0.20084 | 253200
1167 | 2 | 49 | 14 | 0 | 1 | 0.14938 | 253200
1168 | 2 | 49 | 15 | 0 | 0.8366 | 0.11804 | 253200
1169 | 2 | 49 | 16 | 0 | 0.4765 | 0.083659 | 253200
1170 | 2 | 49 | 17 | 0 | 0.14106 | 0.051248 | 253200
1171 | 2 | 49 | 18 | 0 | 0 | 0.037056 | 253200
1172 | 2 | 49 | 19 | 1 | 0 | 0.031983 | 253000
1173 | 2 | 49 | 20 | 1 | 0 | 0.028438 | 252800
1174 | 2 | 49 | 21 | 0 | 0 | 0.027034 | 252800
1175 | 2 | 49 | 22 | 0 | 0 | 0.032446 | 252800
1176 | 2 | 49 | 23 | 0 | 0 | 0.054826 | 252800
1177 | 2 | 50 | 0 | 0 | 0 | 0.077477 | 252800
1178 | 2 | 50 | 1 | 0 | 0 | 0.084314 | 252800
1179 | 2 | 50 | 2 | 0 | 0 | 0.083375 | 252800
1180 | 2 | 50 | 3 | 0 | 0 | 0.12283 | 252800
1181 | 2 | 50 | 4 | 0 | 0 | 0.2078 | 252800
1182 | 2 | 50 | 5 | 0 | 0 | 0.21017 | 252800
1183 | 2 | 50 | 6 | 0 | 0 | 0.23339 | 252800
1184 | 2 | 50 | 7 | 1 | 0.13185 | 0.18509 | 252600
1185 | 2 | 50 | 8 | 1 | 0.44537 | 0.25975 | 252400
1186 | 2 | 50 | 9 | 0 | 0.78195 | 0.19031 | 252400
1187 | 2 | 50 | 10 | 0 | 1 | 0.17375 | 252400
1188 | 2 | 50 | 11 | 0 | 1 | 0.12749 | 252400
1189 | 2 | 50 | 12 | 0 | 1 | 0.16951 | 252400
1190 | 2 | 50 | 13 | 0 | 1 | 0.21318 | 252400
1191 | 2 | 50 | 14 | 0 | 1 | 0.14808 | 252400
1192 | 2 | 50 | 15 | 0 | 0.78195 | 0.17475 | 252400
1193 | 2 | 50 | 16 | 0 | 0.44537 | 0.19848 | 252400
1194 | 2 | 50 | 17 | 0 | 0.13185 | 0.18394 | 252400
1195 | 2 | 50 | 18 | 0 | 0 | 0.25783 | 252400
1196 | 2 | 50 | 19 | 1 | 0 | 0.2076 | 252200
1197 | 2 | 50 | 20 | 1 | 0 | 0.19861 | 252000
1198 | 2 | 50 | 21 | 0 | 0 | 0.24158 | 252000
1199 | 2 | 50 | 22 | 0 | 0 | 0.22748 | 252000
1200 | 2 | 50 | 23 | 0 | 0 | 0.26217 | 252000
1201 | 2 | 51 | 0 | 0 | 0 | 0.19911 | 252000
1202 | 2 | 51 | 1 | 0 | 0 | 0.24665 | 252000
1203 | 2 | 51 | 2 | 0 | 0 | 0.32429 | 252000
1204 | 2 | 51 | 3 | 0 | 0 | 0.24242 | 252000
1205 | 2 | 51 | 4 | 0 | 0 | 0.19822 | 252000
1206 | 2 | 51 | 5 | 0 | 0 | 0.16058 | 252000
1207 | 2 | 51 | 6 | 0 | 0 | 0.15081 | 252000
1208 | 2 | 51 | 7 | 1 | 0.13766 | 0.20488 | 251800
1209 | 2 | 51 | 8 | 1 | 0.46501 | 0.20303 | 251600
1210 | 2 | 51 | 9 | 0 | 0.81642 | 0.24253 | 251600
1211 | 2 | 51 | 10 | 0 | 1 | 0.30407 | 251600
1212 | 2 | 51 | 11 | 0 | 1 | 0.30784 | 251600
1213 | 2 | 51 | 12 | 0 | 1 | 0.28442 | 251600
1214 | 2 | 51 | 13 | 0 | 1 | 0.44746 | 251600
1215 | 2 | 51 | 14 | 0 | 1 | 0.47641 | 251600
1216 | 2 | 51 | 15 | 0 | 0.81642 | 0.59116 | 251600
1217 | 2 | 51 | 16 | 0 | 0.46501 | 0.55323 | 251600
1218 | 2 | 51 | 17 | 0 | 0.13766 | 0.56195 | 251600
1219 | 2 | 51 | 18 | 0 | 0 | 0.37353 | 251600
1220 | 2 | 51 | 19 | 1 | 0 | 0.44633 | 251400
1221 | 2 | 51 | 20 | 1 | 0 | 0.3689 | 251200
1222 | 2 | 51 | 21 | 0 | 0 | 0.37306 | 251200
1223 | 2 | 51 | 22 | 0 | 0 | 0.42717 | 251200
1224 | 2 | 51 | 23 | 0 | 0 | 0.31987 | 251200
1225 | 2 | 52 | 0 | 0 | 0 | 0.29867 | 251200
1226 | 2 | 52 | 1 | 0 | 0 | 0.28318 | 251200
1227 | 2 | 52 | 2 | 0 | 0 | 0.29158 | 251200
1228 | 2 | 52 | 3 | 0 | 0 | 0.30696 | 251200
1229 | 2 | 52 | 4 | 0 | 0 | 0.20905 | 251200
1230 | 2 | 52 | 5 | 0 | 0 | 0.12666 | 251200
1231 | 2 | 52 | 6 | 0 | 0 | 0.11736 | 251200
1232 | 2 | 52 | 7 | 1 | 0.11824 | 0.2132 | 251000
1233 | 2 | 52 | 8 | 1 | 0.39939 | 0.21386 | 250800
1234 | 2 | 52 | 9 | 0 | 0.70122 | 0.18579 | 250800
1235 | 2 | 52 | 10 | 0 | 0.96223 | 0.077877 | 250800
1236 | 2 | 52 | 11 | 0 | 1 | 0.087981 | 250800
1237 | 2 | 52 | 12 | 0 | 1 | 0.10647 | 250800
1238 | 2 | 52 | 13 | 0 | 1 | 0.1126 | 250800
1239 | 2 | 52 | 14 | 0 | 0.96223 | 0.10493 | 250800
1240 | 2 | 52 | 15 | 0 | 0.70122 | 0.10583 | 250800
1241 | 2 | 52 | 16 | 0 | 0.39939 | 0.12468 | 250800
1242 | 2 | 52 | 17 | 0 | 0.11824 | 0.093106 | 250800
1243 | 2 | 52 | 18 | 0 | 0 | 0.099935 | 250800
1244 | 2 | 52 | 19 | 1 | 0 | 0.12841 | 250600
1245 | 2 | 52 | 20 | 1 | 0 | 0.14217 | 250400
1246 | 2 | 52 | 21 | 0 | 0 | 0.16307 | 250400
1247 | 2 | 52 | 22 | 0 | 0 | 0.15444 | 250400
1248 | 2 | 52 | 23 | 0 | 0 | 0.15387 | 250400
1249 | 2 | 53 | 0 | 0 | 0 | 0.14238 | 250400
1250 | 2 | 53 | 1 | 0 | 0 | 0.12351 | 250400
1251 | 2 | 53 | 2 | 0 | 0 | 0.14364 | 250400
1252 | 2 | 53 | 3 | 0 | 0 | 0.17214 | 250400
1253 | 2 | 53 | 4 | 0 | 0 | 0.13998 | 250400
1254 | 2 | 53 | 5 | 0 | 0 | 0.13522 | 250400
1255 | 2 | 53 | 6 | 0 | 0 | 0.11969 | 250400
1256 | 2 | 53 | 7 | 1 | 0.099927 | 0.10873 | 250200
1257 | 2 | 53 | 8 | 1 | 0.33755 | 0.12513 | 250000
1258 | 2 | 53 | 9 | 0 | 0.59264 | 0.16237 | 250000
1259 | 2 | 53 | 10 | 0 | 0.81324 | 0.16592 | 250000
1260 | 2 | 53 | 11 | 0 | 0.96159 | 0.17462 | 250000
1261 | 2 | 53 | 12 | 0 | 1 | 0.15573 | 250000
1262 | 2 | 53 | 13 | 0 | 0.96159 | 0.11849 | 250000
1263 | 2 | 53 | 14 | 0 | 0.81324 | 0.17048 | 250000
1264 | 2 | 53 | 15 | 0 | 0.59264 | 0.17559 | 250000
1265 | 2 | 53 | 16 | 0 | 0.33755 | 0.12442 | 250000
1266 | 2 | 53 | 17 | 0 | 0.099927 | 0.10992 | 250000
1267 | 2 | 53 | 18 | 0 | 0 | 0.17844 | 250000
1268 | 2 | 53 | 19 | 1 | 0 | 0.18956 | 249800
1269 | 2 | 53 | 20 | 1 | 0 | 0.37074 | 249600
1270 | 2 | 53 | 21 | 0 | 0 | 0.38615 | 249600
1271 | 2 | 53 | 22 | 0 | 0 | 0.37478 | 249600
1272 | 2 | 53 | 23 | 0 | 0 | 0.33126 | 249600
1273 | 2 | 54 | 0 | 0 | 0 | 0.24361 | 249600
1274 | 2 | 54 | 1 | 0 | 0 | 0.28696 | 249600
1275 | 2 | 54 | 2 | 0 | 0 | 0.38689 | 249600
1276 | 2 | 54 | 3 | 0 | 0 | 0.43878 | 249600
1277 | 2 | 54 | 4 | 0 | 0 | 0.36237 | 249600
1278 | 2 | 54 | 5 | 0 | 0 | 0.49102 | 249600
1279 | 2 | 54 | 6 | 0 | 0 | 0.49765 | 249600
1280 | 2 | 54 | 7 | 1 | 0.14006 | 0.60199 | 249400
1281 | 2 | 54 | 8 | 1 | 0.47312 | 0.38849 | 249200
1282 | 2 | 54 | 9 | 0 | 0.83066 | 0.37979 | 249200
1283 | 2 | 54 | 10 | 0 | 1 | 0.31106 | 249200
1284 | 2 | 54 | 11 | 0 | 1 | 0.40437 | 249200
1285 | 2 | 54 | 12 | 0 | 1 | 0.44269 | 249200
1286 | 2 | 54 | 13 | 0 | 1 | 0.82494 | 249200
1287 | 2 | 54 | 14 | 0 | 1 | 0.97557 | 249200
1288 | 2 | 54 | 15 | 0 | 0.83066 | 1 | 249200
1289 | 2 | 54 | 16 | 0 | 0.47312 | 0.65149 | 249200
1290 | 2 | 54 | 17 | 0 | 0.14006 | 0.51837 | 249200
1291 | 2 | 54 | 18 | 0 | 0 | 0.52523 | 249200
1292 | 2 | 54 | 19 | 1 | 0 | 0.43982 | 249000
1293 | 2 | 54 | 20 | 1 | 0 | 0.3478 | 248800
1294 | 2 | 54 | 21 | 0 | 0 | 0.28356 | 248800
1295 | 2 | 54 | 22 | 0 | 0 | 0.21796 | 248800
1296 | 2 | 54 | 23 | 0 | 0 | 0.11445 | 248800
1297 | 2 | 55 | 0 | 0 | 0 | 0.098004 | 248800
1298 | 2 | 55 | 1 | 0 | 0 | 0.18776 | 248800
1299 | 2 | 55 | 2 | 0 | 0 | 0.2249 | 248800
1300 | 2 | 55 | 3 | 0 | 0 | 0.16191 | 248800
1301 | 2 | 55 | 4 | 0 | 0 | 0.19904 | 248800
1302 | 2 | 55 | 5 | 0 | 0 | 0.22671 | 248800
1303 | 2 | 55 | 6 | 0 | 0 | 0.30758 | 248800
1304 | 2 | 55 | 7 | 1 | 0.14446 | 0.37478 | 248600
1305 | 2 | 55 | 8 | 1 | 0.48799 | 0.31882 | 248400
1306 | 2 | 55 | 9 | 0 | 0.85677 | 0.2446 | 248400
1307 | 2 | 55 | 10 | 0 | 1 | 0.33132 | 248400
1308 | 2 | 55 | 11 | 0 | 1 | 0.22951 | 248400
1309 | 2 | 55 | 12 | 0 | 1 | 0.27611 | 248400
1310 | 2 | 55 | 13 | 0 | 1 | 0.26357 | 248400
1311 | 2 | 55 | 14 | 0 | 1 | 0.25375 | 248400
1312 | 2 | 55 | 15 | 0 | 0.85677 | 0.32682 | 248400
1313 | 2 | 55 | 16 | 0 | 0.48799 | 0.2311 | 248400
1314 | 2 | 55 | 17 | 0 | 0.14446 | 0.25211 | 248400
1315 | 2 | 55 | 18 | 0 | 0 | 0.25668 | 248400
1316 | 2 | 55 | 19 | 1 | 0 | 0.33069 | 248200
1317 | 2 | 55 | 20 | 1 | 0 | 0.30469 | 248000
1318 | 2 | 55 | 21 | 0 | 0 | 0.3884 | 248000
1319 | 2 | 55 | 22 | 0 | 0 | 0.41276 | 248000
1320 | 2 | 55 | 23 | 0 | 0 | 0.38573 | 248000
1321 | 2 | 56 | 0 | 0 | 0 | 0.34887 | 248000
1322 | 2 | 56 | 1 | 0 | 0 | 0.16779 | 248000
1323 | 2 | 56 | 2 | 0 | 0 | 0.18872 | 248000
1324 | 2 | 56 | 3 | 0 | 0 | 0.16161 | 248000
1325 | 2 | 56 | 4 | 0 | 0 | 0.20252 | 248000
1326 | 2 | 56 | 5 | 0 | 0 | 0.28488 | 248000
1327 | 2 | 56 | 6 | 0 | 0 | 0.22361 | 248000
1328 | 2 | 56 | 7 | 1 | 0.11809 | 0.17369 | 247800
1329 | 2 | 56 | 8 | 1 | 0.39891 | 0.17331 | 247600
1330 | 2 | 56 | 9 | 0 | 0.70038 | 0.17973 | 247600
1331 | 2 | 56 | 10 | 0 | 0.96108 | 0.27385 | 247600
1332 | 2 | 56 | 11 | 0 | 1 | 0.19816 | 247600
1333 | 2 | 56 | 12 | 0 | 1 | 0.18 | 247600
1334 | 2 | 56 | 13 | 0 | 1 | 0.17539 | 247600
1335 | 2 | 56 | 14 | 0 | 0.96108 | 0.24852 | 247600
1336 | 2 | 56 | 15 | 0 | 0.70038 | 0.23977 | 247600
1337 | 2 | 56 | 16 | 0 | 0.39891 | 0.28962 | 247600
1338 | 2 | 56 | 17 | 0 | 0.11809 | 0.24248 | 247600
1339 | 2 | 56 | 18 | 0 | 0 | 0.17649 | 247600
1340 | 2 | 56 | 19 | 1 | 0 | 0.17581 | 247400
1341 | 2 | 56 | 20 | 1 | 0 | 0.18105 | 247200
1342 | 2 | 56 | 21 | 0 | 0 | 0.18226 | 247200
1343 | 2 | 56 | 22 | 0 | 0 | 0.15976 | 247200
1344 | 2 | 56 | 23 | 0 | 0 | 0.18195 | 247200
1345 | 2 | 57 | 0 | 0 | 0 | 0.18594 | 247200
1346 | 2 | 57 | 1 | 0 | 0 | 0.14585 | 247200
1347 | 2 | 57 | 2 | 0 | 0 | 0.16402 | 247200
1348 | 2 | 57 | 3 | 0 | 0 | 0.16983 | 247200
1349 | 2 | 57 | 4 | 0 | 0 | 0.24296 | 247200
1350 | 2 | 57 | 5 | 0 | 0 | 0.19399 | 247200
1351 | 2 | 57 | 6 | 0 | 0 | 0.16353 | 247200
1352 | 2 | 57 | 7 | 1 | 0.11719 | 0.34748 | 247000
1353 | 2 | 57 | 8 | 1 | 0.39585 | 0.29785 | 246800
1354 | 2 | 57 | 9 | 0 | 0.695 | 0.2655 | 246800
1355 | 2 | 57 | 10 | 0 | 0.9537 | 0.23184 | 246800
1356 | 2 | 57 | 11 | 0 | 1 | 0.23313 | 246800
1357 | 2 | 57 | 12 | 0 | 1 | 0.26642 | 246800
1358 | 2 | 57 | 13 | 0 | 1 | 0.25749 | 246800
1359 | 2 | 57 | 14 | 0 | 0.9537 | 0.31968 | 246800
1360 | 2 | 57 | 15 | 0 | 0.695 | 0.42583 | 246800
1361 | 2 | 57 | 16 | 0 | 0.39585 | 0.37479 | 246800
1362 | 2 | 57 | 17 | 0 | 0.11719 | 0.36176 | 246800
1363 | 2 | 57 | 18 | 0 | 0 | 0.38542 | 246800
1364 | 2 | 57 | 19 | 1 | 0 | 0.28569 | 246600
1365 | 2 | 57 | 20 | 1 | 0 | 0.16527 | 246400
1366 | 2 | 57 | 21 | 0 | 0 | 0.13833 | 246400
1367 | 2 | 57 | 22 | 0 | 0 | 0.10822 | 246400
1368 | 2 | 57 | 23 | 0 | 0 | 0.10149 | 246400
1369 | 2 | 58 | 0 | 0 | 0 | 0.072129 | 246400
1370 | 2 | 58 | 1 | 0 | 0 | 0.082752 | 246400
1371 | 2 | 58 | 2 | 0 | 0 | 0.11409 | 246400
1372 | 2 | 58 | 3 | 0 | 0 | 0.094529 | 246400
1373 | 2 | 58 | 4 | 0 | 0 | 0.075192 | 246400
1374 | 2 | 58 | 5 | 0 | 0 | 0.073693 | 246400
1375 | 2 | 58 | 6 | 0 | 0 | 0.068342 | 246400
1376 | 2 | 58 | 7 | 1 | 0.13979 | 0.089842 | 246200
1377 | 2 | 58 | 8 | 1 | 0.4722 | 0.15345 | 246000
1378 | 2 | 58 | 9 | 0 | 0.82906 | 0.15855 | 246000
1379 | 2 | 58 | 10 | 0 | 1 | 0.1259 | 246000
1380 | 2 | 58 | 11 | 0 | 1 | 0.18479 | 246000
1381 | 2 | 58 | 12 | 0 | 1 | 0.16097 | 246000
1382 | 2 | 58 | 13 | 0 | 1 | 0.16815 | 246000
1383 | 2 | 58 | 14 | 0 | 1 | 0.14749 | 246000
1384 | 2 | 58 | 15 | 0 | 0.82906 | 0.16109 | 246000
1385 | 2 | 58 | 16 | 0 | 0.4722 | 0.13331 | 246000
1386 | 2 | 58 | 17 | 0 | 0.13979 | 0.092686 | 246000
1387 | 2 | 58 | 18 | 0 | 0 | 0.094948 | 246000
1388 | 2 | 58 | 19 | 1 | 0 | 0.076568 | 245800
1389 | 2 | 58 | 20 | 1 | 0 | 0.11791 | 245600
1390 | 2 | 58 | 21 | 0 | 0 | 0.092702 | 245600
1391 | 2 | 58 | 22 | 0 | 0 | 0.076501 | 245600
1392 | 2 | 58 | 23 | 0 | 0 | 0.087459 | 245600
1393 | 2 | 59 | 0 | 0 | 0 | 0.08143 | 245600
1394 | 2 | 59 | 1 | 0 | 0 | 0.065699 | 245600
1395 | 2 | 59 | 2 | 0 | 0 | 0.053743 | 245600
1396 | 2 | 59 | 3 | 0 | 0 | 0.074169 | 245600
1397 | 2 | 59 | 4 | 0 | 0 | 0.068664 | 245600
1398 | 2 | 59 | 5 | 0 | 0 | 0.061559 | 245600
1399 | 2 | 59 | 6 | 0 | 0 | 0.087762 | 245600
1400 | 2 | 59 | 7 | 1 | 0.14693 | 0.086613 | 245400
1401 | 2 | 59 | 8 | 1 | 0.49632 | 0.16275 | 245200
1402 | 2 | 59 | 9 | 0 | 0.8714 | 0.26668 | 245200
1403 | 2 | 59 | 10 | 0 | 1 | 0.29925 | 245200
1404 | 2 | 59 | 11 | 0 | 1 | 0.27032 | 245200
1405 | 2 | 59 | 12 | 0 | 1 | 0.34241 | 245200
1406 | 2 | 59 | 13 | 0 | 1 | 0.40898 | 245200
1407 | 2 | 59 | 14 | 0 | 1 | 0.28891 | 245200
1408 | 2 | 59 | 15 | 0 | 0.8714 | 0.33748 | 245200
1409 | 2 | 59 | 16 | 0 | 0.49632 | 0.2366 | 245200
1410 | 2 | 59 | 17 | 0 | 0.14693 | 0.24496 | 245200
1411 | 2 | 59 | 18 | 0 | 0 | 0.29186 | 245200
1412 | 2 | 59 | 19 | 1 | 0 | 0.3348 | 245000
1413 | 2 | 59 | 20 | 1 | 0 | 0.34931 | 244800
1414 | 2 | 59 | 21 | 0 | 0 | 0.29211 | 244800
1415 | 2 | 59 | 22 | 0 | 0 | 0.20384 | 244800
1416 | 2 | 59 | 23 | 0 | 0 | 0.17126 | 244800
1417 | 3 | 60 | 0 | 0 | 0 | 0.30861 | 244800
1418 | 3 | 60 | 1 | 0 | 0 | 0.22962 | 244800
1419 | 3 | 60 | 2 | 0 | 0 | 0.17615 | 244800
1420 | 3 | 60 | 3 | 0 | 0 | 0.20539 | 244800
1421 | 3 | 60 | 4 | 0 | 0 | 0.25204 | 244800
1422 | 3 | 60 | 5 | 0 | 0 | 0.31947 | 244800
1423 | 3 | 60 | 6 | 0 | 0 | 0.22489 | 244800
1424 | 3 | 60 | 7 | 1 | 0.24678 | 0.30064 | 244600
1425 | 3 | 60 | 8 | 1 | 0.6003 | 0.1671 | 244400
1426 | 3 | 60 | 9 | 0 | 0.95844 | 0.16906 | 244400
1427 | 3 | 60 | 10 | 0 | 1 | 0.27619 | 244400
1428 | 3 | 60 | 11 | 0 | 1 | 0.33185 | 244400
1429 | 3 | 60 | 12 | 0 | 1 | 0.37628 | 244400
1430 | 3 | 60 | 13 | 0 | 1 | 0.38943 | 244400
1431 | 3 | 60 | 14 | 0 | 1 | 0.50297 | 244400
1432 | 3 | 60 | 15 | 0 | 0.95844 | 0.34518 | 244400
1433 | 3 | 60 | 16 | 0 | 0.6003 | 0.52222 | 244400
1434 | 3 | 60 | 17 | 0 | 0.24678 | 0.45552 | 244400
1435 | 3 | 60 | 18 | 0 | 0 | 0.2224 | 244400
1436 | 3 | 60 | 19 | 1 | 0 | 0.18929 | 244200
1437 | 3 | 60 | 20 | 1 | 0 | 0.1346 | 244000
1438 | 3 | 60 | 21 | 0 | 0 | 0.17152 | 244000
1439 | 3 | 60 | 22 | 0 | 0 | 0.18582 | 244000
1440 | 3 | 60 | 23 | 0 | 0 | 0.134 | 244000
1441 | 3 | 61 | 0 | 0 | 0 | 0.14582 | 244000
1442 | 3 | 61 | 1 | 0 | 0 | 0.10688 | 244000
1443 | 3 | 61 | 2 | 0 | 0 | 0.092317 | 244000
1444 | 3 | 61 | 3 | 0 | 0 | 0.10867 | 244000
1445 | 3 | 61 | 4 | 0 | 0 | 0.063324 | 244000
1446 | 3 | 61 | 5 | 0 | 0 | 0.092465 | 244000
1447 | 3 | 61 | 6 | 0 | 0 | 0.089447 | 244000
1448 | 3 | 61 | 7 | 1 | 0.20991 | 0.082429 | 243800
1449 | 3 | 61 | 8 | 1 | 0.51061 | 0.1038 | 243600
1450 | 3 | 61 | 9 | 0 | 0.81524 | 0.11736 | 243600
1451 | 3 | 61 | 10 | 0 | 1 | 0.14903 | 243600
1452 | 3 | 61 | 11 | 0 | 1 | 0.12555 | 243600
1453 | 3 | 61 | 12 | 0 | 1 | 0.13995 | 243600
1454 | 3 | 61 | 13 | 0 | 1 | 0.22179 | 243600
1455 | 3 | 61 | 14 | 0 | 1 | 0.16923 | 243600
1456 | 3 | 61 | 15 | 0 | 0.81524 | 0.26021 | 243600
1457 | 3 | 61 | 16 | 0 | 0.51061 | 0.22207 | 243600
1458 | 3 | 61 | 17 | 0 | 0.20991 | 0.20791 | 243600
1459 | 3 | 61 | 18 | 0 | 0 | 0.20137 | 243600
1460 | 3 | 61 | 19 | 1 | 0 | 0.1529 | 243400
1461 | 3 | 61 | 20 | 1 | 0 | 0.27137 | 243200
1462 | 3 | 61 | 21 | 0 | 0 | 0.32647 | 243200
1463 | 3 | 61 | 22 | 0 | 0 | 0.56155 | 243200
1464 | 3 | 61 | 23 | 0 | 0 | 0.51534 | 243200
1465 | 3 | 62 | 0 | 0 | 0 | 0.38761 | 243200
1466 | 3 | 62 | 1 | 0 | 0 | 0.40801 | 243200
1467 | 3 | 62 | 2 | 0 | 0 | 0.33943 | 243200
1468 | 3 | 62 | 3 | 0 | 0 | 0.2199 | 243200
1469 | 3 | 62 | 4 | 0 | 0 | 0.23402 | 243200
1470 | 3 | 62 | 5 | 0 | 0 | 0.23624 | 243200
1471 | 3 | 62 | 6 | 0 | 0 | 0.45953 | 243200
1472 | 3 | 62 | 7 | 1 | 0.25093 | 0.27489 | 243000
1473 | 3 | 62 | 8 | 1 | 0.6104 | 0.28011 | 242800
1474 | 3 | 62 | 9 | 0 | 0.97457 | 0.39575 | 242800
1475 | 3 | 62 | 10 | 0 | 1 | 0.36984 | 242800
1476 | 3 | 62 | 11 | 0 | 1 | 0.39894 | 242800
1477 | 3 | 62 | 12 | 0 | 1 | 0.41494 | 242800
1478 | 3 | 62 | 13 | 0 | 1 | 0.41558 | 242800
1479 | 3 | 62 | 14 | 0 | 1 | 0.40234 | 242800
1480 | 3 | 62 | 15 | 0 | 0.97457 | 0.47659 | 242800
1481 | 3 | 62 | 16 | 0 | 0.6104 | 0.72578 | 242800
1482 | 3 | 62 | 17 | 0 | 0.25093 | 0.76085 | 242800
1483 | 3 | 62 | 18 | 0 | 0 | 0.87863 | 242800
1484 | 3 | 62 | 19 | 1 | 0 | 0.78039 | 242600
1485 | 3 | 62 | 20 | 1 | 0 | 0.93977 | 242400
1486 | 3 | 62 | 21 | 0 | 0 | 0.60686 | 242400
1487 | 3 | 62 | 22 | 0 | 0 | 0.56059 | 242400
1488 | 3 | 62 | 23 | 0 | 0 | 0.49731 | 242400
1489 | 3 | 63 | 0 | 0 | 0 | 0.49483 | 242400
1490 | 3 | 63 | 1 | 0 | 0 | 0.49677 | 242400
1491 | 3 | 63 | 2 | 0 | 0 | 0.41485 | 242400
1492 | 3 | 63 | 3 | 0 | 0 | 0.43703 | 242400
1493 | 3 | 63 | 4 | 0 | 0 | 0.5884 | 242400
1494 | 3 | 63 | 5 | 0 | 0 | 0.58179 | 242400
1495 | 3 | 63 | 6 | 0 | 0 | 0.49642 | 242400
1496 | 3 | 63 | 7 | 1 | 0.24021 | 0.66364 | 242200
1497 | 3 | 63 | 8 | 1 | 0.58432 | 0.54439 | 242000
1498 | 3 | 63 | 9 | 0 | 0.93293 | 0.5673 | 242000
1499 | 3 | 63 | 10 | 0 | 1 | 0.61094 | 242000
1500 | 3 | 63 | 11 | 0 | 1 | 0.53915 | 242000
1501 | 3 | 63 | 12 | 0 | 1 | 0.49926 | 242000
1502 | 3 | 63 | 13 | 0 | 1 | 0.40465 | 242000
1503 | 3 | 63 | 14 | 0 | 1 | 0.48608 | 242000
1504 | 3 | 63 | 15 | 0 | 0.93293 | 0.51097 | 242000
1505 | 3 | 63 | 16 | 0 | 0.58432 | 0.46534 | 242000
1506 | 3 | 63 | 17 | 0 | 0.24021 | 0.44788 | 242000
1507 | 3 | 63 | 18 | 0 | 0 | 0.44964 | 242000
1508 | 3 | 63 | 19 | 1 | 0 | 0.50287 | 241800
1509 | 3 | 63 | 20 | 1 | 0 | 0.47754 | 241600
1510 | 3 | 63 | 21 | 0 | 0 | 0.24 | 241600
1511 | 3 | 63 | 22 | 0 | 0 | 0.17983 | 241600
1512 | 3 | 63 | 23 | 0 | 0 | 0.15731 | 241600
1513 | 3 | 64 | 0 | 0 | 0 | 0.1319 | 241600
1514 | 3 | 64 | 1 | 0 | 0 | 0.15379 | 241600
1515 | 3 | 64 | 2 | 0 | 0 | 0.15683 | 241600
1516 | 3 | 64 | 3 | 0 | 0 | 0.15491 | 241600
1517 | 3 | 64 | 4 | 0 | 0 | 0.17395 | 241600
1518 | 3 | 64 | 5 | 0 | 0 | 0.26613 | 241600
1519 | 3 | 64 | 6 | 0 | 0 | 0.23627 | 241600
1520 | 3 | 64 | 7 | 1 | 0.27245 | 0.17425 | 241400
1521 | 3 | 64 | 8 | 1 | 0.66275 | 0.14757 | 241200
1522 | 3 | 64 | 9 | 0 | 1 | 0.24907 | 241200
1523 | 3 | 64 | 10 | 0 | 1 | 0.21292 | 241200
1524 | 3 | 64 | 11 | 0 | 1 | 0.22575 | 241200
1525 | 3 | 64 | 12 | 0 | 1 | 0.21004 | 241200
1526 | 3 | 64 | 13 | 0 | 1 | 0.16876 | 241200
1527 | 3 | 64 | 14 | 0 | 1 | 0.19416 | 241200
1528 | 3 | 64 | 15 | 0 | 1 | 0.14511 | 241200
1529 | 3 | 64 | 16 | 0 | 0.66275 | 0.18632 | 241200
1530 | 3 | 64 | 17 | 0 | 0.27245 | 0.23735 | 241200
1531 | 3 | 64 | 18 | 0 | 0 | 0.26399 | 241200
1532 | 3 | 64 | 19 | 1 | 0 | 0.26592 | 241000
1533 | 3 | 64 | 20 | 1 | 0 | 0.30592 | 240800
1534 | 3 | 64 | 21 | 0 | 0 | 0.31371 | 240800
1535 | 3 | 64 | 22 | 0 | 0 | 0.26862 | 240800
1536 | 3 | 64 | 23 | 0 | 0 | 0.26752 | 240800
1537 | 3 | 65 | 0 | 0 | 0 | 0.18702 | 240800
1538 | 3 | 65 | 1 | 0 | 0 | 0.175 | 240800
1539 | 3 | 65 | 2 | 0 | 0 | 0.20506 | 240800
1540 | 3 | 65 | 3 | 0 | 0 | 0.23788 | 240800
1541 | 3 | 65 | 4 | 0 | 0 | 0.22408 | 240800
1542 | 3 | 65 | 5 | 0 | 0 | 0.42012 | 240800
1543 | 3 | 65 | 6 | 0 | 0 | 0.4212 | 240800
1544 | 3 | 65 | 7 | 1 | 0.2754 | 0.3299 | 240600
1545 | 3 | 65 | 8 | 1 | 0.66994 | 0.39007 | 240400
1546 | 3 | 65 | 9 | 0 | 1 | 0.34639 | 240400
1547 | 3 | 65 | 10 | 0 | 1 | 0.23204 | 240400
1548 | 3 | 65 | 11 | 0 | 1 | 0.31603 | 240400
1549 | 3 | 65 | 12 | 0 | 1 | 0.24696 | 240400
1550 | 3 | 65 | 13 | 0 | 1 | 0.29288 | 240400
1551 | 3 | 65 | 14 | 0 | 1 | 0.32227 | 240400
1552 | 3 | 65 | 15 | 0 | 1 | 0.38891 | 240400
1553 | 3 | 65 | 16 | 0 | 0.66994 | 0.3601 | 240400
1554 | 3 | 65 | 17 | 0 | 0.2754 | 0.29799 | 240400
1555 | 3 | 65 | 18 | 0 | 0 | 0.19485 | 240400
1556 | 3 | 65 | 19 | 1 | 0 | 0.1631 | 240200
1557 | 3 | 65 | 20 | 1 | 0 | 0.16025 | 240000
1558 | 3 | 65 | 21 | 0 | 0 | 0.22406 | 240000
1559 | 3 | 65 | 22 | 0 | 0 | 0.16248 | 240000
1560 | 3 | 65 | 23 | 0 | 0 | 0.12262 | 240000
1561 | 3 | 66 | 0 | 0 | 0 | 0.12218 | 240000
1562 | 3 | 66 | 1 | 0 | 0 | 0.17142 | 240000
1563 | 3 | 66 | 2 | 0 | 0 | 0.21142 | 240000
1564 | 3 | 66 | 3 | 0 | 0 | 0.24638 | 240000
1565 | 3 | 66 | 4 | 0 | 0 | 0.28607 | 240000
1566 | 3 | 66 | 5 | 0 | 0 | 0.31174 | 240000
1567 | 3 | 66 | 6 | 0 | 0 | 0.24716 | 240000
1568 | 3 | 66 | 7 | 1 | 0.24467 | 0.25197 | 239800
1569 | 3 | 66 | 8 | 1 | 0.59518 | 0.32718 | 239600
1570 | 3 | 66 | 9 | 0 | 0.95026 | 0.33316 | 239600
1571 | 3 | 66 | 10 | 0 | 1 | 0.31562 | 239600
1572 | 3 | 66 | 11 | 0 | 1 | 0.27718 | 239600
1573 | 3 | 66 | 12 | 0 | 1 | 0.21973 | 239600
1574 | 3 | 66 | 13 | 0 | 1 | 0.18697 | 239600
1575 | 3 | 66 | 14 | 0 | 1 | 0.22462 | 239600
1576 | 3 | 66 | 15 | 0 | 0.95026 | 0.29399 | 239600
1577 | 3 | 66 | 16 | 0 | 0.59518 | 0.30788 | 239600
1578 | 3 | 66 | 17 | 0 | 0.24467 | 0.37643 | 239600
1579 | 3 | 66 | 18 | 0 | 0 | 0.26785 | 239600
1580 | 3 | 66 | 19 | 1 | 0 | 0.30224 | 239400
1581 | 3 | 66 | 20 | 1 | 0 | 0.45637 | 239200
1582 | 3 | 66 | 21 | 0 | 0 | 0.34715 | 239200
1583 | 3 | 66 | 22 | 0 | 0 | 0.27226 | 239200
1584 | 3 | 66 | 23 | 0 | 0 | 0.33513 | 239200
1585 | 3 | 67 | 0 | 0 | 0 | 0.2033 | 239200
1586 | 3 | 67 | 1 | 0 | 0 | 0.2163 | 239200
1587 | 3 | 67 | 2 | 0 | 0 | 0.25018 | 239200
1588 | 3 | 67 | 3 | 0 | 0 | 0.18724 | 239200
1589 | 3 | 67 | 4 | 0 | 0 | 0.18808 | 239200
1590 | 3 | 67 | 5 | 0 | 0 | 0.25781 | 239200
1591 | 3 | 67 | 6 | 0 | 0 | 0.29682 | 239200
1592 | 3 | 67 | 7 | 1 | 0.23969 | 0.3114 | 239000
1593 | 3 | 67 | 8 | 1 | 0.58306 | 0.29685 | 238800
1594 | 3 | 67 | 9 | 0 | 0.9309 | 0.37789 | 238800
1595 | 3 | 67 | 10 | 0 | 1 | 0.51911 | 238800
1596 | 3 | 67 | 11 | 0 | 1 | 0.39615 | 238800
1597 | 3 | 67 | 12 | 0 | 1 | 0.30693 | 238800
1598 | 3 | 67 | 13 | 0 | 1 | 0.44279 | 238800
1599 | 3 | 67 | 14 | 0 | 1 | 0.49006 | 238800
1600 | 3 | 67 | 15 | 0 | 0.9309 | 0.57294 | 238800
1601 | 3 | 67 | 16 | 0 | 0.58306 | 0.67535 | 238800
1602 | 3 | 67 | 17 | 0 | 0.23969 | 0.59128 | 238800
1603 | 3 | 67 | 18 | 0 | 0 | 0.81878 | 238800
1604 | 3 | 67 | 19 | 1 | 0 | 0.91535 | 238600
1605 | 3 | 67 | 20 | 1 | 0 | 0.91766 | 238400
1606 | 3 | 67 | 21 | 0 | 0 | 0.65399 | 238400
1607 | 3 | 67 | 22 | 0 | 0 | 0.34182 | 238400
1608 | 3 | 67 | 23 | 0 | 0 | 0.39678 | 238400
1609 | 3 | 68 | 0 | 0 | 0 | 0.55579 | 238400
1610 | 3 | 68 | 1 | 0 | 0 | 0.45668 | 238400
1611 | 3 | 68 | 2 | 0 | 0 | 0.526 | 238400
1612 | 3 | 68 | 3 | 0 | 0 | 0.51309 | 238400
1613 | 3 | 68 | 4 | 0 | 0 | 0.61746 | 238400
1614 | 3 | 68 | 5 | 0 | 0 | 0.67329 | 238400
1615 | 3 | 68 | 6 | 0 | 0 | 0.64997 | 238400
1616 | 3 | 68 | 7 | 1 | 0.25018 | 0.90922 | 238200
1617 | 3 | 68 | 8 | 1 | 0.60857 | 0.74644 | 238000
1618 | 3 | 68 | 9 | 0 | 0.97164 | 0.66644 | 238000
1619 | 3 | 68 | 10 | 0 | 1 | 1 | 238000
1620 | 3 | 68 | 11 | 0 | 1 | 0.95897 | 238000
1621 | 3 | 68 | 12 | 0 | 1 | 1 | 238000
1622 | 3 | 68 | 13 | 0 | 1 | 1 | 238000
1623 | 3 | 68 | 14 | 0 | 1 | 1 | 238000
1624 | 3 | 68 | 15 | 0 | 0.97164 | 1 | 238000
1625 | 3 | 68 | 16 | 0 | 0.60857 | 0.64913 | 238000
1626 | 3 | 68 | 17 | 0 | 0.25018 | 0.66116 | 238000
1627 | 3 | 68 | 18 | 0 | 0 | 0.51985 | 238000
1628 | 3 | 68 | 19 | 1 | 0 | 0.5591 | 237800
1629 | 3 | 68 | 20 | 1 | 0 | 0.44098 | 237600
1630 | 3 | 68 | 21 | 0 | 0 | 0.31318 | 237600
1631 | 3 | 68 | 22 | 0 | 0 | 0.30738 | 237600
1632 | 3 | 68 | 23 | 0 | 0 | 0.26795 | 237600
1633 | 3 | 69 | 0 | 0 | 0 | 0.24835 | 237600
1634 | 3 | 69 | 1 | 0 | 0 | 0.30583 | 237600
1635 | 3 | 69 | 2 | 0 | 0 | 0.19974 | 237600
1636 | 3 | 69 | 3 | 0 | 0 | 0.15417 | 237600
1637 | 3 | 69 | 4 | 0 | 0 | 0.18158 | 237600
1638 | 3 | 69 | 5 | 0 | 0 | 0.16936 | 237600
1639 | 3 | 69 | 6 | 0 | 0 | 0.18867 | 237600
1640 | 3 | 69 | 7 | 1 | 0.19152 | 0.21254 | 237400
1641 | 3 | 69 | 8 | 1 | 0.46588 | 0.20875 | 237200
1642 | 3 | 69 | 9 | 0 | 0.74382 | 0.18305 | 237200
1643 | 3 | 69 | 10 | 0 | 0.97798 | 0.25461 | 237200
1644 | 3 | 69 | 11 | 0 | 1 | 0.18163 | 237200
1645 | 3 | 69 | 12 | 0 | 1 | 0.21722 | 237200
1646 | 3 | 69 | 13 | 0 | 1 | 0.36329 | 237200
1647 | 3 | 69 | 14 | 0 | 0.97798 | 0.2631 | 237200
1648 | 3 | 69 | 15 | 0 | 0.74382 | 0.17883 | 237200
1649 | 3 | 69 | 16 | 0 | 0.46588 | 0.20507 | 237200
1650 | 3 | 69 | 17 | 0 | 0.19152 | 0.22923 | 237200
1651 | 3 | 69 | 18 | 0 | 0 | 0.35209 | 237200
1652 | 3 | 69 | 19 | 1 | 0 | 0.22753 | 237000
1653 | 3 | 69 | 20 | 1 | 0 | 0.18904 | 236800
1654 | 3 | 69 | 21 | 0 | 0 | 0.23867 | 236800
1655 | 3 | 69 | 22 | 0 | 0 | 0.24658 | 236800
1656 | 3 | 69 | 23 | 0 | 0 | 0.21599 | 236800
1657 | 3 | 70 | 0 | 0 | 0 | 0.26549 | 236800
1658 | 3 | 70 | 1 | 0 | 0 | 0.32899 | 236800
1659 | 3 | 70 | 2 | 0 | 0 | 0.24798 | 236800
1660 | 3 | 70 | 3 | 0 | 0 | 0.20573 | 236800
1661 | 3 | 70 | 4 | 0 | 0 | 0.17586 | 236800
1662 | 3 | 70 | 5 | 0 | 0 | 0.21733 | 236800
1663 | 3 | 70 | 6 | 0 | 0 | 0.18539 | 236800
1664 | 3 | 70 | 7 | 1 | 0.26177 | 0.15004 | 236600
1665 | 3 | 70 | 8 | 1 | 0.63677 | 0.154 | 236400
1666 | 3 | 70 | 9 | 0 | 1 | 0.14163 | 236400
1667 | 3 | 70 | 10 | 0 | 1 | 0.15448 | 236400
1668 | 3 | 70 | 11 | 0 | 1 | 0.24773 | 236400
1669 | 3 | 70 | 12 | 0 | 1 | 0.23471 | 236400
1670 | 3 | 70 | 13 | 0 | 1 | 0.22482 | 236400
1671 | 3 | 70 | 14 | 0 | 1 | 0.18715 | 236400
1672 | 3 | 70 | 15 | 0 | 1 | 0.17441 | 236400
1673 | 3 | 70 | 16 | 0 | 0.63677 | 0.26505 | 236400
1674 | 3 | 70 | 17 | 0 | 0.26177 | 0.34151 | 236400
1675 | 3 | 70 | 18 | 0 | 0 | 0.28164 | 236400
1676 | 3 | 70 | 19 | 1 | 0 | 0.24334 | 236200
1677 | 3 | 70 | 20 | 1 | 0 | 0.23864 | 236000
1678 | 3 | 70 | 21 | 0 | 0 | 0.32367 | 236000
1679 | 3 | 70 | 22 | 0 | 0 | 0.3733 | 236000
1680 | 3 | 70 | 23 | 0 | 0 | 0.57617 | 236000
1681 | 3 | 71 | 0 | 0 | 0 | 0.48285 | 236000
1682 | 3 | 71 | 1 | 0 | 0 | 0.37701 | 236000
1683 | 3 | 71 | 2 | 0 | 0 | 0.43316 | 236000
1684 | 3 | 71 | 3 | 0 | 0 | 0.33488 | 236000
1685 | 3 | 71 | 4 | 0 | 0 | 0.56541 | 236000
1686 | 3 | 71 | 5 | 0 | 0 | 0.57724 | 236000
1687 | 3 | 71 | 6 | 0 | 0 | 0.5076 | 236000
1688 | 3 | 71 | 7 | 1 | 0.23125 | 0.3891 | 235800
1689 | 3 | 71 | 8 | 1 | 0.56253 | 0.36009 | 235600
1690 | 3 | 71 | 9 | 0 | 0.89813 | 0.31061 | 235600
1691 | 3 | 71 | 10 | 0 | 1 | 0.35878 | 235600
1692 | 3 | 71 | 11 | 0 | 1 | 0.48209 | 235600
1693 | 3 | 71 | 12 | 0 | 1 | 0.50132 | 235600
1694 | 3 | 71 | 13 | 0 | 1 | 0.5214 | 235600
1695 | 3 | 71 | 14 | 0 | 1 | 0.85447 | 235600
1696 | 3 | 71 | 15 | 0 | 0.89813 | 1 | 235600
1697 | 3 | 71 | 16 | 0 | 0.56253 | 1 | 235600
1698 | 3 | 71 | 17 | 0 | 0.23125 | 0.9603 | 235600
1699 | 3 | 71 | 18 | 0 | 0 | 1 | 235600
1700 | 3 | 71 | 19 | 1 | 0 | 0.86176 | 235400
1701 | 3 | 71 | 20 | 1 | 0 | 0.57067 | 235200
1702 | 3 | 71 | 21 | 0 | 0 | 0.36374 | 235200
1703 | 3 | 71 | 22 | 0 | 0 | 0.45814 | 235200
1704 | 3 | 71 | 23 | 0 | 0 | 0.36441 | 235200
1705 | 3 | 72 | 0 | 0 | 0 | 0.31928 | 235200
1706 | 3 | 72 | 1 | 0 | 0 | 0.28333 | 235200
1707 | 3 | 72 | 2 | 0 | 0 | 0.20872 | 235200
1708 | 3 | 72 | 3 | 0 | 0 | 0.26573 | 235200
1709 | 3 | 72 | 4 | 0 | 0 | 0.24626 | 235200
1710 | 3 | 72 | 5 | 0 | 0 | 0.25906 | 235200
1711 | 3 | 72 | 6 | 0 | 0 | 0.22119 | 235200
1712 | 3 | 72 | 7 | 1 | 0.22337 | 0.16528 | 235000
1713 | 3 | 72 | 8 | 1 | 0.54337 | 0.21767 | 234800
1714 | 3 | 72 | 9 | 0 | 0.86754 | 0.16185 | 234800
1715 | 3 | 72 | 10 | 0 | 1 | 0.14286 | 234800
1716 | 3 | 72 | 11 | 0 | 1 | 0.1461 | 234800
1717 | 3 | 72 | 12 | 0 | 1 | 0.17509 | 234800
1718 | 3 | 72 | 13 | 0 | 1 | 0.161 | 234800
1719 | 3 | 72 | 14 | 0 | 1 | 0.23748 | 234800
1720 | 3 | 72 | 15 | 0 | 0.86754 | 0.22338 | 234800
1721 | 3 | 72 | 16 | 0 | 0.54337 | 0.26751 | 234800
1722 | 3 | 72 | 17 | 0 | 0.22337 | 0.19052 | 234800
1723 | 3 | 72 | 18 | 0 | 0 | 0.19589 | 234800
1724 | 3 | 72 | 19 | 1 | 0 | 0.15332 | 234600
1725 | 3 | 72 | 20 | 1 | 0 | 0.14946 | 234400
1726 | 3 | 72 | 21 | 0 | 0 | 0.195 | 234400
1727 | 3 | 72 | 22 | 0 | 0 | 0.1748 | 234400
1728 | 3 | 72 | 23 | 0 | 0 | 0.21968 | 234400
1729 | 3 | 73 | 0 | 0 | 0 | 0.16666 | 234400
1730 | 3 | 73 | 1 | 0 | 0 | 0.0976 | 234400
1731 | 3 | 73 | 2 | 0 | 0 | 0.16739 | 234400
1732 | 3 | 73 | 3 | 0 | 0 | 0.30428 | 234400
1733 | 3 | 73 | 4 | 0 | 0 | 0.30469 | 234400
1734 | 3 | 73 | 5 | 0 | 0 | 0.45931 | 234400
1735 | 3 | 73 | 6 | 0 | 0 | 0.6962 | 234400
1736 | 3 | 73 | 7 | 1 | 0.23646 | 0.53832 | 234200
1737 | 3 | 73 | 8 | 1 | 0.5752 | 0.38066 | 234000
1738 | 3 | 73 | 9 | 0 | 0.91836 | 0.43187 | 234000
1739 | 3 | 73 | 10 | 0 | 1 | 0.29833 | 234000
1740 | 3 | 73 | 11 | 0 | 1 | 0.27074 | 234000
1741 | 3 | 73 | 12 | 0 | 1 | 0.19628 | 234000
1742 | 3 | 73 | 13 | 0 | 1 | 0.21113 | 234000
1743 | 3 | 73 | 14 | 0 | 1 | 0.18695 | 234000
1744 | 3 | 73 | 15 | 0 | 0.91836 | 0.19702 | 234000
1745 | 3 | 73 | 16 | 0 | 0.5752 | 0.19496 | 234000
1746 | 3 | 73 | 17 | 0 | 0.23646 | 0.20424 | 234000
1747 | 3 | 73 | 18 | 0 | 0 | 0.24719 | 234000
1748 | 3 | 73 | 19 | 1 | 0 | 0.39359 | 233800
1749 | 3 | 73 | 20 | 1 | 0 | 0.3372 | 233600
1750 | 3 | 73 | 21 | 0 | 0 | 0.32604 | 233600
1751 | 3 | 73 | 22 | 0 | 0 | 0.34998 | 233600
1752 | 3 | 73 | 23 | 0 | 0 | 0.46557 | 233600
1753 | 3 | 74 | 0 | 0 | 0 | 0.5515 | 233600
1754 | 3 | 74 | 1 | 0 | 0 | 0.36908 | 233600
1755 | 3 | 74 | 2 | 0 | 0 | 0.25647 | 233600
1756 | 3 | 74 | 3 | 0 | 0 | 0.34799 | 233600
1757 | 3 | 74 | 4 | 0 | 0 | 0.4585 | 233600
1758 | 3 | 74 | 5 | 0 | 0 | 0.4454 | 233600
1759 | 3 | 74 | 6 | 0 | 0 | 0.65795 | 233600
1760 | 3 | 74 | 7 | 1 | 0.22564 | 0.54625 | 233400
1761 | 3 | 74 | 8 | 1 | 0.54887 | 0.39764 | 233200
1762 | 3 | 74 | 9 | 0 | 0.87633 | 0.45725 | 233200
1763 | 3 | 74 | 10 | 0 | 1 | 0.39537 | 233200
1764 | 3 | 74 | 11 | 0 | 1 | 0.35022 | 233200
1765 | 3 | 74 | 12 | 0 | 1 | 0.24855 | 233200
1766 | 3 | 74 | 13 | 0 | 1 | 0.26888 | 233200
1767 | 3 | 74 | 14 | 0 | 1 | 0.34863 | 233200
1768 | 3 | 74 | 15 | 0 | 0.87633 | 0.25816 | 233200
1769 | 3 | 74 | 16 | 0 | 0.54887 | 0.17486 | 233200
1770 | 3 | 74 | 17 | 0 | 0.22564 | 0.16443 | 233200
1771 | 3 | 74 | 18 | 0 | 0 | 0.14694 | 233200
1772 | 3 | 74 | 19 | 1 | 0 | 0.23106 | 233000
1773 | 3 | 74 | 20 | 1 | 0 | 0.22761 | 232800
1774 | 3 | 74 | 21 | 0 | 0 | 0.28059 | 232800
1775 | 3 | 74 | 22 | 0 | 0 | 0.26314 | 232800
1776 | 3 | 74 | 23 | 0 | 0 | 0.21486 | 232800
1777 | 3 | 75 | 0 | 0 | 0 | 0.30594 | 232800
1778 | 3 | 75 | 1 | 0 | 0 | 0.29689 | 232800
1779 | 3 | 75 | 2 | 0 | 0 | 0.27785 | 232800
1780 | 3 | 75 | 3 | 0 | 0 | 0.32126 | 232800
1781 | 3 | 75 | 4 | 0 | 0 | 0.54664 | 232800
1782 | 3 | 75 | 5 | 0 | 0 | 0.38164 | 232800
1783 | 3 | 75 | 6 | 0 | 0 | 0.39977 | 232800
1784 | 3 | 75 | 7 | 1 | 0.21071 | 0.4326 | 232600
1785 | 3 | 75 | 8 | 1 | 0.51256 | 0.35744 | 232400
1786 | 3 | 75 | 9 | 0 | 0.81836 | 0.35652 | 232400
1787 | 3 | 75 | 10 | 0 | 1 | 0.64766 | 232400
1788 | 3 | 75 | 11 | 0 | 1 | 1 | 232400
1789 | 3 | 75 | 12 | 0 | 1 | 1 | 232400
1790 | 3 | 75 | 13 | 0 | 1 | 1 | 232400
1791 | 3 | 75 | 14 | 0 | 1 | 0.69047 | 232400
1792 | 3 | 75 | 15 | 0 | 0.81836 | 0.70515 | 232400
1793 | 3 | 75 | 16 | 0 | 0.51256 | 1 | 232400
1794 | 3 | 75 | 17 | 0 | 0.21071 | 0.98814 | 232400
1795 | 3 | 75 | 18 | 0 | 0 | 1 | 232400
1796 | 3 | 75 | 19 | 1 | 0 | 0.87134 | 232200
1797 | 3 | 75 | 20 | 1 | 0 | 0.83902 | 232000
1798 | 3 | 75 | 21 | 0 | 0 | 0.97493 | 232000
1799 | 3 | 75 | 22 | 0 | 0 | 0.95377 | 232000
1800 | 3 | 75 | 23 | 0 | 0 | 1 | 232000
1801 | 3 | 76 | 0 | 0 | 0 | 0.73091 | 232000
1802 | 3 | 76 | 1 | 0 | 0 | 0.66388 | 232000
1803 | 3 | 76 | 2 | 0 | 0 | 0.60381 | 232000
1804 | 3 | 76 | 3 | 0 | 0 | 0.4254 | 232000
1805 | 3 | 76 | 4 | 0 | 0 | 0.39243 | 232000
1806 | 3 | 76 | 5 | 0 | 0 | 0.43097 | 232000
1807 | 3 | 76 | 6 | 0 | 0 | 0.53785 | 232000
1808 | 3 | 76 | 7 | 1 | 0.22402 | 0.55285 | 231800
1809 | 3 | 76 | 8 | 1 | 0.54495 | 0.94194 | 231600
1810 | 3 | 76 | 9 | 0 | 0.87006 | 0.60207 | 231600
1811 | 3 | 76 | 10 | 0 | 1 | 0.80041 | 231600
1812 | 3 | 76 | 11 | 0 | 1 | 0.99443 | 231600
1813 | 3 | 76 | 12 | 0 | 1 | 1 | 231600
1814 | 3 | 76 | 13 | 0 | 1 | 1 | 231600
1815 | 3 | 76 | 14 | 0 | 1 | 1 | 231600
1816 | 3 | 76 | 15 | 0 | 0.87006 | 1 | 231600
1817 | 3 | 76 | 16 | 0 | 0.54495 | 0.90997 | 231600
1818 | 3 | 76 | 17 | 0 | 0.22402 | 0.98602 | 231600
1819 | 3 | 76 | 18 | 0 | 0 | 0.79888 | 231600
1820 | 3 | 76 | 19 | 1 | 0 | 0.90807 | 231400
1821 | 3 | 76 | 20 | 1 | 0 | 0.79822 | 231200
1822 | 3 | 76 | 21 | 0 | 0 | 0.61536 | 231200
1823 | 3 | 76 | 22 | 0 | 0 | 0.7696 | 231200
1824 | 3 | 76 | 23 | 0 | 0 | 0.6021 | 231200
1825 | 3 | 77 | 0 | 0 | 0 | 0.60884 | 231200
1826 | 3 | 77 | 1 | 0 | 0 | 0.85003 | 231200
1827 | 3 | 77 | 2 | 0 | 0 | 0.63695 | 231200
1828 | 3 | 77 | 3 | 0 | 0 | 0.87929 | 231200
1829 | 3 | 77 | 4 | 0 | 0 | 0.62838 | 231200
1830 | 3 | 77 | 5 | 0 | 0 | 0.69269 | 231200
1831 | 3 | 77 | 6 | 0 | 0 | 0.45789 | 231200
1832 | 3 | 77 | 7 | 1 | 0.23901 | 0.37216 | 231000
1833 | 3 | 77 | 8 | 1 | 0.58142 | 0.47523 | 230800
1834 | 3 | 77 | 9 | 0 | 0.92829 | 0.62589 | 230800
1835 | 3 | 77 | 10 | 0 | 1 | 0.60689 | 230800
1836 | 3 | 77 | 11 | 0 | 1 | 0.42211 | 230800
1837 | 3 | 77 | 12 | 0 | 1 | 0.40183 | 230800
1838 | 3 | 77 | 13 | 0 | 1 | 0.43485 | 230800
1839 | 3 | 77 | 14 | 0 | 1 | 0.31006 | 230800
1840 | 3 | 77 | 15 | 0 | 0.92829 | 0.35783 | 230800
1841 | 3 | 77 | 16 | 0 | 0.58142 | 0.27587 | 230800
1842 | 3 | 77 | 17 | 0 | 0.23901 | 0.28072 | 230800
1843 | 3 | 77 | 18 | 0 | 0 | 0.42869 | 230800
1844 | 3 | 77 | 19 | 1 | 0 | 0.46743 | 230600
1845 | 3 | 77 | 20 | 1 | 0 | 0.66717 | 230400
1846 | 3 | 77 | 21 | 0 | 0 | 0.62038 | 230400
1847 | 3 | 77 | 22 | 0 | 0 | 0.4689 | 230400
1848 | 3 | 77 | 23 | 0 | 0 | 0.37152 | 230400
1849 | 3 | 78 | 0 | 0 | 0 | 0.35257 | 230400
1850 | 3 | 78 | 1 | 0 | 0 | 0.24445 | 230400
1851 | 3 | 78 | 2 | 0 | 0 | 0.25849 | 230400
1852 | 3 | 78 | 3 | 0 | 0 | 0.29371 | 230400
1853 | 3 | 78 | 4 | 0 | 0 | 0.2646 | 230400
1854 | 3 | 78 | 5 | 0 | 0 | 0.24199 | 230400
1855 | 3 | 78 | 6 | 0 | 0 | 0.17056 | 230400
1856 | 3 | 78 | 7 | 1 | 0.2443 | 0.22049 | 230200
1857 | 3 | 78 | 8 | 1 | 0.59428 | 0.34059 | 230000
1858 | 3 | 78 | 9 | 0 | 0.94882 | 0.39036 | 230000
1859 | 3 | 78 | 10 | 0 | 1 | 0.4864 | 230000
1860 | 3 | 78 | 11 | 0 | 1 | 0.52073 | 230000
1861 | 3 | 78 | 12 | 0 | 1 | 0.55674 | 230000
1862 | 3 | 78 | 13 | 0 | 1 | 0.48506 | 230000
1863 | 3 | 78 | 14 | 0 | 1 | 0.44022 | 230000
1864 | 3 | 78 | 15 | 0 | 0.94882 | 0.36547 | 230000
1865 | 3 | 78 | 16 | 0 | 0.59428 | 0.44653 | 230000
1866 | 3 | 78 | 17 | 0 | 0.2443 | 0.32566 | 230000
1867 | 3 | 78 | 18 | 0 | 0 | 0.26217 | 230000
1868 | 3 | 78 | 19 | 1 | 0 | 0.25028 | 229800
1869 | 3 | 78 | 20 | 1 | 0 | 0.1884 | 229600
1870 | 3 | 78 | 21 | 0 | 0 | 0.21687 | 229600
1871 | 3 | 78 | 22 | 0 | 0 | 0.2012 | 229600
1872 | 3 | 78 | 23 | 0 | 0 | 0.23923 | 229600
1873 | 3 | 79 | 0 | 0 | 0 | 0.20734 | 229600
1874 | 3 | 79 | 1 | 0 | 0 | 0.1433 | 229600
1875 | 3 | 79 | 2 | 0 | 0 | 0.1374 | 229600
1876 | 3 | 79 | 3 | 0 | 0 | 0.1393 | 229600
1877 | 3 | 79 | 4 | 0 | 0 | 0.13532 | 229600
1878 | 3 | 79 | 5 | 0 | 0 | 0.13366 | 229600
1879 | 3 | 79 | 6 | 0 | 0 | 0.15374 | 229600
1880 | 3 | 79 | 7 | 1 | 0.22752 | 0.18116 | 229400
1881 | 3 | 79 | 8 | 1 | 0.55346 | 0.32543 | 229200
1882 | 3 | 79 | 9 | 0 | 0.88365 | 0.38258 | 229200
1883 | 3 | 79 | 10 | 0 | 1 | 0.58703 | 229200
1884 | 3 | 79 | 11 | 0 | 1 | 0.87229 | 229200
1885 | 3 | 79 | 12 | 0 | 1 | 1 | 229200
1886 | 3 | 79 | 13 | 0 | 1 | 0.97023 | 229200
1887 | 3 | 79 | 14 | 0 | 1 | 0.68045 | 229200
1888 | 3 | 79 | 15 | 0 | 0.88365 | 0.69023 | 229200
1889 | 3 | 79 | 16 | 0 | 0.55346 | 0.70303 | 229200
1890 | 3 | 79 | 17 | 0 | 0.22752 | 1 | 229200
1891 | 3 | 79 | 18 | 0 | 0 | 0.8437 | 229200
1892 | 3 | 79 | 19 | 1 | 0 | 0.53904 | 229000
1893 | 3 | 79 | 20 | 1 | 0 | 0.46726 | 228800
1894 | 3 | 79 | 21 | 0 | 0 | 0.32247 | 228800
1895 | 3 | 79 | 22 | 0 | 0 | 0.34523 | 228800
1896 | 3 | 79 | 23 | 0 | 0 | 0.30781 | 228800
1897 | 3 | 80 | 0 | 0 | 0 | 0.27381 | 228800
1898 | 3 | 80 | 1 | 0 | 0 | 0.13732 | 228800
1899 | 3 | 80 | 2 | 0 | 0 | 0.098488 | 228800
1900 | 3 | 80 | 3 | 0 | 0 | 0.17449 | 228800
1901 | 3 | 80 | 4 | 0 | 0 | 0.15372 | 228800
1902 | 3 | 80 | 5 | 0 | 0 | 0.17708 | 228800
1903 | 3 | 80 | 6 | 0 | 0 | 0.22329 | 228800
1904 | 3 | 80 | 7 | 1 | 0.20867 | 0.23197 | 228600
1905 | 3 | 80 | 8 | 1 | 0.5076 | 0.13885 | 228400
1906 | 3 | 80 | 9 | 0 | 0.81044 | 0.10243 | 228400
1907 | 3 | 80 | 10 | 0 | 1 | 0.11435 | 228400
1908 | 3 | 80 | 11 | 0 | 1 | 0.17926 | 228400
1909 | 3 | 80 | 12 | 0 | 1 | 0.2344 | 228400
1910 | 3 | 80 | 13 | 0 | 1 | 0.19527 | 228400
1911 | 3 | 80 | 14 | 0 | 1 | 0.19331 | 228400
1912 | 3 | 80 | 15 | 0 | 0.81044 | 0.17324 | 228400
1913 | 3 | 80 | 16 | 0 | 0.5076 | 0.1386 | 228400
1914 | 3 | 80 | 17 | 0 | 0.20867 | 0.12385 | 228400
1915 | 3 | 80 | 18 | 0 | 0 | 0.16959 | 228400
1916 | 3 | 80 | 19 | 1 | 0 | 0.1944 | 228200
1917 | 3 | 80 | 20 | 1 | 0 | 0.17321 | 228000
1918 | 3 | 80 | 21 | 0 | 0 | 0.28881 | 228000
1919 | 3 | 80 | 22 | 0 | 0 | 0.35596 | 228000
1920 | 3 | 80 | 23 | 0 | 0 | 0.27635 | 228000
1921 | 3 | 81 | 0 | 0 | 0 | 0.31442 | 228000
1922 | 3 | 81 | 1 | 0 | 0 | 0.32694 | 228000
1923 | 3 | 81 | 2 | 0 | 0 | 0.36971 | 228000
1924 | 3 | 81 | 3 | 0 | 0 | 0.2864 | 228000
1925 | 3 | 81 | 4 | 0 | 0 | 0.37472 | 228000
1926 | 3 | 81 | 5 | 0 | 0 | 0.44225 | 228000
1927 | 3 | 81 | 6 | 0 | 0 | 0.59447 | 228000
1928 | 3 | 81 | 7 | 1 | 0.24835 | 0.4052 | 227800
1929 | 3 | 81 | 8 | 1 | 0.60412 | 0.40005 | 227600
1930 | 3 | 81 | 9 | 0 | 0.96454 | 0.40404 | 227600
1931 | 3 | 81 | 10 | 0 | 1 | 0.36874 | 227600
1932 | 3 | 81 | 11 | 0 | 1 | 0.39438 | 227600
1933 | 3 | 81 | 12 | 0 | 1 | 0.52443 | 227600
1934 | 3 | 81 | 13 | 0 | 1 | 0.53429 | 227600
1935 | 3 | 81 | 14 | 0 | 1 | 0.53011 | 227600
1936 | 3 | 81 | 15 | 0 | 0.96454 | 0.50591 | 227600
1937 | 3 | 81 | 16 | 0 | 0.60412 | 0.46884 | 227600
1938 | 3 | 81 | 17 | 0 | 0.24835 | 0.3904 | 227600
1939 | 3 | 81 | 18 | 0 | 0 | 0.28625 | 227600
1940 | 3 | 81 | 19 | 1 | 0 | 0.22162 | 227400
1941 | 3 | 81 | 20 | 1 | 0 | 0.18378 | 227200
1942 | 3 | 81 | 21 | 0 | 0 | 0.15616 | 227200
1943 | 3 | 81 | 22 | 0 | 0 | 0.29052 | 227200
1944 | 3 | 81 | 23 | 0 | 0 | 0.31553 | 227200
1945 | 3 | 82 | 0 | 0 | 0 | 0.34879 | 227200
1946 | 3 | 82 | 1 | 0 | 0 | 0.29901 | 227200
1947 | 3 | 82 | 2 | 0 | 0 | 0.22584 | 227200
1948 | 3 | 82 | 3 | 0 | 0 | 0.2631 | 227200
1949 | 3 | 82 | 4 | 0 | 0 | 0.34993 | 227200
1950 | 3 | 82 | 5 | 0 | 0 | 0.32238 | 227200
1951 | 3 | 82 | 6 | 0 | 0 | 0.24586 | 227200
1952 | 3 | 82 | 7 | 1 | 0.21486 | 0.29076 | 227000
1953 | 3 | 82 | 8 | 1 | 0.52265 | 0.2633 | 226800
1954 | 3 | 82 | 9 | 0 | 0.83447 | 0.33006 | 226800
1955 | 3 | 82 | 10 | 0 | 1 | 0.35089 | 226800
1956 | 3 | 82 | 11 | 0 | 1 | 0.37191 | 226800
1957 | 3 | 82 | 12 | 0 | 1 | 0.50626 | 226800
1958 | 3 | 82 | 13 | 0 | 1 | 0.49241 | 226800
1959 | 3 | 82 | 14 | 0 | 1 | 0.37351 | 226800
1960 | 3 | 82 | 15 | 0 | 0.83447 | 0.38699 | 226800
1961 | 3 | 82 | 16 | 0 | 0.52265 | 0.26205 | 226800
1962 | 3 | 82 | 17 | 0 | 0.21486 | 0.27435 | 226800
1963 | 3 | 82 | 18 | 0 | 0 | 0.30618 | 226800
1964 | 3 | 82 | 19 | 1 | 0 | 0.23313 | 226600
1965 | 3 | 82 | 20 | 1 | 0 | 0.23161 | 226400
1966 | 3 | 82 | 21 | 0 | 0 | 0.25252 | 226400
1967 | 3 | 82 | 22 | 0 | 0 | 0.24882 | 226400
1968 | 3 | 82 | 23 | 0 | 0 | 0.21914 | 226400
1969 | 3 | 83 | 0 | 0 | 0 | 0.24378 | 226400
1970 | 3 | 83 | 1 | 0 | 0 | 0.39048 | 226400
1971 | 3 | 83 | 2 | 0 | 0 | 0.33702 | 226400
1972 | 3 | 83 | 3 | 0 | 0 | 0.43914 | 226400
1973 | 3 | 83 | 4 | 0 | 0 | 0.65643 | 226400
1974 | 3 | 83 | 5 | 0 | 0 | 0.95657 | 226400
1975 | 3 | 83 | 6 | 0 | 0 | 0.9783 | 226400
1976 | 3 | 83 | 7 | 1 | 0.22521 | 1 | 226200
1977 | 3 | 83 | 8 | 1 | 0.54783 | 1 | 226000
1978 | 3 | 83 | 9 | 0 | 0.87467 | 1 | 226000
1979 | 3 | 83 | 10 | 0 | 1 | 0.89013 | 226000
1980 | 3 | 83 | 11 | 0 | 1 | 1 | 226000
1981 | 3 | 83 | 12 | 0 | 1 | 1 | 226000
1982 | 3 | 83 | 13 | 0 | 1 | 1 | 226000
1983 | 3 | 83 | 14 | 0 | 1 | 1 | 226000
1984 | 3 | 83 | 15 | 0 | 0.87467 | 1 | 226000
1985 | 3 | 83 | 16 | 0 | 0.54783 | 0.89283 | 226000
1986 | 3 | 83 | 17 | 0 | 0.22521 | 1 | 226000
1987 | 3 | 83 | 18 | 0 | 0 | 1 | 226000
1988 | 3 | 83 | 19 | 1 | 0 | 1 | 225800
1989 | 3 | 83 | 20 | 1 | 0 | 1 | 225600
1990 | 3 | 83 | 21 | 0 | 0 | 1 | 225600
1991 | 3 | 83 | 22 | 0 | 0 | 1 | 225600
1992 | 3 | 83 | 23 | 0 | 0 | 1 | 225600
1993 | 3 | 84 | 0 | 0 | 0 | 0.64607 | 225600
1994 | 3 | 84 | 1 | 0 | 0 | 0.42672 | 225600
1995 | 3 | 84 | 2 | 0 | 0 | 0.60771 | 225600
1996 | 3 | 84 | 3 | 0 | 0 | 0.70173 | 225600
1997 | 3 | 84 | 4 | 0 | 0 | 0.37033 | 225600
1998 | 3 | 84 | 5 | 0 | 0 | 0.40624 | 225600
1999 | 3 | 84 | 6 | 0 | 0 | 0.66215 | 225600
2000 | 3 | 84 | 7 | 1 | 0.23004 | 0.44523 | 225400
2001 | 3 | 84 | 8 | 1 | 0.55959 | 0.38783 | 225200
2002 | 3 | 84 | 9 | 0 | 0.89343 | 0.4134 | 225200
2003 | 3 | 84 | 10 | 0 | 1 | 0.36276 | 225200
2004 | 3 | 84 | 11 | 0 | 1 | 0.37719 | 225200
2005 | 3 | 84 | 12 | 0 | 1 | 0.32985 | 225200
2006 | 3 | 84 | 13 | 0 | 1 | 0.33039 | 225200
2007 | 3 | 84 | 14 | 0 | 1 | 0.43822 | 225200
2008 | 3 | 84 | 15 | 0 | 0.89343 | 0.36297 | 225200
2009 | 3 | 84 | 16 | 0 | 0.55959 | 0.32406 | 225200
2010 | 3 | 84 | 17 | 0 | 0.23004 | 0.38521 | 225200
2011 | 3 | 84 | 18 | 0 | 0 | 0.24227 | 225200
2012 | 3 | 84 | 19 | 1 | 0 | 0.20947 | 225000
2013 | 3 | 84 | 20 | 1 | 0 | 0.17214 | 224800
2014 | 3 | 84 | 21 | 0 | 0 | 0.14115 | 224800
2015 | 3 | 84 | 22 | 0 | 0 | 0.1556 | 224800
2016 | 3 | 84 | 23 | 0 | 0 | 0.16406 | 224800
2017 | 3 | 85 | 0 | 0 | 0 | 0.13424 | 224800
2018 | 3 | 85 | 1 | 0 | 0 | 0.13464 | 224800
2019 | 3 | 85 | 2 | 0 | 0 | 0.14943 | 224800
2020 | 3 | 85 | 3 | 0 | 0 | 0.13308 | 224800
2021 | 3 | 85 | 4 | 0 | 0 | 0.12407 | 224800
2022 | 3 | 85 | 5 | 0 | 0 | 0.11571 | 224800
2023 | 3 | 85 | 6 | 0 | 0 | 0.10368 | 224800
2024 | 3 | 85 | 7 | 1 | 0.22697 | 0.12241 | 224600
2025 | 3 | 85 | 8 | 1 | 0.55212 | 0.15209 | 224400
2026 | 3 | 85 | 9 | 0 | 0.88151 | 0.17822 | 224400
2027 | 3 | 85 | 10 | 0 | 1 | 0.20078 | 224400
2028 | 3 | 85 | 11 | 0 | 1 | 0.25179 | 224400
2029 | 3 | 85 | 12 | 0 | 1 | 0.22013 | 224400
2030 | 3 | 85 | 13 | 0 | 1 | 0.26362 | 224400
2031 | 3 | 85 | 14 | 0 | 1 | 0.16543 | 224400
2032 | 3 | 85 | 15 | 0 | 0.88151 | 0.16281 | 224400
2033 | 3 | 85 | 16 | 0 | 0.55212 | 0.14836 | 224400
2034 | 3 | 85 | 17 | 0 | 0.22697 | 0.1282 | 224400
2035 | 3 | 85 | 18 | 0 | 0 | 0.15008 | 224400
2036 | 3 | 85 | 19 | 1 | 0 | 0.1116 | 224200
2037 | 3 | 85 | 20 | 1 | 0 | 0.086933 | 224000
2038 | 3 | 85 | 21 | 0 | 0 | 0.065836 | 224000
2039 | 3 | 85 | 22 | 0 | 0 | 0.071503 | 224000
2040 | 3 | 85 | 23 | 0 | 0 | 0.0942 | 224000
2041 | 3 | 86 | 0 | 0 | 0 | 0.094114 | 224000
2042 | 3 | 86 | 1 | 0 | 0 | 0.11056 | 224000
2043 | 3 | 86 | 2 | 0 | 0 | 0.1811 | 224000
2044 | 3 | 86 | 3 | 0 | 0 | 0.18467 | 224000
2045 | 3 | 86 | 4 | 0 | 0 | 0.14886 | 224000
2046 | 3 | 86 | 5 | 0 | 0 | 0.22068 | 224000
2047 | 3 | 86 | 6 | 0 | 0 | 0.25238 | 224000
2048 | 3 | 86 | 7 | 1 | 0.24061 | 0.24502 | 223800
2049 | 3 | 86 | 8 | 1 | 0.58529 | 0.22587 | 223600
2050 | 3 | 86 | 9 | 0 | 0.93447 | 0.21791 | 223600
2051 | 3 | 86 | 10 | 0 | 1 | 0.16434 | 223600
2052 | 3 | 86 | 11 | 0 | 1 | 0.27339 | 223600
2053 | 3 | 86 | 12 | 0 | 1 | 0.21805 | 223600
2054 | 3 | 86 | 13 | 0 | 1 | 0.17051 | 223600
2055 | 3 | 86 | 14 | 0 | 1 | 0.18605 | 223600
2056 | 3 | 86 | 15 | 0 | 0.93447 | 0.18896 | 223600
2057 | 3 | 86 | 16 | 0 | 0.58529 | 0.24942 | 223600
2058 | 3 | 86 | 17 | 0 | 0.24061 | 0.40794 | 223600
2059 | 3 | 86 | 18 | 0 | 0 | 0.47466 | 223600
2060 | 3 | 86 | 19 | 1 | 0 | 0.33028 | 223400
2061 | 3 | 86 | 20 | 1 | 0 | 0.35102 | 223200
2062 | 3 | 86 | 21 | 0 | 0 | 0.3189 | 223200
2063 | 3 | 86 | 22 | 0 | 0 | 0.27646 | 223200
2064 | 3 | 86 | 23 | 0 | 0 | 0.34666 | 223200
2065 | 3 | 87 | 0 | 0 | 0 | 0.27524 | 223200
2066 | 3 | 87 | 1 | 0 | 0 | 0.30532 | 223200
2067 | 3 | 87 | 2 | 0 | 0 | 0.35759 | 223200
2068 | 3 | 87 | 3 | 0 | 0 | 0.26198 | 223200
2069 | 3 | 87 | 4 | 0 | 0 | 0.21238 | 223200
2070 | 3 | 87 | 5 | 0 | 0 | 0.26655 | 223200
2071 | 3 | 87 | 6 | 0 | 0 | 0.30843 | 223200
2072 | 3 | 87 | 7 | 1 | 0.25501 | 0.24739 | 223000
2073 | 3 | 87 | 8 | 1 | 0.62033 | 0.25899 | 222800
2074 | 3 | 87 | 9 | 0 | 0.99042 | 0.28373 | 222800
2075 | 3 | 87 | 10 | 0 | 1 | 0.2824 | 222800
2076 | 3 | 87 | 11 | 0 | 1 | 0.34299 | 222800
2077 | 3 | 87 | 12 | 0 | 1 | 0.30983 | 222800
2078 | 3 | 87 | 13 | 0 | 1 | 0.22484 | 222800
2079 | 3 | 87 | 14 | 0 | 1 | 0.20673 | 222800
2080 | 3 | 87 | 15 | 0 | 0.99042 | 0.14668 | 222800
2081 | 3 | 87 | 16 | 0 | 0.62033 | 0.156 | 222800
2082 | 3 | 87 | 17 | 0 | 0.25501 | 0.10219 | 222800
2083 | 3 | 87 | 18 | 0 | 0 | 0.13167 | 222800
2084 | 3 | 87 | 19 | 1 | 0 | 0.15047 | 222600
2085 | 3 | 87 | 20 | 1 | 0 | 0.17132 | 222400
2086 | 3 | 87 | 21 | 0 | 0 | 0.21855 | 222400
2087 | 3 | 87 | 22 | 0 | 0 | 0.27581 | 222400
2088 | 3 | 87 | 23 | 0 | 0 | 0.29774 | 222400
2089 | 3 | 88 | 0 | 0 | 0 | 0.20972 | 222400
2090 | 3 | 88 | 1 | 0 | 0 | 0.2239 | 222400
2091 | 3 | 88 | 2 | 0 | 0 | 0.20552 | 222400
2092 | 3 | 88 | 3 | 0 | 0 | 0.19232 | 222400
2093 | 3 | 88 | 4 | 0 | 0 | 0.1467 | 222400
2094 | 3 | 88 | 5 | 0 | 0 | 0.097232 | 222400
2095 | 3 | 88 | 6 | 0 | 0 | 0.10931 | 222400
2096 | 3 | 88 | 7 | 1 | 0.19404 | 0.16406 | 222200
2097 | 3 | 88 | 8 | 1 | 0.47202 | 0.22108 | 222000
2098 | 3 | 88 | 9 | 0 | 0.75362 | 0.36552 | 222000
2099 | 3 | 88 | 10 | 0 | 0.99087 | 0.27478 | 222000
2100 | 3 | 88 | 11 | 0 | 1 | 0.27227 | 222000
2101 | 3 | 88 | 12 | 0 | 1 | 0.30679 | 222000
2102 | 3 | 88 | 13 | 0 | 1 | 0.298 | 222000
2103 | 3 | 88 | 14 | 0 | 0.99087 | 0.26615 | 222000
2104 | 3 | 88 | 15 | 0 | 0.75362 | 0.34486 | 222000
2105 | 3 | 88 | 16 | 0 | 0.47202 | 0.49897 | 222000
2106 | 3 | 88 | 17 | 0 | 0.19404 | 0.42541 | 222000
2107 | 3 | 88 | 18 | 0 | 0 | 0.47615 | 222000
2108 | 3 | 88 | 19 | 1 | 0 | 0.48611 | 221800
2109 | 3 | 88 | 20 | 1 | 0 | 0.37779 | 221600
2110 | 3 | 88 | 21 | 0 | 0 | 0.29038 | 221600
2111 | 3 | 88 | 22 | 0 | 0 | 0.34805 | 221600
2112 | 3 | 88 | 23 | 0 | 0 | 0.38463 | 221600
2113 | 3 | 89 | 0 | 0 | 0 | 0.36784 | 221600
2114 | 3 | 89 | 1 | 0 | 0 | 0.41364 | 221600
2115 | 3 | 89 | 2 | 0 | 0 | 0.40597 | 221600
2116 | 3 | 89 | 3 | 0 | 0 | 0.39049 | 221600
2117 | 3 | 89 | 4 | 0 | 0 | 0.51719 | 221600
2118 | 3 | 89 | 5 | 0 | 0 | 0.90884 | 221600
2119 | 3 | 89 | 6 | 0 | 0 | 0.50919 | 221600
2120 | 3 | 89 | 7 | 1 | 0.25518 | 0.42665 | 221400
2121 | 3 | 89 | 8 | 1 | 0.62074 | 0.35441 | 221200
2122 | 3 | 89 | 9 | 0 | 0.99107 | 0.36102 | 221200
2123 | 3 | 89 | 10 | 0 | 1 | 0.41452 | 221200
2124 | 3 | 89 | 11 | 0 | 1 | 0.38228 | 221200
2125 | 3 | 89 | 12 | 0 | 1 | 0.2857 | 221200
2126 | 3 | 89 | 13 | 0 | 1 | 0.41177 | 221200
2127 | 3 | 89 | 14 | 0 | 1 | 0.35548 | 221200
2128 | 3 | 89 | 15 | 0 | 0.99107 | 0.33615 | 221200
2129 | 3 | 89 | 16 | 0 | 0.62074 | 0.54082 | 221200
2130 | 3 | 89 | 17 | 0 | 0.25518 | 0.36211 | 221200
2131 | 3 | 89 | 18 | 0 | 0 | 0.32262 | 221200
2132 | 3 | 89 | 19 | 1 | 0 | 0.28565 | 221000
2133 | 3 | 89 | 20 | 1 | 0 | 0.23348 | 220800
2134 | 3 | 89 | 21 | 0 | 0 | 0.20412 | 220800
2135 | 3 | 89 | 22 | 0 | 0 | 0.2635 | 220800
2136 | 3 | 89 | 23 | 0 | 0 | 0.24223 | 220800
2137 | 3 | 90 | 0 | 0 | 0 | 0.3052 | 220800
2138 | 3 | 90 | 1 | 0 | 0 | 0.24876 | 220800
2139 | 3 | 90 | 2 | 0 | 0 | 0.3486 | 220800
2140 | 3 | 90 | 3 | 0 | 0 | 0.42081 | 220800
2141 | 3 | 90 | 4 | 0 | 0 | 0.55506 | 220800
2142 | 3 | 90 | 5 | 0 | 0 | 0.38812 | 220800
2143 | 3 | 90 | 6 | 0 | 0 | 0.51375 | 220800
2144 | 3 | 90 | 7 | 1 | 0.24094 | 0.26456 | 220600
2145 | 3 | 90 | 8 | 1 | 0.58609 | 0.16906 | 220400
2146 | 3 | 90 | 9 | 0 | 0.93575 | 0.21212 | 220400
2147 | 3 | 90 | 10 | 0 | 1 | 0.27714 | 220400
2148 | 3 | 90 | 11 | 0 | 1 | 0.263 | 220400
2149 | 3 | 90 | 12 | 0 | 1 | 0.23302 | 220400
2150 | 3 | 90 | 13 | 0 | 1 | 0.18885 | 220400
2151 | 3 | 90 | 14 | 0 | 1 | 0.19375 | 220400
2152 | 3 | 90 | 15 | 0 | 0.93575 | 0.15366 | 220400
2153 | 3 | 90 | 16 | 0 | 0.58609 | 0.22494 | 220400
2154 | 3 | 90 | 17 | 0 | 0.24094 | 0.16136 | 220400
2155 | 3 | 90 | 18 | 0 | 0 | 0.15107 | 220400
2156 | 3 | 90 | 19 | 1 | 0 | 0.14771 | 220200
2157 | 3 | 90 | 20 | 1 | 0 | 0.24512 | 220000
2158 | 3 | 90 | 21 | 0 | 0 | 0.28016 | 220000
2159 | 3 | 90 | 22 | 0 | 0 | 0.23207 | 220000
2160 | 3 | 90 | 23 | 0 | 0 | 0.20991 | 220000
2161 | 4 | 91 | 0 | 0 | 0 | 0.23991 | 220000
2162 | 4 | 91 | 1 | 0 | 0 | 0.20888 | 220000
2163 | 4 | 91 | 2 | 0 | 0 | 0.27134 | 220000
2164 | 4 | 91 | 3 | 0 | 0 | 0.30941 | 220000
2165 | 4 | 91 | 4 | 0 | 0 | 0.31949 | 220000
2166 | 4 | 91 | 5 | 0 | 0 | 0.43374 | 220000
2167 | 4 | 91 | 6 | 0 | 0.059783 | 0.46474 | 220000
2168 | 4 | 91 | 7 | 1 | 0.36127 | 0.423 | 219800
2169 | 4 | 91 | 8 | 1 | 0.72503 | 0.29398 | 219600
2170 | 4 | 91 | 9 | 0 | 1 | 0.27384 | 219600
2171 | 4 | 91 | 10 | 0 | 1 | 0.21764 | 219600
2172 | 4 | 91 | 11 | 0 | 1 | 0.29546 | 219600
2173 | 4 | 91 | 12 | 0 | 1 | 0.2209 | 219600
2174 | 4 | 91 | 13 | 0 | 1 | 0.34786 | 219600
2175 | 4 | 91 | 14 | 0 | 1 | 0.47665 | 219600
2176 | 4 | 91 | 15 | 0 | 1 | 0.3244 | 219600
2177 | 4 | 91 | 16 | 0 | 0.72503 | 0.33108 | 219600
2178 | 4 | 91 | 17 | 0 | 0.36127 | 0.60986 | 219600
2179 | 4 | 91 | 18 | 0 | 0.059783 | 0.60924 | 219600
2180 | 4 | 91 | 19 | 1 | 0 | 0.80828 | 219400
2181 | 4 | 91 | 20 | 1 | 0 | 1 | 219200
2182 | 4 | 91 | 21 | 0 | 0 | 1 | 219200
2183 | 4 | 91 | 22 | 0 | 0 | 0.66257 | 219200
2184 | 4 | 91 | 23 | 0 | 0 | 0.56147 | 219200
2185 | 4 | 92 | 0 | 0 | 0 | 0.74754 | 219200
2186 | 4 | 92 | 1 | 0 | 0 | 1 | 219200
2187 | 4 | 92 | 2 | 0 | 0 | 0.62319 | 219200
2188 | 4 | 92 | 3 | 0 | 0 | 0.7107 | 219200
2189 | 4 | 92 | 4 | 0 | 0 | 0.68902 | 219200
2190 | 4 | 92 | 5 | 0 | 0 | 0.48041 | 219200
2191 | 4 | 92 | 6 | 0 | 0.054534 | 0.62278 | 219200
2192 | 4 | 92 | 7 | 1 | 0.32955 | 0.49048 | 219000
2193 | 4 | 92 | 8 | 1 | 0.66138 | 0.49825 | 218800
2194 | 4 | 92 | 9 | 0 | 0.98403 | 0.40223 | 218800
2195 | 4 | 92 | 10 | 0 | 1 | 0.39111 | 218800
2196 | 4 | 92 | 11 | 0 | 1 | 0.54404 | 218800
2197 | 4 | 92 | 12 | 0 | 1 | 0.64795 | 218800
2198 | 4 | 92 | 13 | 0 | 1 | 0.43294 | 218800
2199 | 4 | 92 | 14 | 0 | 1 | 0.50711 | 218800
2200 | 4 | 92 | 15 | 0 | 0.98403 | 0.44815 | 218800
2201 | 4 | 92 | 16 | 0 | 0.66138 | 0.36392 | 218800
2202 | 4 | 92 | 17 | 0 | 0.32955 | 0.32165 | 218800
2203 | 4 | 92 | 18 | 0 | 0.054534 | 0.22001 | 218800
2204 | 4 | 92 | 19 | 1 | 0 | 0.2747 | 218600
2205 | 4 | 92 | 20 | 1 | 0 | 0.26815 | 218400
2206 | 4 | 92 | 21 | 0 | 0 | 0.30551 | 218400
2207 | 4 | 92 | 22 | 0 | 0 | 0.29357 | 218400
2208 | 4 | 92 | 23 | 0 | 0 | 0.24844 | 218400
2209 | 4 | 93 | 0 | 0 | 0 | 0.21569 | 218400
2210 | 4 | 93 | 1 | 0 | 0 | 0.23514 | 218400
2211 | 4 | 93 | 2 | 0 | 0 | 0.24353 | 218400
2212 | 4 | 93 | 3 | 0 | 0 | 0.16248 | 218400
2213 | 4 | 93 | 4 | 0 | 0 | 0.20703 | 218400
2214 | 4 | 93 | 5 | 0 | 0 | 0.18025 | 218400
2215 | 4 | 93 | 6 | 0 | 0.051399 | 0.18573 | 218400
2216 | 4 | 93 | 7 | 1 | 0.3106 | 0.15611 | 218200
2217 | 4 | 93 | 8 | 1 | 0.62335 | 0.19929 | 218000
2218 | 4 | 93 | 9 | 0 | 0.92746 | 0.22104 | 218000
2219 | 4 | 93 | 10 | 0 | 1 | 0.23146 | 218000
2220 | 4 | 93 | 11 | 0 | 1 | 0.17787 | 218000
2221 | 4 | 93 | 12 | 0 | 1 | 0.18553 | 218000
2222 | 4 | 93 | 13 | 0 | 1 | 0.18156 | 218000
2223 | 4 | 93 | 14 | 0 | 1 | 0.22407 | 218000
2224 | 4 | 93 | 15 | 0 | 0.92746 | 0.26217 | 218000
2225 | 4 | 93 | 16 | 0 | 0.62335 | 0.20149 | 218000
2226 | 4 | 93 | 17 | 0 | 0.3106 | 0.13493 | 218000
2227 | 4 | 93 | 18 | 0 | 0.051399 | 0.12768 | 218000
2228 | 4 | 93 | 19 | 1 | 0 | 0.11797 | 217800
2229 | 4 | 93 | 20 | 1 | 0 | 0.079799 | 217600
2230 | 4 | 93 | 21 | 0 | 0 | 0.11543 | 217600
2231 | 4 | 93 | 22 | 0 | 0 | 0.13499 | 217600
2232 | 4 | 93 | 23 | 0 | 0 | 0.18423 | 217600
2233 | 4 | 94 | 0 | 0 | 0 | 0.18698 | 217600
2234 | 4 | 94 | 1 | 0 | 0 | 0.27027 | 217600
2235 | 4 | 94 | 2 | 0 | 0 | 0.19209 | 217600
2236 | 4 | 94 | 3 | 0 | 0 | 0.2472 | 217600
2237 | 4 | 94 | 4 | 0 | 0 | 0.26488 | 217600
2238 | 4 | 94 | 5 | 0 | 0 | 0.22762 | 217600
2239 | 4 | 94 | 6 | 0 | 0.063311 | 0.29134 | 217600
2240 | 4 | 94 | 7 | 1 | 0.38259 | 0.19988 | 217400
2241 | 4 | 94 | 8 | 1 | 0.76782 | 0.16171 | 217200
2242 | 4 | 94 | 9 | 0 | 1 | 0.20926 | 217200
2243 | 4 | 94 | 10 | 0 | 1 | 0.2306 | 217200
2244 | 4 | 94 | 11 | 0 | 1 | 0.32762 | 217200
2245 | 4 | 94 | 12 | 0 | 1 | 0.22361 | 217200
2246 | 4 | 94 | 13 | 0 | 1 | 0.32132 | 217200
2247 | 4 | 94 | 14 | 0 | 1 | 0.29533 | 217200
2248 | 4 | 94 | 15 | 0 | 1 | 0.28864 | 217200
2249 | 4 | 94 | 16 | 0 | 0.76782 | 0.38576 | 217200
2250 | 4 | 94 | 17 | 0 | 0.38259 | 0.41735 | 217200
2251 | 4 | 94 | 18 | 0 | 0.063311 | 0.43914 | 217200
2252 | 4 | 94 | 19 | 1 | 0 | 0.51832 | 217000
2253 | 4 | 94 | 20 | 1 | 0 | 0.56998 | 216800
2254 | 4 | 94 | 21 | 0 | 0 | 0.67299 | 216800
2255 | 4 | 94 | 22 | 0 | 0 | 0.63854 | 216800
2256 | 4 | 94 | 23 | 0 | 0 | 0.61422 | 216800
2257 | 4 | 95 | 0 | 0 | 0 | 0.62883 | 216800
2258 | 4 | 95 | 1 | 0 | 0 | 0.39076 | 216800
2259 | 4 | 95 | 2 | 0 | 0 | 0.45034 | 216800
2260 | 4 | 95 | 3 | 0 | 0 | 0.3934 | 216800
2261 | 4 | 95 | 4 | 0 | 0 | 0.44592 | 216800
2262 | 4 | 95 | 5 | 0 | 0 | 0.50801 | 216800
2263 | 4 | 95 | 6 | 0 | 0.056729 | 0.44594 | 216800
2264 | 4 | 95 | 7 | 1 | 0.34281 | 0.42288 | 216600
2265 | 4 | 95 | 8 | 1 | 0.688 | 0.31952 | 216400
2266 | 4 | 95 | 9 | 0 | 1 | 0.3923 | 216400
2267 | 4 | 95 | 10 | 0 | 1 | 0.41325 | 216400
2268 | 4 | 95 | 11 | 0 | 1 | 0.6534 | 216400
2269 | 4 | 95 | 12 | 0 | 1 | 0.61449 | 216400
2270 | 4 | 95 | 13 | 0 | 1 | 0.48848 | 216400
2271 | 4 | 95 | 14 | 0 | 1 | 0.40027 | 216400
2272 | 4 | 95 | 15 | 0 | 1 | 0.30735 | 216400
2273 | 4 | 95 | 16 | 0 | 0.688 | 0.43958 | 216400
2274 | 4 | 95 | 17 | 0 | 0.34281 | 0.32391 | 216400
2275 | 4 | 95 | 18 | 0 | 0.056729 | 0.252 | 216400
2276 | 4 | 95 | 19 | 1 | 0 | 0.16989 | 216200
2277 | 4 | 95 | 20 | 1 | 0 | 0.12196 | 216000
2278 | 4 | 95 | 21 | 0 | 0 | 0.20121 | 216000
2279 | 4 | 95 | 22 | 0 | 0 | 0.21097 | 216000
2280 | 4 | 95 | 23 | 0 | 0 | 0.20121 | 216000
2281 | 4 | 96 | 0 | 0 | 0 | 0.1551 | 216000
2282 | 4 | 96 | 1 | 0 | 0 | 0.1363 | 216000
2283 | 4 | 96 | 2 | 0 | 0 | 0.11357 | 216000
2284 | 4 | 96 | 3 | 0 | 0 | 0.16712 | 216000
2285 | 4 | 96 | 4 | 0 | 0 | 0.15689 | 216000
2286 | 4 | 96 | 5 | 0 | 0 | 0.13944 | 216000
2287 | 4 | 96 | 6 | 0 | 0.044887 | 0.1312 | 216000
2288 | 4 | 96 | 7 | 1 | 0.27125 | 0.19356 | 215800
2289 | 4 | 96 | 8 | 1 | 0.54438 | 0.25464 | 215600
2290 | 4 | 96 | 9 | 0 | 0.80996 | 0.27826 | 215600
2291 | 4 | 96 | 10 | 0 | 1 | 0.28658 | 215600
2292 | 4 | 96 | 11 | 0 | 1 | 0.28805 | 215600
2293 | 4 | 96 | 12 | 0 | 1 | 0.21369 | 215600
2294 | 4 | 96 | 13 | 0 | 1 | 0.14429 | 215600
2295 | 4 | 96 | 14 | 0 | 1 | 0.14855 | 215600
2296 | 4 | 96 | 15 | 0 | 0.80996 | 0.14646 | 215600
2297 | 4 | 96 | 16 | 0 | 0.54438 | 0.29803 | 215600
2298 | 4 | 96 | 17 | 0 | 0.27125 | 0.23277 | 215600
2299 | 4 | 96 | 18 | 0 | 0.044887 | 0.21228 | 215600
2300 | 4 | 96 | 19 | 1 | 0 | 0.20511 | 215400
2301 | 4 | 96 | 20 | 1 | 0 | 0.23123 | 215200
2302 | 4 | 96 | 21 | 0 | 0 | 0.27832 | 215200
2303 | 4 | 96 | 22 | 0 | 0 | 0.29421 | 215200
2304 | 4 | 96 | 23 | 0 | 0 | 0.25596 | 215200
2305 | 4 | 97 | 0 | 0 | 0 | 0.30701 | 215200
2306 | 4 | 97 | 1 | 0 | 0 | 0.24988 | 215200
2307 | 4 | 97 | 2 | 0 | 0 | 0.28215 | 215200
2308 | 4 | 97 | 3 | 0 | 0 | 0.23942 | 215200
2309 | 4 | 97 | 4 | 0 | 0 | 0.25047 | 215200
2310 | 4 | 97 | 5 | 0 | 0 | 0.28843 | 215200
2311 | 4 | 97 | 6 | 0 | 0.05303 | 0.26464 | 215200
2312 | 4 | 97 | 7 | 1 | 0.32046 | 0.2767 | 215000
2313 | 4 | 97 | 8 | 1 | 0.64314 | 0.19453 | 214800
2314 | 4 | 97 | 9 | 0 | 0.9569 | 0.21724 | 214800
2315 | 4 | 97 | 10 | 0 | 1 | 0.27132 | 214800
2316 | 4 | 97 | 11 | 0 | 1 | 0.32249 | 214800
2317 | 4 | 97 | 12 | 0 | 1 | 0.33747 | 214800
2318 | 4 | 97 | 13 | 0 | 1 | 0.25198 | 214800
2319 | 4 | 97 | 14 | 0 | 1 | 0.28321 | 214800
2320 | 4 | 97 | 15 | 0 | 0.9569 | 0.21609 | 214800
2321 | 4 | 97 | 16 | 0 | 0.64314 | 0.19301 | 214800
2322 | 4 | 97 | 17 | 0 | 0.32046 | 0.23537 | 214800
2323 | 4 | 97 | 18 | 0 | 0.05303 | 0.22341 | 214800
2324 | 4 | 97 | 19 | 1 | 0 | 0.15957 | 214600
2325 | 4 | 97 | 20 | 1 | 0 | 0.18858 | 214400
2326 | 4 | 97 | 21 | 0 | 0 | 0.23965 | 214400
2327 | 4 | 97 | 22 | 0 | 0 | 0.27219 | 214400
2328 | 4 | 97 | 23 | 0 | 0 | 0.17782 | 214400
2329 | 4 | 98 | 0 | 0 | 0 | 0.19067 | 214400
2330 | 4 | 98 | 1 | 0 | 0 | 0.1527 | 214400
2331 | 4 | 98 | 2 | 0 | 0 | 0.22977 | 214400
2332 | 4 | 98 | 3 | 0 | 0 | 0.222 | 214400
2333 | 4 | 98 | 4 | 0 | 0 | 0.18574 | 214400
2334 | 4 | 98 | 5 | 0 | 0 | 0.20764 | 214400
2335 | 4 | 98 | 6 | 0 | 0.051099 | 0.23065 | 214400
2336 | 4 | 98 | 7 | 1 | 0.30879 | 0.45908 | 214200
2337 | 4 | 98 | 8 | 1 | 0.61972 | 0.50772 | 214000
2338 | 4 | 98 | 9 | 0 | 0.92205 | 0.66733 | 214000
2339 | 4 | 98 | 10 | 0 | 1 | 0.7802 | 214000
2340 | 4 | 98 | 11 | 0 | 1 | 0.47978 | 214000
2341 | 4 | 98 | 12 | 0 | 1 | 0.5141 | 214000
2342 | 4 | 98 | 13 | 0 | 1 | 0.78851 | 214000
2343 | 4 | 98 | 14 | 0 | 1 | 0.67054 | 214000
2344 | 4 | 98 | 15 | 0 | 0.92205 | 0.53173 | 214000
2345 | 4 | 98 | 16 | 0 | 0.61972 | 0.68894 | 214000
2346 | 4 | 98 | 17 | 0 | 0.30879 | 0.64332 | 214000
2347 | 4 | 98 | 18 | 0 | 0.051099 | 0.69442 | 214000
2348 | 4 | 98 | 19 | 1 | 0 | 0.45635 | 213800
2349 | 4 | 98 | 20 | 1 | 0 | 0.4931 | 213600
2350 | 4 | 98 | 21 | 0 | 0 | 0.35969 | 213600
2351 | 4 | 98 | 22 | 0 | 0 | 0.35133 | 213600
2352 | 4 | 98 | 23 | 0 | 0 | 0.29525 | 213600
2353 | 4 | 99 | 0 | 0 | 0 | 0.27107 | 213600
2354 | 4 | 99 | 1 | 0 | 0 | 0.28891 | 213600
2355 | 4 | 99 | 2 | 0 | 0 | 0.2253 | 213600
2356 | 4 | 99 | 3 | 0 | 0 | 0.25993 | 213600
2357 | 4 | 99 | 4 | 0 | 0 | 0.36186 | 213600
2358 | 4 | 99 | 5 | 0 | 0 | 0.48449 | 213600
2359 | 4 | 99 | 6 | 0 | 0.050516 | 0.47133 | 213600
2360 | 4 | 99 | 7 | 1 | 0.30527 | 0.67378 | 213400
2361 | 4 | 99 | 8 | 1 | 0.61265 | 0.76827 | 213200
2362 | 4 | 99 | 9 | 0 | 0.91153 | 0.55887 | 213200
2363 | 4 | 99 | 10 | 0 | 1 | 0.39931 | 213200
2364 | 4 | 99 | 11 | 0 | 1 | 0.36507 | 213200
2365 | 4 | 99 | 12 | 0 | 1 | 0.32194 | 213200
2366 | 4 | 99 | 13 | 0 | 1 | 0.3258 | 213200
2367 | 4 | 99 | 14 | 0 | 1 | 0.2727 | 213200
2368 | 4 | 99 | 15 | 0 | 0.91153 | 0.37597 | 213200
2369 | 4 | 99 | 16 | 0 | 0.61265 | 0.51322 | 213200
2370 | 4 | 99 | 17 | 0 | 0.30527 | 0.60429 | 213200
2371 | 4 | 99 | 18 | 0 | 0.050516 | 0.8165 | 213200
2372 | 4 | 99 | 19 | 1 | 0 | 0.88653 | 213000
2373 | 4 | 99 | 20 | 1 | 0 | 0.6103 | 212800
2374 | 4 | 99 | 21 | 0 | 0 | 0.616 | 212800
2375 | 4 | 99 | 22 | 0 | 0 | 0.65557 | 212800
2376 | 4 | 99 | 23 | 0 | 0 | 1 | 212800
2377 | 4 | 100 | 0 | 0 | 0 | 0.95296 | 212800
2378 | 4 | 100 | 1 | 0 | 0 | 0.66288 | 212800
2379 | 4 | 100 | 2 | 0 | 0 | 0.39923 | 212800
2380 | 4 | 100 | 3 | 0 | 0 | 0.40794 | 212800
2381 | 4 | 100 | 4 | 0 | 0 | 0.37508 | 212800
2382 | 4 | 100 | 5 | 0 | 0 | 0.34545 | 212800
2383 | 4 | 100 | 6 | 0 | 0.058348 | 0.27867 | 212800
2384 | 4 | 100 | 7 | 1 | 0.3526 | 0.23658 | 212600
2385 | 4 | 100 | 8 | 1 | 0.70763 | 0.18916 | 212400
2386 | 4 | 100 | 9 | 0 | 1 | 0.29834 | 212400
2387 | 4 | 100 | 10 | 0 | 1 | 0.39215 | 212400
2388 | 4 | 100 | 11 | 0 | 1 | 0.43196 | 212400
2389 | 4 | 100 | 12 | 0 | 1 | 0.31619 | 212400
2390 | 4 | 100 | 13 | 0 | 1 | 0.31198 | 212400
2391 | 4 | 100 | 14 | 0 | 1 | 0.27107 | 212400
2392 | 4 | 100 | 15 | 0 | 1 | 0.24391 | 212400
2393 | 4 | 100 | 16 | 0 | 0.70763 | 0.14049 | 212400
2394 | 4 | 100 | 17 | 0 | 0.3526 | 0.12138 | 212400
2395 | 4 | 100 | 18 | 0 | 0.058348 | 0.12143 | 212400
2396 | 4 | 100 | 19 | 1 | 0 | 0.11199 | 212200
2397 | 4 | 100 | 20 | 1 | 0 | 0.071955 | 212000
2398 | 4 | 100 | 21 | 0 | 0 | 0.072029 | 212000
2399 | 4 | 100 | 22 | 0 | 0 | 0.082016 | 212000
2400 | 4 | 100 | 23 | 0 | 0 | 0.094557 | 212000
2401 | 4 | 101 | 0 | 0 | 0 | 0.11742 | 212000
2402 | 4 | 101 | 1 | 0 | 0 | 0.1869 | 212000
2403 | 4 | 101 | 2 | 0 | 0 | 0.26588 | 212000
2404 | 4 | 101 | 3 | 0 | 0 | 0.29943 | 212000
2405 | 4 | 101 | 4 | 0 | 0 | 0.34716 | 212000
2406 | 4 | 101 | 5 | 0 | 0 | 0.45811 | 212000
2407 | 4 | 101 | 6 | 0 | 0.0532 | 0.44245 | 212000
2408 | 4 | 101 | 7 | 1 | 0.32149 | 0.40159 | 211800
2409 | 4 | 101 | 8 | 1 | 0.64519 | 0.45176 | 211600
2410 | 4 | 101 | 9 | 0 | 0.95995 | 0.53623 | 211600
2411 | 4 | 101 | 10 | 0 | 1 | 0.83834 | 211600
2412 | 4 | 101 | 11 | 0 | 1 | 0.61108 | 211600
2413 | 4 | 101 | 12 | 0 | 1 | 0.36852 | 211600
2414 | 4 | 101 | 13 | 0 | 1 | 0.28769 | 211600
2415 | 4 | 101 | 14 | 0 | 1 | 0.35276 | 211600
2416 | 4 | 101 | 15 | 0 | 0.95995 | 0.28299 | 211600
2417 | 4 | 101 | 16 | 0 | 0.64519 | 0.25297 | 211600
2418 | 4 | 101 | 17 | 0 | 0.32149 | 0.19443 | 211600
2419 | 4 | 101 | 18 | 0 | 0.0532 | 0.22916 | 211600
2420 | 4 | 101 | 19 | 1 | 0 | 0.24316 | 211400
2421 | 4 | 101 | 20 | 1 | 0 | 0.22191 | 211200
2422 | 4 | 101 | 21 | 0 | 0 | 0.29153 | 211200
2423 | 4 | 101 | 22 | 0 | 0 | 0.16203 | 211200
2424 | 4 | 101 | 23 | 0 | 0 | 0.15278 | 211200
2425 | 4 | 102 | 0 | 0 | 0 | 0.15107 | 211200
2426 | 4 | 102 | 1 | 0 | 0 | 0.13283 | 211200
2427 | 4 | 102 | 2 | 0 | 0 | 0.11883 | 211200
2428 | 4 | 102 | 3 | 0 | 0 | 0.10027 | 211200
2429 | 4 | 102 | 4 | 0 | 0 | 0.14803 | 211200
2430 | 4 | 102 | 5 | 0 | 0 | 0.18527 | 211200
2431 | 4 | 102 | 6 | 0 | 0.058389 | 0.2158 | 211200
2432 | 4 | 102 | 7 | 1 | 0.35285 | 0.24318 | 211000
2433 | 4 | 102 | 8 | 1 | 0.70813 | 0.27326 | 210800
2434 | 4 | 102 | 9 | 0 | 1 | 0.29944 | 210800
2435 | 4 | 102 | 10 | 0 | 1 | 0.42887 | 210800
2436 | 4 | 102 | 11 | 0 | 1 | 0.54819 | 210800
2437 | 4 | 102 | 12 | 0 | 1 | 0.59835 | 210800
2438 | 4 | 102 | 13 | 0 | 1 | 0.97968 | 210800
2439 | 4 | 102 | 14 | 0 | 1 | 0.58923 | 210800
2440 | 4 | 102 | 15 | 0 | 1 | 0.73477 | 210800
2441 | 4 | 102 | 16 | 0 | 0.70813 | 0.74376 | 210800
2442 | 4 | 102 | 17 | 0 | 0.35285 | 0.5066 | 210800
2443 | 4 | 102 | 18 | 0 | 0.058389 | 0.39513 | 210800
2444 | 4 | 102 | 19 | 1 | 0 | 0.31208 | 210600
2445 | 4 | 102 | 20 | 1 | 0 | 0.3192 | 210400
2446 | 4 | 102 | 21 | 0 | 0 | 0.64371 | 210400
2447 | 4 | 102 | 22 | 0 | 0 | 0.55193 | 210400
2448 | 4 | 102 | 23 | 0 | 0 | 0.47117 | 210400
2449 | 4 | 103 | 0 | 0 | 0 | 0.52799 | 210400
2450 | 4 | 103 | 1 | 0 | 0 | 0.4335 | 210400
2451 | 4 | 103 | 2 | 0 | 0 | 0.4273 | 210400
2452 | 4 | 103 | 3 | 0 | 0 | 0.59119 | 210400
2453 | 4 | 103 | 4 | 0 | 0 | 0.66492 | 210400
2454 | 4 | 103 | 5 | 0 | 0 | 0.81341 | 210400
2455 | 4 | 103 | 6 | 0 | 0.049785 | 1 | 210400
2456 | 4 | 103 | 7 | 1 | 0.30085 | 0.84639 | 210200
2457 | 4 | 103 | 8 | 1 | 0.60378 | 0.7629 | 210000
2458 | 4 | 103 | 9 | 0 | 0.89834 | 0.62848 | 210000
2459 | 4 | 103 | 10 | 0 | 1 | 0.58758 | 210000
2460 | 4 | 103 | 11 | 0 | 1 | 0.53566 | 210000
2461 | 4 | 103 | 12 | 0 | 1 | 0.48484 | 210000
2462 | 4 | 103 | 13 | 0 | 1 | 0.33912 | 210000
2463 | 4 | 103 | 14 | 0 | 1 | 0.30572 | 210000
2464 | 4 | 103 | 15 | 0 | 0.89834 | 0.49752 | 210000
2465 | 4 | 103 | 16 | 0 | 0.60378 | 0.53253 | 210000
2466 | 4 | 103 | 17 | 0 | 0.30085 | 0.83632 | 210000
2467 | 4 | 103 | 18 | 0 | 0.049785 | 0.78791 | 210000
2468 | 4 | 103 | 19 | 1 | 0 | 0.67988 | 209800
2469 | 4 | 103 | 20 | 1 | 0 | 0.92658 | 209600
2470 | 4 | 103 | 21 | 0 | 0 | 0.93618 | 209600
2471 | 4 | 103 | 22 | 0 | 0 | 1 | 209600
2472 | 4 | 103 | 23 | 0 | 0 | 0.94755 | 209600
2473 | 4 | 104 | 0 | 0 | 0 | 0.84217 | 209600
2474 | 4 | 104 | 1 | 0 | 0 | 1 | 209600
2475 | 4 | 104 | 2 | 0 | 0 | 1 | 209600
2476 | 4 | 104 | 3 | 0 | 0 | 0.45798 | 209600
2477 | 4 | 104 | 4 | 0 | 0 | 0.40305 | 209600
2478 | 4 | 104 | 5 | 0 | 0 | 0.35706 | 209600
2479 | 4 | 104 | 6 | 0 | 0.058585 | 0.37726 | 209600
2480 | 4 | 104 | 7 | 1 | 0.35403 | 0.44212 | 209400
2481 | 4 | 104 | 8 | 1 | 0.71051 | 0.43422 | 209200
2482 | 4 | 104 | 9 | 0 | 1 | 0.50934 | 209200
2483 | 4 | 104 | 10 | 0 | 1 | 0.3512 | 209200
2484 | 4 | 104 | 11 | 0 | 1 | 0.49049 | 209200
2485 | 4 | 104 | 12 | 0 | 1 | 0.63027 | 209200
2486 | 4 | 104 | 13 | 0 | 1 | 0.34591 | 209200
2487 | 4 | 104 | 14 | 0 | 1 | 0.32327 | 209200
2488 | 4 | 104 | 15 | 0 | 1 | 0.42319 | 209200
2489 | 4 | 104 | 16 | 0 | 0.71051 | 0.60521 | 209200
2490 | 4 | 104 | 17 | 0 | 0.35403 | 0.50448 | 209200
2491 | 4 | 104 | 18 | 0 | 0.058585 | 0.30565 | 209200
2492 | 4 | 104 | 19 | 1 | 0 | 0.35013 | 209000
2493 | 4 | 104 | 20 | 1 | 0 | 0.27604 | 208800
2494 | 4 | 104 | 21 | 0 | 0 | 0.34203 | 208800
2495 | 4 | 104 | 22 | 0 | 0 | 0.35884 | 208800
2496 | 4 | 104 | 23 | 0 | 0 | 0.36828 | 208800
2497 | 4 | 105 | 0 | 0 | 0 | 0.29102 | 208800
2498 | 4 | 105 | 1 | 0 | 0 | 0.27171 | 208800
2499 | 4 | 105 | 2 | 0 | 0 | 0.32947 | 208800
2500 | 4 | 105 | 3 | 0 | 0 | 0.42084 | 208800
2501 | 4 | 105 | 4 | 0 | 0 | 0.45728 | 208800
2502 | 4 | 105 | 5 | 0 | 0 | 0.37134 | 208800
2503 | 4 | 105 | 6 | 0 | 0.042997 | 0.40601 | 208800
2504 | 4 | 105 | 7 | 1 | 0.25983 | 0.57097 | 208600
2505 | 4 | 105 | 8 | 1 | 0.52145 | 0.73874 | 208400
2506 | 4 | 105 | 9 | 0 | 0.77585 | 0.67441 | 208400
2507 | 4 | 105 | 10 | 0 | 0.98576 | 0.68378 | 208400
2508 | 4 | 105 | 11 | 0 | 1 | 0.58894 | 208400
2509 | 4 | 105 | 12 | 0 | 1 | 0.56151 | 208400
2510 | 4 | 105 | 13 | 0 | 1 | 0.63406 | 208400
2511 | 4 | 105 | 14 | 0 | 0.98576 | 0.43469 | 208400
2512 | 4 | 105 | 15 | 0 | 0.77585 | 0.33517 | 208400
2513 | 4 | 105 | 16 | 0 | 0.52145 | 0.55893 | 208400
2514 | 4 | 105 | 17 | 0 | 0.25983 | 0.67779 | 208400
2515 | 4 | 105 | 18 | 0 | 0.042997 | 0.75582 | 208400
2516 | 4 | 105 | 19 | 1 | 0 | 0.68702 | 208200
2517 | 4 | 105 | 20 | 1 | 0 | 0.59036 | 208000
2518 | 4 | 105 | 21 | 0 | 0 | 0.39141 | 208000
2519 | 4 | 105 | 22 | 0 | 0 | 0.23946 | 208000
2520 | 4 | 105 | 23 | 0 | 0 | 0.28039 | 208000
2521 | 4 | 106 | 0 | 0 | 0 | 0.30303 | 208000
2522 | 4 | 106 | 1 | 0 | 0 | 0.31664 | 208000
2523 | 4 | 106 | 2 | 0 | 0 | 0.23939 | 208000
2524 | 4 | 106 | 3 | 0 | 0 | 0.3167 | 208000
2525 | 4 | 106 | 4 | 0 | 0 | 0.42736 | 208000
2526 | 4 | 106 | 5 | 0 | 0 | 0.42288 | 208000
2527 | 4 | 106 | 6 | 0 | 0.050537 | 0.38977 | 208000
2528 | 4 | 106 | 7 | 1 | 0.30539 | 0.46671 | 207800
2529 | 4 | 106 | 8 | 1 | 0.6129 | 0.45122 | 207600
2530 | 4 | 106 | 9 | 0 | 0.9119 | 0.39535 | 207600
2531 | 4 | 106 | 10 | 0 | 1 | 0.39015 | 207600
2532 | 4 | 106 | 11 | 0 | 1 | 0.33985 | 207600
2533 | 4 | 106 | 12 | 0 | 1 | 0.25039 | 207600
2534 | 4 | 106 | 13 | 0 | 1 | 0.31314 | 207600
2535 | 4 | 106 | 14 | 0 | 1 | 0.30262 | 207600
2536 | 4 | 106 | 15 | 0 | 0.9119 | 0.44586 | 207600
2537 | 4 | 106 | 16 | 0 | 0.6129 | 0.43498 | 207600
2538 | 4 | 106 | 17 | 0 | 0.30539 | 0.4984 | 207600
2539 | 4 | 106 | 18 | 0 | 0.050537 | 0.36916 | 207600
2540 | 4 | 106 | 19 | 1 | 0 | 0.47128 | 207400
2541 | 4 | 106 | 20 | 1 | 0 | 0.25336 | 207200
2542 | 4 | 106 | 21 | 0 | 0 | 0.31374 | 207200
2543 | 4 | 106 | 22 | 0 | 0 | 0.23143 | 207200
2544 | 4 | 106 | 23 | 0 | 0 | 0.29001 | 207200
2545 | 4 | 107 | 0 | 0 | 0 | 0.24377 | 207200
2546 | 4 | 107 | 1 | 0 | 0 | 0.25607 | 207200
2547 | 4 | 107 | 2 | 0 | 0 | 0.18042 | 207200
2548 | 4 | 107 | 3 | 0 | 0 | 0.14112 | 207200
2549 | 4 | 107 | 4 | 0 | 0 | 0.098853 | 207200
2550 | 4 | 107 | 5 | 0 | 0 | 0.12454 | 207200
2551 | 4 | 107 | 6 | 0 | 0.050359 | 0.10265 | 207200
2552 | 4 | 107 | 7 | 1 | 0.30432 | 0.071873 | 207000
2553 | 4 | 107 | 8 | 1 | 0.61074 | 0.068338 | 206800
2554 | 4 | 107 | 9 | 0 | 0.9087 | 0.074436 | 206800
2555 | 4 | 107 | 10 | 0 | 1 | 0.10435 | 206800
2556 | 4 | 107 | 11 | 0 | 1 | 0.11343 | 206800
2557 | 4 | 107 | 12 | 0 | 1 | 0.12983 | 206800
2558 | 4 | 107 | 13 | 0 | 1 | 0.1851 | 206800
2559 | 4 | 107 | 14 | 0 | 1 | 0.24656 | 206800
2560 | 4 | 107 | 15 | 0 | 0.9087 | 0.25378 | 206800
2561 | 4 | 107 | 16 | 0 | 0.61074 | 0.30698 | 206800
2562 | 4 | 107 | 17 | 0 | 0.30432 | 0.68683 | 206800
2563 | 4 | 107 | 18 | 0 | 0.050359 | 0.49673 | 206800
2564 | 4 | 107 | 19 | 1 | 0 | 0.45043 | 206600
2565 | 4 | 107 | 20 | 1 | 0 | 0.58281 | 206400
2566 | 4 | 107 | 21 | 0 | 0 | 0.76083 | 206400
2567 | 4 | 107 | 22 | 0 | 0 | 0.68769 | 206400
2568 | 4 | 107 | 23 | 0 | 0 | 0.40759 | 206400
2569 | 4 | 108 | 0 | 0 | 0 | 0.34304 | 206400
2570 | 4 | 108 | 1 | 0 | 0 | 0.25405 | 206400
2571 | 4 | 108 | 2 | 0 | 0 | 0.21329 | 206400
2572 | 4 | 108 | 3 | 0 | 0 | 0.25204 | 206400
2573 | 4 | 108 | 4 | 0 | 0 | 0.33126 | 206400
2574 | 4 | 108 | 5 | 0 | 0 | 0.59857 | 206400
2575 | 4 | 108 | 6 | 0 | 0.058964 | 0.53008 | 206400
2576 | 4 | 108 | 7 | 1 | 0.35632 | 0.40455 | 206200
2577 | 4 | 108 | 8 | 1 | 0.7151 | 0.46137 | 206000
2578 | 4 | 108 | 9 | 0 | 1 | 0.36633 | 206000
2579 | 4 | 108 | 10 | 0 | 1 | 0.33117 | 206000
2580 | 4 | 108 | 11 | 0 | 1 | 0.38508 | 206000
2581 | 4 | 108 | 12 | 0 | 1 | 0.39119 | 206000
2582 | 4 | 108 | 13 | 0 | 1 | 0.40679 | 206000
2583 | 4 | 108 | 14 | 0 | 1 | 0.35111 | 206000
2584 | 4 | 108 | 15 | 0 | 1 | 0.39263 | 206000
2585 | 4 | 108 | 16 | 0 | 0.7151 | 0.35728 | 206000
2586 | 4 | 108 | 17 | 0 | 0.35632 | 0.19568 | 206000
2587 | 4 | 108 | 18 | 0 | 0.058964 | 0.31341 | 206000
2588 | 4 | 108 | 19 | 1 | 0 | 0.24382 | 205800
2589 | 4 | 108 | 20 | 1 | 0 | 0.25604 | 205600
2590 | 4 | 108 | 21 | 0 | 0 | 0.34743 | 205600
2591 | 4 | 108 | 22 | 0 | 0 | 0.20035 | 205600
2592 | 4 | 108 | 23 | 0 | 0 | 0.15484 | 205600
2593 | 4 | 109 | 0 | 0 | 0 | 0.16745 | 205600
2594 | 4 | 109 | 1 | 0 | 0 | 0.1568 | 205600
2595 | 4 | 109 | 2 | 0 | 0 | 0.16217 | 205600
2596 | 4 | 109 | 3 | 0 | 0 | 0.17416 | 205600
2597 | 4 | 109 | 4 | 0 | 0 | 0.21495 | 205600
2598 | 4 | 109 | 5 | 0 | 0 | 0.27868 | 205600
2599 | 4 | 109 | 6 | 0 | 0.047283 | 0.26914 | 205600
2600 | 4 | 109 | 7 | 1 | 0.28573 | 0.25732 | 205400
2601 | 4 | 109 | 8 | 1 | 0.57343 | 0.35869 | 205200
2602 | 4 | 109 | 9 | 0 | 0.85318 | 0.38961 | 205200
2603 | 4 | 109 | 10 | 0 | 1 | 0.69341 | 205200
2604 | 4 | 109 | 11 | 0 | 1 | 0.47009 | 205200
2605 | 4 | 109 | 12 | 0 | 1 | 0.37455 | 205200
2606 | 4 | 109 | 13 | 0 | 1 | 0.26528 | 205200
2607 | 4 | 109 | 14 | 0 | 1 | 0.25781 | 205200
2608 | 4 | 109 | 15 | 0 | 0.85318 | 0.23954 | 205200
2609 | 4 | 109 | 16 | 0 | 0.57343 | 0.27361 | 205200
2610 | 4 | 109 | 17 | 0 | 0.28573 | 0.28413 | 205200
2611 | 4 | 109 | 18 | 0 | 0.047283 | 0.17247 | 205200
2612 | 4 | 109 | 19 | 1 | 0 | 0.23602 | 205000
2613 | 4 | 109 | 20 | 1 | 0 | 0.16463 | 204800
2614 | 4 | 109 | 21 | 0 | 0 | 0.19046 | 204800
2615 | 4 | 109 | 22 | 0 | 0 | 0.20936 | 204800
2616 | 4 | 109 | 23 | 0 | 0 | 0.21609 | 204800
2617 | 4 | 110 | 0 | 0 | 0 | 0.20822 | 204800
2618 | 4 | 110 | 1 | 0 | 0 | 0.25185 | 204800
2619 | 4 | 110 | 2 | 0 | 0 | 0.16837 | 204800
2620 | 4 | 110 | 3 | 0 | 0 | 0.31684 | 204800
2621 | 4 | 110 | 4 | 0 | 0 | 0.38529 | 204800
2622 | 4 | 110 | 5 | 0 | 0 | 0.43174 | 204800
2623 | 4 | 110 | 6 | 0 | 0.059324 | 0.47239 | 204800
2624 | 4 | 110 | 7 | 1 | 0.3585 | 0.7556 | 204600
2625 | 4 | 110 | 8 | 1 | 0.71947 | 0.58168 | 204400
2626 | 4 | 110 | 9 | 0 | 1 | 0.61124 | 204400
2627 | 4 | 110 | 10 | 0 | 1 | 0.7225 | 204400
2628 | 4 | 110 | 11 | 0 | 1 | 0.64921 | 204400
2629 | 4 | 110 | 12 | 0 | 1 | 0.60962 | 204400
2630 | 4 | 110 | 13 | 0 | 1 | 0.50772 | 204400
2631 | 4 | 110 | 14 | 0 | 1 | 0.29312 | 204400
2632 | 4 | 110 | 15 | 0 | 1 | 0.35823 | 204400
2633 | 4 | 110 | 16 | 0 | 0.71947 | 0.44239 | 204400
2634 | 4 | 110 | 17 | 0 | 0.3585 | 0.25152 | 204400
2635 | 4 | 110 | 18 | 0 | 0.059324 | 0.20561 | 204400
2636 | 4 | 110 | 19 | 1 | 0 | 0.20134 | 204200
2637 | 4 | 110 | 20 | 1 | 0 | 0.15443 | 204000
2638 | 4 | 110 | 21 | 0 | 0 | 0.158 | 204000
2639 | 4 | 110 | 22 | 0 | 0 | 0.18831 | 204000
2640 | 4 | 110 | 23 | 0 | 0 | 0.22538 | 204000
2641 | 4 | 111 | 0 | 0 | 0 | 0.2373 | 204000
2642 | 4 | 111 | 1 | 0 | 0 | 0.23277 | 204000
2643 | 4 | 111 | 2 | 0 | 0 | 0.18417 | 204000
2644 | 4 | 111 | 3 | 0 | 0 | 0.17794 | 204000
2645 | 4 | 111 | 4 | 0 | 0 | 0.24406 | 204000
2646 | 4 | 111 | 5 | 0 | 0 | 0.27784 | 204000
2647 | 4 | 111 | 6 | 0 | 0.054946 | 0.22715 | 204000
2648 | 4 | 111 | 7 | 1 | 0.33204 | 0.25836 | 203800
2649 | 4 | 111 | 8 | 1 | 0.66637 | 0.37434 | 203600
2650 | 4 | 111 | 9 | 0 | 0.99146 | 0.52215 | 203600
2651 | 4 | 111 | 10 | 0 | 1 | 0.8056 | 203600
2652 | 4 | 111 | 11 | 0 | 1 | 0.71438 | 203600
2653 | 4 | 111 | 12 | 0 | 1 | 1 | 203600
2654 | 4 | 111 | 13 | 0 | 1 | 0.76939 | 203600
2655 | 4 | 111 | 14 | 0 | 1 | 0.68366 | 203600
2656 | 4 | 111 | 15 | 0 | 0.99146 | 0.49449 | 203600
2657 | 4 | 111 | 16 | 0 | 0.66637 | 0.59902 | 203600
2658 | 4 | 111 | 17 | 0 | 0.33204 | 0.63424 | 203600
2659 | 4 | 111 | 18 | 0 | 0.054946 | 0.39255 | 203600
2660 | 4 | 111 | 19 | 1 | 0 | 0.40885 | 203400
2661 | 4 | 111 | 20 | 1 | 0 | 0.51169 | 203200
2662 | 4 | 111 | 21 | 0 | 0 | 0.34717 | 203200
2663 | 4 | 111 | 22 | 0 | 0 | 0.29429 | 203200
2664 | 4 | 111 | 23 | 0 | 0 | 0.34459 | 203200
2665 | 4 | 112 | 0 | 0 | 0 | 0.32205 | 203200
2666 | 4 | 112 | 1 | 0 | 0 | 0.38681 | 203200
2667 | 4 | 112 | 2 | 0 | 0 | 0.2848 | 203200
2668 | 4 | 112 | 3 | 0 | 0 | 0.32177 | 203200
2669 | 4 | 112 | 4 | 0 | 0 | 0.34849 | 203200
2670 | 4 | 112 | 5 | 0 | 0 | 0.31253 | 203200
2671 | 4 | 112 | 6 | 0 | 0.064696 | 0.35634 | 203200
2672 | 4 | 112 | 7 | 1 | 0.39096 | 0.45632 | 203000
2673 | 4 | 112 | 8 | 1 | 0.78461 | 0.57213 | 202800
2674 | 4 | 112 | 9 | 0 | 1 | 0.6862 | 202800
2675 | 4 | 112 | 10 | 0 | 1 | 0.69014 | 202800
2676 | 4 | 112 | 11 | 0 | 1 | 0.83902 | 202800
2677 | 4 | 112 | 12 | 0 | 1 | 0.5818 | 202800
2678 | 4 | 112 | 13 | 0 | 1 | 0.93428 | 202800
2679 | 4 | 112 | 14 | 0 | 1 | 1 | 202800
2680 | 4 | 112 | 15 | 0 | 1 | 0.86139 | 202800
2681 | 4 | 112 | 16 | 0 | 0.78461 | 0.78765 | 202800
2682 | 4 | 112 | 17 | 0 | 0.39096 | 0.55472 | 202800
2683 | 4 | 112 | 18 | 0 | 0.064696 | 0.53418 | 202800
2684 | 4 | 112 | 19 | 1 | 0 | 0.54512 | 202600
2685 | 4 | 112 | 20 | 1 | 0 | 0.52331 | 202400
2686 | 4 | 112 | 21 | 0 | 0 | 0.46171 | 202400
2687 | 4 | 112 | 22 | 0 | 0 | 0.58596 | 202400
2688 | 4 | 112 | 23 | 0 | 0 | 0.62826 | 202400
2689 | 4 | 113 | 0 | 0 | 0 | 0.59573 | 202400
2690 | 4 | 113 | 1 | 0 | 0 | 0.84706 | 202400
2691 | 4 | 113 | 2 | 0 | 0 | 1 | 202400
2692 | 4 | 113 | 3 | 0 | 0 | 0.88566 | 202400
2693 | 4 | 113 | 4 | 0 | 0 | 1 | 202400
2694 | 4 | 113 | 5 | 0 | 0 | 1 | 202400
2695 | 4 | 113 | 6 | 0 | 0.059974 | 0.9133 | 202400
2696 | 4 | 113 | 7 | 1 | 0.36242 | 1 | 202200
2697 | 4 | 113 | 8 | 1 | 0.72735 | 1 | 202000
2698 | 4 | 113 | 9 | 0 | 1 | 1 | 202000
2699 | 4 | 113 | 10 | 0 | 1 | 0.90672 | 202000
2700 | 4 | 113 | 11 | 0 | 1 | 0.75419 | 202000
2701 | 4 | 113 | 12 | 0 | 1 | 0.55395 | 202000
2702 | 4 | 113 | 13 | 0 | 1 | 0.46851 | 202000
2703 | 4 | 113 | 14 | 0 | 1 | 0.47282 | 202000
2704 | 4 | 113 | 15 | 0 | 1 | 0.58549 | 202000
2705 | 4 | 113 | 16 | 0 | 0.72735 | 0.45871 | 202000
2706 | 4 | 113 | 17 | 0 | 0.36242 | 0.49417 | 202000
2707 | 4 | 113 | 18 | 0 | 0.059974 | 0.61996 | 202000
2708 | 4 | 113 | 19 | 1 | 0 | 1 | 201800
2709 | 4 | 113 | 20 | 1 | 0 | 0.63939 | 201600
2710 | 4 | 113 | 21 | 0 | 0 | 0.53319 | 201600
2711 | 4 | 113 | 22 | 0 | 0 | 0.39781 | 201600
2712 | 4 | 113 | 23 | 0 | 0 | 0.48676 | 201600
2713 | 4 | 114 | 0 | 0 | 0 | 0.68268 | 201600
2714 | 4 | 114 | 1 | 0 | 0 | 0.56756 | 201600
2715 | 4 | 114 | 2 | 0 | 0 | 0.45933 | 201600
2716 | 4 | 114 | 3 | 0 | 0 | 0.34827 | 201600
2717 | 4 | 114 | 4 | 0 | 0 | 0.25586 | 201600
2718 | 4 | 114 | 5 | 0 | 0 | 0.24256 | 201600
2719 | 4 | 114 | 6 | 0 | 0.051161 | 0.24693 | 201600
2720 | 4 | 114 | 7 | 1 | 0.30917 | 0.20278 | 201400
2721 | 4 | 114 | 8 | 1 | 0.62047 | 0.27664 | 201200
2722 | 4 | 114 | 9 | 0 | 0.92317 | 0.34059 | 201200
2723 | 4 | 114 | 10 | 0 | 1 | 0.27676 | 201200
2724 | 4 | 114 | 11 | 0 | 1 | 0.49512 | 201200
2725 | 4 | 114 | 12 | 0 | 1 | 0.45353 | 201200
2726 | 4 | 114 | 13 | 0 | 1 | 0.63357 | 201200
2727 | 4 | 114 | 14 | 0 | 1 | 0.75216 | 201200
2728 | 4 | 114 | 15 | 0 | 0.92317 | 0.62398 | 201200
2729 | 4 | 114 | 16 | 0 | 0.62047 | 0.34415 | 201200
2730 | 4 | 114 | 17 | 0 | 0.30917 | 0.51015 | 201200
2731 | 4 | 114 | 18 | 0 | 0.051161 | 0.48594 | 201200
2732 | 4 | 114 | 19 | 1 | 0 | 0.55425 | 201000
2733 | 4 | 114 | 20 | 1 | 0 | 0.34744 | 200800
2734 | 4 | 114 | 21 | 0 | 0 | 0.39486 | 200800
2735 | 4 | 114 | 22 | 0 | 0 | 0.34784 | 200800
2736 | 4 | 114 | 23 | 0 | 0 | 0.26017 | 200800
2737 | 4 | 115 | 0 | 0 | 0 | 0.28169 | 200800
2738 | 4 | 115 | 1 | 0 | 0 | 0.20021 | 200800
2739 | 4 | 115 | 2 | 0 | 0 | 0.23252 | 200800
2740 | 4 | 115 | 3 | 0 | 0 | 0.17945 | 200800
2741 | 4 | 115 | 4 | 0 | 0 | 0.15109 | 200800
2742 | 4 | 115 | 5 | 0 | 0 | 0.17792 | 200800
2743 | 4 | 115 | 6 | 0 | 0.057126 | 0.17522 | 200800
2744 | 4 | 115 | 7 | 1 | 0.34521 | 0.20176 | 200600
2745 | 4 | 115 | 8 | 1 | 0.69281 | 0.35673 | 200400
2746 | 4 | 115 | 9 | 0 | 1 | 0.28366 | 200400
2747 | 4 | 115 | 10 | 0 | 1 | 0.31188 | 200400
2748 | 4 | 115 | 11 | 0 | 1 | 0.28853 | 200400
2749 | 4 | 115 | 12 | 0 | 1 | 0.26285 | 200400
2750 | 4 | 115 | 13 | 0 | 1 | 0.33621 | 200400
2751 | 4 | 115 | 14 | 0 | 1 | 0.28675 | 200400
2752 | 4 | 115 | 15 | 0 | 1 | 0.28249 | 200400
2753 | 4 | 115 | 16 | 0 | 0.69281 | 0.32582 | 200400
2754 | 4 | 115 | 17 | 0 | 0.34521 | 0.24522 | 200400
2755 | 4 | 115 | 18 | 0 | 0.057126 | 0.22217 | 200400
2756 | 4 | 115 | 19 | 1 | 0 | 0.15691 | 200200
2757 | 4 | 115 | 20 | 1 | 0 | 0.21498 | 200000
2758 | 4 | 115 | 21 | 0 | 0 | 0.2385 | 200000
2759 | 4 | 115 | 22 | 0 | 0 | 0.25415 | 200000
2760 | 4 | 115 | 23 | 0 | 0 | 0.32715 | 200000
2761 | 4 | 116 | 0 | 0 | 0 | 0.29874 | 200000
2762 | 4 | 116 | 1 | 0 | 0 | 0.299 | 200000
2763 | 4 | 116 | 2 | 0 | 0 | 0.24583 | 200000
2764 | 4 | 116 | 3 | 0 | 0 | 0.19004 | 200000
2765 | 4 | 116 | 4 | 0 | 0 | 0.20777 | 200000
2766 | 4 | 116 | 5 | 0 | 0 | 0.22469 | 200000
2767 | 4 | 116 | 6 | 0 | 0.049577 | 0.23161 | 200000
2768 | 4 | 116 | 7 | 1 | 0.29959 | 0.51266 | 199800
2769 | 4 | 116 | 8 | 1 | 0.60126 | 0.54014 | 199600
2770 | 4 | 116 | 9 | 0 | 0.89458 | 0.30516 | 199600
2771 | 4 | 116 | 10 | 0 | 1 | 0.40716 | 199600
2772 | 4 | 116 | 11 | 0 | 1 | 0.34434 | 199600
2773 | 4 | 116 | 12 | 0 | 1 | 0.38658 | 199600
2774 | 4 | 116 | 13 | 0 | 1 | 0.35918 | 199600
2775 | 4 | 116 | 14 | 0 | 1 | 0.44201 | 199600
2776 | 4 | 116 | 15 | 0 | 0.89458 | 0.34903 | 199600
2777 | 4 | 116 | 16 | 0 | 0.60126 | 0.26854 | 199600
2778 | 4 | 116 | 17 | 0 | 0.29959 | 0.37077 | 199600
2779 | 4 | 116 | 18 | 0 | 0.049577 | 0.27758 | 199600
2780 | 4 | 116 | 19 | 1 | 0 | 0.19657 | 199400
2781 | 4 | 116 | 20 | 1 | 0 | 0.144 | 199200
2782 | 4 | 116 | 21 | 0 | 0 | 0.095759 | 199200
2783 | 4 | 116 | 22 | 0 | 0 | 0.075038 | 199200
2784 | 4 | 116 | 23 | 0 | 0 | 0.096239 | 199200
2785 | 4 | 117 | 0 | 0 | 0 | 0.084681 | 199200
2786 | 4 | 117 | 1 | 0 | 0 | 0.074515 | 199200
2787 | 4 | 117 | 2 | 0 | 0 | 0.12418 | 199200
2788 | 4 | 117 | 3 | 0 | 0 | 0.16155 | 199200
2789 | 4 | 117 | 4 | 0 | 0 | 0.16975 | 199200
2790 | 4 | 117 | 5 | 0 | 0 | 0.15185 | 199200
2791 | 4 | 117 | 6 | 0 | 0.05096 | 0.12754 | 199200
2792 | 4 | 117 | 7 | 1 | 0.30795 | 0.12248 | 199000
2793 | 4 | 117 | 8 | 1 | 0.61803 | 0.13498 | 198800
2794 | 4 | 117 | 9 | 0 | 0.91954 | 0.11249 | 198800
2795 | 4 | 117 | 10 | 0 | 1 | 0.099138 | 198800
2796 | 4 | 117 | 11 | 0 | 1 | 0.13922 | 198800
2797 | 4 | 117 | 12 | 0 | 1 | 0.21284 | 198800
2798 | 4 | 117 | 13 | 0 | 1 | 0.18554 | 198800
2799 | 4 | 117 | 14 | 0 | 1 | 0.22058 | 198800
2800 | 4 | 117 | 15 | 0 | 0.91954 | 0.23853 | 198800
2801 | 4 | 117 | 16 | 0 | 0.61803 | 0.21636 | 198800
2802 | 4 | 117 | 17 | 0 | 0.30795 | 0.3338 | 198800
2803 | 4 | 117 | 18 | 0 | 0.05096 | 0.28944 | 198800
2804 | 4 | 117 | 19 | 1 | 0 | 0.20295 | 198600
2805 | 4 | 117 | 20 | 1 | 0 | 0.14911 | 198400
2806 | 4 | 117 | 21 | 0 | 0 | 0.13896 | 198400
2807 | 4 | 117 | 22 | 0 | 0 | 0.12837 | 198400
2808 | 4 | 117 | 23 | 0 | 0 | 0.14647 | 198400
2809 | 4 | 118 | 0 | 0 | 0 | 0.1356 | 198400
2810 | 4 | 118 | 1 | 0 | 0 | 0.12947 | 198400
2811 | 4 | 118 | 2 | 0 | 0 | 0.15468 | 198400
2812 | 4 | 118 | 3 | 0 | 0 | 0.12407 | 198400
2813 | 4 | 118 | 4 | 0 | 0 | 0.10749 | 198400
2814 | 4 | 118 | 5 | 0 | 0 | 0.1332 | 198400
2815 | 4 | 118 | 6 | 0 | 0.056021 | 0.088239 | 198400
2816 | 4 | 118 | 7 | 1 | 0.33853 | 0.09375 | 198200
2817 | 4 | 118 | 8 | 1 | 0.67941 | 0.077895 | 198000
2818 | 4 | 118 | 9 | 0 | 1 | 0.092989 | 198000
2819 | 4 | 118 | 10 | 0 | 1 | 0.1027 | 198000
2820 | 4 | 118 | 11 | 0 | 1 | 0.14981 | 198000
2821 | 4 | 118 | 12 | 0 | 1 | 0.19929 | 198000
2822 | 4 | 118 | 13 | 0 | 1 | 0.21744 | 198000
2823 | 4 | 118 | 14 | 0 | 1 | 0.21457 | 198000
2824 | 4 | 118 | 15 | 0 | 1 | 0.17895 | 198000
2825 | 4 | 118 | 16 | 0 | 0.67941 | 0.17305 | 198000
2826 | 4 | 118 | 17 | 0 | 0.33853 | 0.22642 | 198000
2827 | 4 | 118 | 18 | 0 | 0.056021 | 0.20923 | 198000
2828 | 4 | 118 | 19 | 1 | 0 | 0.18679 | 197800
2829 | 4 | 118 | 20 | 1 | 0 | 0.20372 | 197600
2830 | 4 | 118 | 21 | 0 | 0 | 0.18547 | 197600
2831 | 4 | 118 | 22 | 0 | 0 | 0.1073 | 197600
2832 | 4 | 118 | 23 | 0 | 0 | 0.15645 | 197600
2833 | 4 | 119 | 0 | 0 | 0 | 0.18108 | 197600
2834 | 4 | 119 | 1 | 0 | 0 | 0.18994 | 197600
2835 | 4 | 119 | 2 | 0 | 0 | 0.17747 | 197600
2836 | 4 | 119 | 3 | 0 | 0 | 0.22754 | 197600
2837 | 4 | 119 | 4 | 0 | 0 | 0.22839 | 197600
2838 | 4 | 119 | 5 | 0 | 0 | 0.15887 | 197600
2839 | 4 | 119 | 6 | 0 | 0.054308 | 0.12262 | 197600
2840 | 4 | 119 | 7 | 1 | 0.32818 | 0.11965 | 197400
2841 | 4 | 119 | 8 | 1 | 0.65863 | 0.15312 | 197200
2842 | 4 | 119 | 9 | 0 | 0.97995 | 0.14376 | 197200
2843 | 4 | 119 | 10 | 0 | 1 | 0.15649 | 197200
2844 | 4 | 119 | 11 | 0 | 1 | 0.12211 | 197200
2845 | 4 | 119 | 12 | 0 | 1 | 0.12351 | 197200
2846 | 4 | 119 | 13 | 0 | 1 | 0.11203 | 197200
2847 | 4 | 119 | 14 | 0 | 1 | 0.080637 | 197200
2848 | 4 | 119 | 15 | 0 | 0.97995 | 0.11433 | 197200
2849 | 4 | 119 | 16 | 0 | 0.65863 | 0.12326 | 197200
2850 | 4 | 119 | 17 | 0 | 0.32818 | 0.10832 | 197200
2851 | 4 | 119 | 18 | 0 | 0.054308 | 0.11942 | 197200
2852 | 4 | 119 | 19 | 1 | 0 | 0.11758 | 197000
2853 | 4 | 119 | 20 | 1 | 0 | 0.10556 | 196800
2854 | 4 | 119 | 21 | 0 | 0 | 0.19435 | 196800
2855 | 4 | 119 | 22 | 0 | 0 | 0.25033 | 196800
2856 | 4 | 119 | 23 | 0 | 0 | 0.32712 | 196800
2857 | 4 | 120 | 0 | 0 | 0 | 0.38522 | 196800
2858 | 4 | 120 | 1 | 0 | 0 | 0.3638 | 196800
2859 | 4 | 120 | 2 | 0 | 0 | 0.27024 | 196800
2860 | 4 | 120 | 3 | 0 | 0 | 0.30644 | 196800
2861 | 4 | 120 | 4 | 0 | 0 | 0.35656 | 196800
2862 | 4 | 120 | 5 | 0 | 0 | 0.40404 | 196800
2863 | 4 | 120 | 6 | 0 | 0.054685 | 0.39349 | 196800
2864 | 4 | 120 | 7 | 1 | 0.33047 | 0.47133 | 196600
2865 | 4 | 120 | 8 | 1 | 0.66321 | 0.40419 | 196400
2866 | 4 | 120 | 9 | 0 | 0.98676 | 0.5407 | 196400
2867 | 4 | 120 | 10 | 0 | 1 | 0.58698 | 196400
2868 | 4 | 120 | 11 | 0 | 1 | 0.6973 | 196400
2869 | 4 | 120 | 12 | 0 | 1 | 0.53612 | 196400
2870 | 4 | 120 | 13 | 0 | 1 | 0.62361 | 196400
2871 | 4 | 120 | 14 | 0 | 1 | 0.63135 | 196400
2872 | 4 | 120 | 15 | 0 | 0.98676 | 0.68773 | 196400
2873 | 4 | 120 | 16 | 0 | 0.66321 | 0.71573 | 196400
2874 | 4 | 120 | 17 | 0 | 0.33047 | 0.78291 | 196400
2875 | 4 | 120 | 18 | 0 | 0.054685 | 0.95232 | 196400
2876 | 4 | 120 | 19 | 1 | 0 | 1 | 196200
2877 | 4 | 120 | 20 | 1 | 0 | 0.80177 | 196000
2878 | 4 | 120 | 21 | 0 | 0 | 0.68859 | 196000
2879 | 4 | 120 | 22 | 0 | 0 | 0.74636 | 196000
2880 | 4 | 120 | 23 | 0 | 0 | 0.56493 | 196000
2881 | 5 | 121 | 0 | 0 | 0 | 0.46248 | 196000
2882 | 5 | 121 | 1 | 0 | 0 | 0.51107 | 196000
2883 | 5 | 121 | 2 | 0 | 0 | 0.47118 | 196000
2884 | 5 | 121 | 3 | 0 | 0 | 0.50658 | 196000
2885 | 5 | 121 | 4 | 0 | 0 | 0.85342 | 196000
2886 | 5 | 121 | 5 | 0 | 0 | 0.76643 | 196000
2887 | 5 | 121 | 6 | 0 | 0.12819 | 0.83984 | 196000
2888 | 5 | 121 | 7 | 1 | 0.43794 | 0.54075 | 195800
2889 | 5 | 121 | 8 | 1 | 0.78581 | 0.46911 | 195600
2890 | 5 | 121 | 9 | 0 | 1 | 0.42382 | 195600
2891 | 5 | 121 | 10 | 0 | 1 | 0.45886 | 195600
2892 | 5 | 121 | 11 | 0 | 1 | 0.49877 | 195600
2893 | 5 | 121 | 12 | 0 | 1 | 0.57857 | 195600
2894 | 5 | 121 | 13 | 0 | 1 | 0.45903 | 195600
2895 | 5 | 121 | 14 | 0 | 1 | 0.51922 | 195600
2896 | 5 | 121 | 15 | 0 | 1 | 0.27421 | 195600
2897 | 5 | 121 | 16 | 0 | 0.78581 | 0.21919 | 195600
2898 | 5 | 121 | 17 | 0 | 0.43794 | 0.17887 | 195600
2899 | 5 | 121 | 18 | 0 | 0.12819 | 0.22615 | 195600
2900 | 5 | 121 | 19 | 1 | 0 | 0.21488 | 195400
2901 | 5 | 121 | 20 | 1 | 0 | 0.2217 | 195200
2902 | 5 | 121 | 21 | 0 | 0 | 0.24929 | 195200
2903 | 5 | 121 | 22 | 0 | 0 | 0.31739 | 195200
2904 | 5 | 121 | 23 | 0 | 0 | 0.26578 | 195200
2905 | 5 | 122 | 0 | 0 | 0 | 0.19696 | 195200
2906 | 5 | 122 | 1 | 0 | 0 | 0.21082 | 195200
2907 | 5 | 122 | 2 | 0 | 0 | 0.2265 | 195200
2908 | 5 | 122 | 3 | 0 | 0 | 0.29628 | 195200
2909 | 5 | 122 | 4 | 0 | 0 | 0.21785 | 195200
2910 | 5 | 122 | 5 | 0 | 0 | 0.2078 | 195200
2911 | 5 | 122 | 6 | 0 | 0.12392 | 0.12344 | 195200
2912 | 5 | 122 | 7 | 1 | 0.42335 | 0.17958 | 195000
2913 | 5 | 122 | 8 | 1 | 0.75963 | 0.16948 | 194800
2914 | 5 | 122 | 9 | 0 | 1 | 0.15064 | 194800
2915 | 5 | 122 | 10 | 0 | 1 | 0.24437 | 194800
2916 | 5 | 122 | 11 | 0 | 1 | 0.34162 | 194800
2917 | 5 | 122 | 12 | 0 | 1 | 0.37723 | 194800
2918 | 5 | 122 | 13 | 0 | 1 | 0.32201 | 194800
2919 | 5 | 122 | 14 | 0 | 1 | 0.39976 | 194800
2920 | 5 | 122 | 15 | 0 | 1 | 0.42903 | 194800
2921 | 5 | 122 | 16 | 0 | 0.75963 | 0.33627 | 194800
2922 | 5 | 122 | 17 | 0 | 0.42335 | 0.34722 | 194800
2923 | 5 | 122 | 18 | 0 | 0.12392 | 0.34449 | 194800
2924 | 5 | 122 | 19 | 1 | 0 | 0.20242 | 194600
2925 | 5 | 122 | 20 | 1 | 0 | 0.21342 | 194400
2926 | 5 | 122 | 21 | 0 | 0 | 0.22926 | 194400
2927 | 5 | 122 | 22 | 0 | 0 | 0.29241 | 194400
2928 | 5 | 122 | 23 | 0 | 0 | 0.27119 | 194400
2929 | 5 | 123 | 0 | 0 | 0 | 0.35532 | 194400
2930 | 5 | 123 | 1 | 0 | 0 | 0.54158 | 194400
2931 | 5 | 123 | 2 | 0 | 0 | 0.53788 | 194400
2932 | 5 | 123 | 3 | 0 | 0 | 0.57802 | 194400
2933 | 5 | 123 | 4 | 0 | 0 | 0.38143 | 194400
2934 | 5 | 123 | 5 | 0 | 0 | 0.44905 | 194400
2935 | 5 | 123 | 6 | 0 | 0.11756 | 0.36471 | 194400
2936 | 5 | 123 | 7 | 1 | 0.4016 | 0.38671 | 194200
2937 | 5 | 123 | 8 | 1 | 0.7206 | 0.26393 | 194000
2938 | 5 | 123 | 9 | 0 | 1 | 0.34874 | 194000
2939 | 5 | 123 | 10 | 0 | 1 | 0.25027 | 194000
2940 | 5 | 123 | 11 | 0 | 1 | 0.30402 | 194000
2941 | 5 | 123 | 12 | 0 | 1 | 0.1839 | 194000
2942 | 5 | 123 | 13 | 0 | 1 | 0.14392 | 194000
2943 | 5 | 123 | 14 | 0 | 1 | 0.16134 | 194000
2944 | 5 | 123 | 15 | 0 | 1 | 0.15407 | 194000
2945 | 5 | 123 | 16 | 0 | 0.7206 | 0.19926 | 194000
2946 | 5 | 123 | 17 | 0 | 0.4016 | 0.27728 | 194000
2947 | 5 | 123 | 18 | 0 | 0.11756 | 0.35625 | 194000
2948 | 5 | 123 | 19 | 1 | 0 | 0.3868 | 193800
2949 | 5 | 123 | 20 | 1 | 0 | 0.34539 | 193600
2950 | 5 | 123 | 21 | 0 | 0 | 0.25985 | 193600
2951 | 5 | 123 | 22 | 0 | 0 | 0.40292 | 193600
2952 | 5 | 123 | 23 | 0 | 0 | 0.43701 | 193600
2953 | 5 | 124 | 0 | 0 | 0 | 0.27399 | 193600
2954 | 5 | 124 | 1 | 0 | 0 | 0.20763 | 193600
2955 | 5 | 124 | 2 | 0 | 0 | 0.24761 | 193600
2956 | 5 | 124 | 3 | 0 | 0 | 0.30054 | 193600
2957 | 5 | 124 | 4 | 0 | 0 | 0.33308 | 193600
2958 | 5 | 124 | 5 | 0 | 0 | 0.37677 | 193600
2959 | 5 | 124 | 6 | 0 | 0.13876 | 0.4831 | 193600
2960 | 5 | 124 | 7 | 1 | 0.47404 | 0.77955 | 193400
2961 | 5 | 124 | 8 | 1 | 0.85058 | 0.55185 | 193200
2962 | 5 | 124 | 9 | 0 | 1 | 0.544 | 193200
2963 | 5 | 124 | 10 | 0 | 1 | 0.63212 | 193200
2964 | 5 | 124 | 11 | 0 | 1 | 1 | 193200
2965 | 5 | 124 | 12 | 0 | 1 | 1 | 193200
2966 | 5 | 124 | 13 | 0 | 1 | 0.94764 | 193200
2967 | 5 | 124 | 14 | 0 | 1 | 1 | 193200
2968 | 5 | 124 | 15 | 0 | 1 | 0.86803 | 193200
2969 | 5 | 124 | 16 | 0 | 0.85058 | 0.5423 | 193200
2970 | 5 | 124 | 17 | 0 | 0.47404 | 0.62466 | 193200
2971 | 5 | 124 | 18 | 0 | 0.13876 | 0.83208 | 193200
2972 | 5 | 124 | 19 | 1 | 0 | 0.83054 | 193000
2973 | 5 | 124 | 20 | 1 | 0 | 0.98865 | 192800
2974 | 5 | 124 | 21 | 0 | 0 | 0.95607 | 192800
2975 | 5 | 124 | 22 | 0 | 0 | 1 | 192800
2976 | 5 | 124 | 23 | 0 | 0 | 0.74144 | 192800
2977 | 5 | 125 | 0 | 0 | 0 | 0.89055 | 192800
2978 | 5 | 125 | 1 | 0 | 0 | 0.90703 | 192800
2979 | 5 | 125 | 2 | 0 | 0 | 0.66984 | 192800
2980 | 5 | 125 | 3 | 0 | 0 | 0.47518 | 192800
2981 | 5 | 125 | 4 | 0 | 0 | 0.48898 | 192800
2982 | 5 | 125 | 5 | 0 | 0 | 0.46771 | 192800
2983 | 5 | 125 | 6 | 0 | 0.12263 | 0.44589 | 192800
2984 | 5 | 125 | 7 | 1 | 0.41895 | 0.3878 | 192600
2985 | 5 | 125 | 8 | 1 | 0.75173 | 0.59913 | 192400
2986 | 5 | 125 | 9 | 0 | 1 | 0.47991 | 192400
2987 | 5 | 125 | 10 | 0 | 1 | 0.44874 | 192400
2988 | 5 | 125 | 11 | 0 | 1 | 0.36406 | 192400
2989 | 5 | 125 | 12 | 0 | 1 | 0.27675 | 192400
2990 | 5 | 125 | 13 | 0 | 1 | 0.28033 | 192400
2991 | 5 | 125 | 14 | 0 | 1 | 0.31422 | 192400
2992 | 5 | 125 | 15 | 0 | 1 | 0.21666 | 192400
2993 | 5 | 125 | 16 | 0 | 0.75173 | 0.22182 | 192400
2994 | 5 | 125 | 17 | 0 | 0.41895 | 0.16409 | 192400
2995 | 5 | 125 | 18 | 0 | 0.12263 | 0.20336 | 192400
2996 | 5 | 125 | 19 | 1 | 0 | 0.26715 | 192200
2997 | 5 | 125 | 20 | 1 | 0 | 0.19535 | 192000
2998 | 5 | 125 | 21 | 0 | 0 | 0.22435 | 192000
2999 | 5 | 125 | 22 | 0 | 0 | 0.20235 | 192000
3000 | 5 | 125 | 23 | 0 | 0 | 0.1807 | 192000
3001 | 5 | 126 | 0 | 0 | 0 | 0.32471 | 192000
3002 | 5 | 126 | 1 | 0 | 0 | 0.38842 | 192000
3003 | 5 | 126 | 2 | 0 | 0 | 0.22043 | 192000
3004 | 5 | 126 | 3 | 0 | 0 | 0.1698 | 192000
3005 | 5 | 126 | 4 | 0 | 0 | 0.23082 | 192000
3006 | 5 | 126 | 5 | 0 | 0 | 0.23589 | 192000
3007 | 5 | 126 | 6 | 0 | 0.12469 | 0.22315 | 192000
3008 | 5 | 126 | 7 | 1 | 0.42598 | 0.23074 | 191800
3009 | 5 | 126 | 8 | 1 | 0.76433 | 0.21636 | 191600
3010 | 5 | 126 | 9 | 0 | 1 | 0.22202 | 191600
3011 | 5 | 126 | 10 | 0 | 1 | 0.30224 | 191600
3012 | 5 | 126 | 11 | 0 | 1 | 0.40414 | 191600
3013 | 5 | 126 | 12 | 0 | 1 | 0.33137 | 191600
3014 | 5 | 126 | 13 | 0 | 1 | 0.33927 | 191600
3015 | 5 | 126 | 14 | 0 | 1 | 0.47278 | 191600
3016 | 5 | 126 | 15 | 0 | 1 | 0.50985 | 191600
3017 | 5 | 126 | 16 | 0 | 0.76433 | 0.45564 | 191600
3018 | 5 | 126 | 17 | 0 | 0.42598 | 0.54108 | 191600
3019 | 5 | 126 | 18 | 0 | 0.12469 | 0.34829 | 191600
3020 | 5 | 126 | 19 | 1 | 0 | 0.28053 | 191400
3021 | 5 | 126 | 20 | 1 | 0 | 0.37135 | 191200
3022 | 5 | 126 | 21 | 0 | 0 | 0.27817 | 191200
3023 | 5 | 126 | 22 | 0 | 0 | 0.27824 | 191200
3024 | 5 | 126 | 23 | 0 | 0 | 0.29447 | 191200
3025 | 5 | 127 | 0 | 0 | 0 | 0.2739 | 191200
3026 | 5 | 127 | 1 | 0 | 0 | 0.35666 | 191200
3027 | 5 | 127 | 2 | 0 | 0 | 0.34604 | 191200
3028 | 5 | 127 | 3 | 0 | 0 | 0.18434 | 191200
3029 | 5 | 127 | 4 | 0 | 0 | 0.23156 | 191200
3030 | 5 | 127 | 5 | 0 | 0 | 0.29616 | 191200
3031 | 5 | 127 | 6 | 0 | 0.12298 | 0.4753 | 191200
3032 | 5 | 127 | 7 | 1 | 0.42015 | 0.47211 | 191000
3033 | 5 | 127 | 8 | 1 | 0.75388 | 0.42504 | 190800
3034 | 5 | 127 | 9 | 0 | 1 | 0.38838 | 190800
3035 | 5 | 127 | 10 | 0 | 1 | 0.51805 | 190800
3036 | 5 | 127 | 11 | 0 | 1 | 0.53369 | 190800
3037 | 5 | 127 | 12 | 0 | 1 | 0.56671 | 190800
3038 | 5 | 127 | 13 | 0 | 1 | 0.65509 | 190800
3039 | 5 | 127 | 14 | 0 | 1 | 0.56606 | 190800
3040 | 5 | 127 | 15 | 0 | 1 | 0.80819 | 190800
3041 | 5 | 127 | 16 | 0 | 0.75388 | 1 | 190800
3042 | 5 | 127 | 17 | 0 | 0.42015 | 0.65968 | 190800
3043 | 5 | 127 | 18 | 0 | 0.12298 | 1 | 190800
3044 | 5 | 127 | 19 | 1 | 0 | 0.78739 | 190600
3045 | 5 | 127 | 20 | 1 | 0 | 0.62445 | 190400
3046 | 5 | 127 | 21 | 0 | 0 | 0.8486 | 190400
3047 | 5 | 127 | 22 | 0 | 0 | 0.83881 | 190400
3048 | 5 | 127 | 23 | 0 | 0 | 1 | 190400
3049 | 5 | 128 | 0 | 0 | 0 | 0.94745 | 190400
3050 | 5 | 128 | 1 | 0 | 0 | 0.83662 | 190400
3051 | 5 | 128 | 2 | 0 | 0 | 1 | 190400
3052 | 5 | 128 | 3 | 0 | 0 | 1 | 190400
3053 | 5 | 128 | 4 | 0 | 0 | 1 | 190400
3054 | 5 | 128 | 5 | 0 | 0 | 1 | 190400
3055 | 5 | 128 | 6 | 0 | 0.11272 | 1 | 190400
3056 | 5 | 128 | 7 | 1 | 0.3851 | 0.85319 | 190200
3057 | 5 | 128 | 8 | 1 | 0.69098 | 0.61436 | 190000
3058 | 5 | 128 | 9 | 0 | 0.98051 | 0.80451 | 190000
3059 | 5 | 128 | 10 | 0 | 1 | 0.93488 | 190000
3060 | 5 | 128 | 11 | 0 | 1 | 0.96098 | 190000
3061 | 5 | 128 | 12 | 0 | 1 | 1 | 190000
3062 | 5 | 128 | 13 | 0 | 1 | 0.93539 | 190000
3063 | 5 | 128 | 14 | 0 | 1 | 1 | 190000
3064 | 5 | 128 | 15 | 0 | 0.98051 | 0.73165 | 190000
3065 | 5 | 128 | 16 | 0 | 0.69098 | 0.64705 | 190000
3066 | 5 | 128 | 17 | 0 | 0.3851 | 0.7182 | 190000
3067 | 5 | 128 | 18 | 0 | 0.11272 | 0.50416 | 190000
3068 | 5 | 128 | 19 | 1 | 0 | 0.27471 | 189800
3069 | 5 | 128 | 20 | 1 | 0 | 0.23161 | 189600
3070 | 5 | 128 | 21 | 0 | 0 | 0.26108 | 189600
3071 | 5 | 128 | 22 | 0 | 0 | 0.28165 | 189600
3072 | 5 | 128 | 23 | 0 | 0 | 0.23041 | 189600
3073 | 5 | 129 | 0 | 0 | 0 | 0.19638 | 189600
3074 | 5 | 129 | 1 | 0 | 0 | 0.26192 | 189600
3075 | 5 | 129 | 2 | 0 | 0 | 0.21869 | 189600
3076 | 5 | 129 | 3 | 0 | 0 | 0.17938 | 189600
3077 | 5 | 129 | 4 | 0 | 0 | 0.15027 | 189600
3078 | 5 | 129 | 5 | 0 | 0 | 0.14305 | 189600
3079 | 5 | 129 | 6 | 0 | 0.11718 | 0.13464 | 189600
3080 | 5 | 129 | 7 | 1 | 0.40033 | 0.14324 | 189400
3081 | 5 | 129 | 8 | 1 | 0.71832 | 0.18339 | 189200
3082 | 5 | 129 | 9 | 0 | 1 | 0.12391 | 189200
3083 | 5 | 129 | 10 | 0 | 1 | 0.12441 | 189200
3084 | 5 | 129 | 11 | 0 | 1 | 0.20125 | 189200
3085 | 5 | 129 | 12 | 0 | 1 | 0.17208 | 189200
3086 | 5 | 129 | 13 | 0 | 1 | 0.15718 | 189200
3087 | 5 | 129 | 14 | 0 | 1 | 0.19598 | 189200
3088 | 5 | 129 | 15 | 0 | 1 | 0.27598 | 189200
3089 | 5 | 129 | 16 | 0 | 0.71832 | 0.25402 | 189200
3090 | 5 | 129 | 17 | 0 | 0.40033 | 0.4379 | 189200
3091 | 5 | 129 | 18 | 0 | 0.11718 | 0.46485 | 189200
3092 | 5 | 129 | 19 | 1 | 0 | 0.5125 | 189000
3093 | 5 | 129 | 20 | 1 | 0 | 0.41009 | 188800
3094 | 5 | 129 | 21 | 0 | 0 | 0.47748 | 188800
3095 | 5 | 129 | 22 | 0 | 0 | 0.42193 | 188800
3096 | 5 | 129 | 23 | 0 | 0 | 0.59874 | 188800
3097 | 5 | 130 | 0 | 0 | 0 | 0.36752 | 188800
3098 | 5 | 130 | 1 | 0 | 0 | 0.30051 | 188800
3099 | 5 | 130 | 2 | 0 | 0 | 0.28602 | 188800
3100 | 5 | 130 | 3 | 0 | 0 | 0.34704 | 188800
3101 | 5 | 130 | 4 | 0 | 0 | 0.26797 | 188800
3102 | 5 | 130 | 5 | 0 | 0 | 0.44193 | 188800
3103 | 5 | 130 | 6 | 0 | 0.12511 | 0.46676 | 188800
3104 | 5 | 130 | 7 | 1 | 0.42741 | 0.46181 | 188600
3105 | 5 | 130 | 8 | 1 | 0.76691 | 0.37959 | 188400
3106 | 5 | 130 | 9 | 0 | 1 | 0.36812 | 188400
3107 | 5 | 130 | 10 | 0 | 1 | 0.39094 | 188400
3108 | 5 | 130 | 11 | 0 | 1 | 0.34316 | 188400
3109 | 5 | 130 | 12 | 0 | 1 | 0.26536 | 188400
3110 | 5 | 130 | 13 | 0 | 1 | 0.26642 | 188400
3111 | 5 | 130 | 14 | 0 | 1 | 0.42387 | 188400
3112 | 5 | 130 | 15 | 0 | 1 | 0.52767 | 188400
3113 | 5 | 130 | 16 | 0 | 0.76691 | 0.66348 | 188400
3114 | 5 | 130 | 17 | 0 | 0.42741 | 0.71605 | 188400
3115 | 5 | 130 | 18 | 0 | 0.12511 | 0.51094 | 188400
3116 | 5 | 130 | 19 | 1 | 0 | 0.39545 | 188200
3117 | 5 | 130 | 20 | 1 | 0 | 0.3051 | 188000
3118 | 5 | 130 | 21 | 0 | 0 | 0.43373 | 188000
3119 | 5 | 130 | 22 | 0 | 0 | 0.5108 | 188000
3120 | 5 | 130 | 23 | 0 | 0 | 0.2833 | 188000
3121 | 5 | 131 | 0 | 0 | 0 | 0.3224 | 188000
3122 | 5 | 131 | 1 | 0 | 0 | 0.29626 | 188000
3123 | 5 | 131 | 2 | 0 | 0 | 0.25012 | 188000
3124 | 5 | 131 | 3 | 0 | 0 | 0.44565 | 188000
3125 | 5 | 131 | 4 | 0 | 0 | 0.33868 | 188000
3126 | 5 | 131 | 5 | 0 | 0 | 0.22102 | 188000
3127 | 5 | 131 | 6 | 0 | 0.12202 | 0.31432 | 188000
3128 | 5 | 131 | 7 | 1 | 0.41685 | 0.45283 | 187800
3129 | 5 | 131 | 8 | 1 | 0.74797 | 0.53967 | 187600
3130 | 5 | 131 | 9 | 0 | 1 | 0.89884 | 187600
3131 | 5 | 131 | 10 | 0 | 1 | 1 | 187600
3132 | 5 | 131 | 11 | 0 | 1 | 0.85981 | 187600
3133 | 5 | 131 | 12 | 0 | 1 | 0.77223 | 187600
3134 | 5 | 131 | 13 | 0 | 1 | 0.69191 | 187600
3135 | 5 | 131 | 14 | 0 | 1 | 0.67404 | 187600
3136 | 5 | 131 | 15 | 0 | 1 | 0.8485 | 187600
3137 | 5 | 131 | 16 | 0 | 0.74797 | 0.80548 | 187600
3138 | 5 | 131 | 17 | 0 | 0.41685 | 0.93811 | 187600
3139 | 5 | 131 | 18 | 0 | 0.12202 | 0.80273 | 187600
3140 | 5 | 131 | 19 | 1 | 0 | 1 | 187400
3141 | 5 | 131 | 20 | 1 | 0 | 0.92748 | 187200
3142 | 5 | 131 | 21 | 0 | 0 | 1 | 187200
3143 | 5 | 131 | 22 | 0 | 0 | 1 | 187200
3144 | 5 | 131 | 23 | 0 | 0 | 1 | 187200
3145 | 5 | 132 | 0 | 0 | 0 | 1 | 187200
3146 | 5 | 132 | 1 | 0 | 0 | 1 | 187200
3147 | 5 | 132 | 2 | 0 | 0 | 1 | 187200
3148 | 5 | 132 | 3 | 0 | 0 | 1 | 187200
3149 | 5 | 132 | 4 | 0 | 0 | 1 | 187200
3150 | 5 | 132 | 5 | 0 | 0 | 1 | 187200
3151 | 5 | 132 | 6 | 0 | 0.11847 | 1 | 187200
3152 | 5 | 132 | 7 | 1 | 0.40472 | 1 | 187000
3153 | 5 | 132 | 8 | 1 | 0.72619 | 0.77785 | 186800
3154 | 5 | 132 | 9 | 0 | 1 | 0.57514 | 186800
3155 | 5 | 132 | 10 | 0 | 1 | 0.56241 | 186800
3156 | 5 | 132 | 11 | 0 | 1 | 0.57386 | 186800
3157 | 5 | 132 | 12 | 0 | 1 | 0.51877 | 186800
3158 | 5 | 132 | 13 | 0 | 1 | 0.52929 | 186800
3159 | 5 | 132 | 14 | 0 | 1 | 0.68226 | 186800
3160 | 5 | 132 | 15 | 0 | 1 | 0.79273 | 186800
3161 | 5 | 132 | 16 | 0 | 0.72619 | 0.54942 | 186800
3162 | 5 | 132 | 17 | 0 | 0.40472 | 0.41442 | 186800
3163 | 5 | 132 | 18 | 0 | 0.11847 | 0.37657 | 186800
3164 | 5 | 132 | 19 | 1 | 0 | 0.31455 | 186600
3165 | 5 | 132 | 20 | 1 | 0 | 0.28304 | 186400
3166 | 5 | 132 | 21 | 0 | 0 | 0.30036 | 186400
3167 | 5 | 132 | 22 | 0 | 0 | 0.46644 | 186400
3168 | 5 | 132 | 23 | 0 | 0 | 0.4345 | 186400
3169 | 5 | 133 | 0 | 0 | 0 | 0.61042 | 186400
3170 | 5 | 133 | 1 | 0 | 0 | 0.54295 | 186400
3171 | 5 | 133 | 2 | 0 | 0 | 0.62469 | 186400
3172 | 5 | 133 | 3 | 0 | 0 | 0.59469 | 186400
3173 | 5 | 133 | 4 | 0 | 0 | 0.50544 | 186400
3174 | 5 | 133 | 5 | 0 | 0 | 0.48515 | 186400
3175 | 5 | 133 | 6 | 0 | 0.12093 | 0.4586 | 186400
3176 | 5 | 133 | 7 | 1 | 0.41313 | 0.74367 | 186200
3177 | 5 | 133 | 8 | 1 | 0.74128 | 0.485 | 186000
3178 | 5 | 133 | 9 | 0 | 1 | 0.54774 | 186000
3179 | 5 | 133 | 10 | 0 | 1 | 0.66623 | 186000
3180 | 5 | 133 | 11 | 0 | 1 | 0.74937 | 186000
3181 | 5 | 133 | 12 | 0 | 1 | 0.99024 | 186000
3182 | 5 | 133 | 13 | 0 | 1 | 0.9032 | 186000
3183 | 5 | 133 | 14 | 0 | 1 | 0.9271 | 186000
3184 | 5 | 133 | 15 | 0 | 1 | 0.77525 | 186000
3185 | 5 | 133 | 16 | 0 | 0.74128 | 0.92285 | 186000
3186 | 5 | 133 | 17 | 0 | 0.41313 | 0.553 | 186000
3187 | 5 | 133 | 18 | 0 | 0.12093 | 0.48516 | 186000
3188 | 5 | 133 | 19 | 1 | 0 | 0.4212 | 185800
3189 | 5 | 133 | 20 | 1 | 0 | 0.31141 | 185600
3190 | 5 | 133 | 21 | 0 | 0 | 0.40953 | 185600
3191 | 5 | 133 | 22 | 0 | 0 | 0.22888 | 185600
3192 | 5 | 133 | 23 | 0 | 0 | 0.37762 | 185600
3193 | 5 | 134 | 0 | 0 | 0 | 0.31009 | 185600
3194 | 5 | 134 | 1 | 0 | 0 | 0.41358 | 185600
3195 | 5 | 134 | 2 | 0 | 0 | 0.47773 | 185600
3196 | 5 | 134 | 3 | 0 | 0 | 0.36755 | 185600
3197 | 5 | 134 | 4 | 0 | 0 | 0.35603 | 185600
3198 | 5 | 134 | 5 | 0 | 0 | 0.43643 | 185600
3199 | 5 | 134 | 6 | 0 | 0.1334 | 0.48954 | 185600
3200 | 5 | 134 | 7 | 1 | 0.45574 | 0.64204 | 185400
3201 | 5 | 134 | 8 | 1 | 0.81773 | 0.68597 | 185200
3202 | 5 | 134 | 9 | 0 | 1 | 0.67323 | 185200
3203 | 5 | 134 | 10 | 0 | 1 | 0.77113 | 185200
3204 | 5 | 134 | 11 | 0 | 1 | 1 | 185200
3205 | 5 | 134 | 12 | 0 | 1 | 1 | 185200
3206 | 5 | 134 | 13 | 0 | 1 | 1 | 185200
3207 | 5 | 134 | 14 | 0 | 1 | 1 | 185200
3208 | 5 | 134 | 15 | 0 | 1 | 1 | 185200
3209 | 5 | 134 | 16 | 0 | 0.81773 | 1 | 185200
3210 | 5 | 134 | 17 | 0 | 0.45574 | 1 | 185200
3211 | 5 | 134 | 18 | 0 | 0.1334 | 1 | 185200
3212 | 5 | 134 | 19 | 1 | 0 | 1 | 185000
3213 | 5 | 134 | 20 | 1 | 0 | 1 | 184800
3214 | 5 | 134 | 21 | 0 | 0 | 1 | 184800
3215 | 5 | 134 | 22 | 0 | 0 | 1 | 184800
3216 | 5 | 134 | 23 | 0 | 0 | 1 | 184800
3217 | 5 | 135 | 0 | 0 | 0 | 0.82611 | 184800
3218 | 5 | 135 | 1 | 0 | 0 | 0.46734 | 184800
3219 | 5 | 135 | 2 | 0 | 0 | 0.48324 | 184800
3220 | 5 | 135 | 3 | 0 | 0 | 0.49881 | 184800
3221 | 5 | 135 | 4 | 0 | 0 | 0.75331 | 184800
3222 | 5 | 135 | 5 | 0 | 0 | 0.4462 | 184800
3223 | 5 | 135 | 6 | 0 | 0.093522 | 0.55035 | 184800
3224 | 5 | 135 | 7 | 1 | 0.3195 | 0.41445 | 184600
3225 | 5 | 135 | 8 | 1 | 0.57328 | 0.35662 | 184400
3226 | 5 | 135 | 9 | 0 | 0.81349 | 0.48164 | 184400
3227 | 5 | 135 | 10 | 0 | 1 | 0.61702 | 184400
3228 | 5 | 135 | 11 | 0 | 1 | 0.34904 | 184400
3229 | 5 | 135 | 12 | 0 | 1 | 0.29802 | 184400
3230 | 5 | 135 | 13 | 0 | 1 | 0.30977 | 184400
3231 | 5 | 135 | 14 | 0 | 1 | 0.28027 | 184400
3232 | 5 | 135 | 15 | 0 | 0.81349 | 0.31419 | 184400
3233 | 5 | 135 | 16 | 0 | 0.57328 | 0.36659 | 184400
3234 | 5 | 135 | 17 | 0 | 0.3195 | 0.33398 | 184400
3235 | 5 | 135 | 18 | 0 | 0.093522 | 0.39251 | 184400
3236 | 5 | 135 | 19 | 1 | 0 | 0.23808 | 184200
3237 | 5 | 135 | 20 | 1 | 0 | 0.22549 | 184000
3238 | 5 | 135 | 21 | 0 | 0 | 0.25186 | 184000
3239 | 5 | 135 | 22 | 0 | 0 | 0.22337 | 184000
3240 | 5 | 135 | 23 | 0 | 0 | 0.2176 | 184000
3241 | 5 | 136 | 0 | 0 | 0 | 0.21425 | 184000
3242 | 5 | 136 | 1 | 0 | 0 | 0.17849 | 184000
3243 | 5 | 136 | 2 | 0 | 0 | 0.16303 | 184000
3244 | 5 | 136 | 3 | 0 | 0 | 0.17604 | 184000
3245 | 5 | 136 | 4 | 0 | 0 | 0.22371 | 184000
3246 | 5 | 136 | 5 | 0 | 0 | 0.25361 | 184000
3247 | 5 | 136 | 6 | 0 | 0.12647 | 0.27436 | 184000
3248 | 5 | 136 | 7 | 1 | 0.43205 | 0.22987 | 183800
3249 | 5 | 136 | 8 | 1 | 0.77523 | 0.21858 | 183600
3250 | 5 | 136 | 9 | 0 | 1 | 0.25564 | 183600
3251 | 5 | 136 | 10 | 0 | 1 | 0.35917 | 183600
3252 | 5 | 136 | 11 | 0 | 1 | 0.45095 | 183600
3253 | 5 | 136 | 12 | 0 | 1 | 0.34124 | 183600
3254 | 5 | 136 | 13 | 0 | 1 | 0.32664 | 183600
3255 | 5 | 136 | 14 | 0 | 1 | 0.50155 | 183600
3256 | 5 | 136 | 15 | 0 | 1 | 0.45783 | 183600
3257 | 5 | 136 | 16 | 0 | 0.77523 | 0.50894 | 183600
3258 | 5 | 136 | 17 | 0 | 0.43205 | 0.46911 | 183600
3259 | 5 | 136 | 18 | 0 | 0.12647 | 0.63888 | 183600
3260 | 5 | 136 | 19 | 1 | 0 | 0.70988 | 183400
3261 | 5 | 136 | 20 | 1 | 0 | 0.65687 | 183200
3262 | 5 | 136 | 21 | 0 | 0 | 0.6044 | 183200
3263 | 5 | 136 | 22 | 0 | 0 | 0.44086 | 183200
3264 | 5 | 136 | 23 | 0 | 0 | 0.53451 | 183200
3265 | 5 | 137 | 0 | 0 | 0 | 0.5065 | 183200
3266 | 5 | 137 | 1 | 0 | 0 | 0.70663 | 183200
3267 | 5 | 137 | 2 | 0 | 0 | 0.5828 | 183200
3268 | 5 | 137 | 3 | 0 | 0 | 0.61578 | 183200
3269 | 5 | 137 | 4 | 0 | 0 | 0.71464 | 183200
3270 | 5 | 137 | 5 | 0 | 0 | 0.53648 | 183200
3271 | 5 | 137 | 6 | 0 | 0.12354 | 0.45485 | 183200
3272 | 5 | 137 | 7 | 1 | 0.42206 | 0.78336 | 183000
3273 | 5 | 137 | 8 | 1 | 0.7573 | 0.88617 | 182800
3274 | 5 | 137 | 9 | 0 | 1 | 1 | 182800
3275 | 5 | 137 | 10 | 0 | 1 | 1 | 182800
3276 | 5 | 137 | 11 | 0 | 1 | 0.85469 | 182800
3277 | 5 | 137 | 12 | 0 | 1 | 0.92166 | 182800
3278 | 5 | 137 | 13 | 0 | 1 | 0.94622 | 182800
3279 | 5 | 137 | 14 | 0 | 1 | 0.74422 | 182800
3280 | 5 | 137 | 15 | 0 | 1 | 0.40324 | 182800
3281 | 5 | 137 | 16 | 0 | 0.7573 | 0.33806 | 182800
3282 | 5 | 137 | 17 | 0 | 0.42206 | 0.49495 | 182800
3283 | 5 | 137 | 18 | 0 | 0.12354 | 0.29166 | 182800
3284 | 5 | 137 | 19 | 1 | 0 | 0.33539 | 182600
3285 | 5 | 137 | 20 | 1 | 0 | 0.38506 | 182400
3286 | 5 | 137 | 21 | 0 | 0 | 0.42311 | 182400
3287 | 5 | 137 | 22 | 0 | 0 | 0.36671 | 182400
3288 | 5 | 137 | 23 | 0 | 0 | 0.28852 | 182400
3289 | 5 | 138 | 0 | 0 | 0 | 0.29798 | 182400
3290 | 5 | 138 | 1 | 0 | 0 | 0.29874 | 182400
3291 | 5 | 138 | 2 | 0 | 0 | 0.22069 | 182400
3292 | 5 | 138 | 3 | 0 | 0 | 0.25295 | 182400
3293 | 5 | 138 | 4 | 0 | 0 | 0.37859 | 182400
3294 | 5 | 138 | 5 | 0 | 0 | 0.43769 | 182400
3295 | 5 | 138 | 6 | 0 | 0.10977 | 0.60573 | 182400
3296 | 5 | 138 | 7 | 1 | 0.37499 | 0.78848 | 182200
3297 | 5 | 138 | 8 | 1 | 0.67285 | 0.92102 | 182000
3298 | 5 | 138 | 9 | 0 | 0.95478 | 0.95748 | 182000
3299 | 5 | 138 | 10 | 0 | 1 | 1 | 182000
3300 | 5 | 138 | 11 | 0 | 1 | 1 | 182000
3301 | 5 | 138 | 12 | 0 | 1 | 0.91227 | 182000
3302 | 5 | 138 | 13 | 0 | 1 | 0.91345 | 182000
3303 | 5 | 138 | 14 | 0 | 1 | 1 | 182000
3304 | 5 | 138 | 15 | 0 | 0.95478 | 1 | 182000
3305 | 5 | 138 | 16 | 0 | 0.67285 | 1 | 182000
3306 | 5 | 138 | 17 | 0 | 0.37499 | 1 | 182000
3307 | 5 | 138 | 18 | 0 | 0.10977 | 1 | 182000
3308 | 5 | 138 | 19 | 1 | 0 | 1 | 181800
3309 | 5 | 138 | 20 | 1 | 0 | 0.94189 | 181600
3310 | 5 | 138 | 21 | 0 | 0 | 0.79198 | 181600
3311 | 5 | 138 | 22 | 0 | 0 | 0.73272 | 181600
3312 | 5 | 138 | 23 | 0 | 0 | 0.56948 | 181600
3313 | 5 | 139 | 0 | 0 | 0 | 0.79338 | 181600
3314 | 5 | 139 | 1 | 0 | 0 | 0.75328 | 181600
3315 | 5 | 139 | 2 | 0 | 0 | 0.69305 | 181600
3316 | 5 | 139 | 3 | 0 | 0 | 0.61248 | 181600
3317 | 5 | 139 | 4 | 0 | 0 | 0.52979 | 181600
3318 | 5 | 139 | 5 | 0 | 0 | 0.5927 | 181600
3319 | 5 | 139 | 6 | 0 | 0.11506 | 0.7646 | 181600
3320 | 5 | 139 | 7 | 1 | 0.39309 | 0.75871 | 181400
3321 | 5 | 139 | 8 | 1 | 0.70532 | 0.62596 | 181200
3322 | 5 | 139 | 9 | 0 | 1 | 0.95031 | 181200
3323 | 5 | 139 | 10 | 0 | 1 | 0.78375 | 181200
3324 | 5 | 139 | 11 | 0 | 1 | 0.96492 | 181200
3325 | 5 | 139 | 12 | 0 | 1 | 0.90009 | 181200
3326 | 5 | 139 | 13 | 0 | 1 | 0.79514 | 181200
3327 | 5 | 139 | 14 | 0 | 1 | 0.64308 | 181200
3328 | 5 | 139 | 15 | 0 | 1 | 0.67714 | 181200
3329 | 5 | 139 | 16 | 0 | 0.70532 | 0.57118 | 181200
3330 | 5 | 139 | 17 | 0 | 0.39309 | 0.31604 | 181200
3331 | 5 | 139 | 18 | 0 | 0.11506 | 0.24434 | 181200
3332 | 5 | 139 | 19 | 1 | 0 | 0.30928 | 181000
3333 | 5 | 139 | 20 | 1 | 0 | 0.24265 | 180800
3334 | 5 | 139 | 21 | 0 | 0 | 0.20796 | 180800
3335 | 5 | 139 | 22 | 0 | 0 | 0.15987 | 180800
3336 | 5 | 139 | 23 | 0 | 0 | 0.15508 | 180800
3337 | 5 | 140 | 0 | 0 | 0 | 0.22409 | 180800
3338 | 5 | 140 | 1 | 0 | 0 | 0.19633 | 180800
3339 | 5 | 140 | 2 | 0 | 0 | 0.25534 | 180800
3340 | 5 | 140 | 3 | 0 | 0 | 0.32331 | 180800
3341 | 5 | 140 | 4 | 0 | 0 | 0.28178 | 180800
3342 | 5 | 140 | 5 | 0 | 0 | 0.36156 | 180800
3343 | 5 | 140 | 6 | 0 | 0.11049 | 0.55505 | 180800
3344 | 5 | 140 | 7 | 1 | 0.37747 | 0.39851 | 180600
3345 | 5 | 140 | 8 | 1 | 0.67729 | 0.4488 | 180400
3346 | 5 | 140 | 9 | 0 | 0.9611 | 0.64625 | 180400
3347 | 5 | 140 | 10 | 0 | 1 | 0.71874 | 180400
3348 | 5 | 140 | 11 | 0 | 1 | 0.73482 | 180400
3349 | 5 | 140 | 12 | 0 | 1 | 0.75255 | 180400
3350 | 5 | 140 | 13 | 0 | 1 | 0.82456 | 180400
3351 | 5 | 140 | 14 | 0 | 1 | 0.65193 | 180400
3352 | 5 | 140 | 15 | 0 | 0.9611 | 0.62181 | 180400
3353 | 5 | 140 | 16 | 0 | 0.67729 | 0.4042 | 180400
3354 | 5 | 140 | 17 | 0 | 0.37747 | 0.25376 | 180400
3355 | 5 | 140 | 18 | 0 | 0.11049 | 0.25011 | 180400
3356 | 5 | 140 | 19 | 1 | 0 | 0.14254 | 180200
3357 | 5 | 140 | 20 | 1 | 0 | 0.17484 | 180000
3358 | 5 | 140 | 21 | 0 | 0 | 0.10045 | 180000
3359 | 5 | 140 | 22 | 0 | 0 | 0.099705 | 180000
3360 | 5 | 140 | 23 | 0 | 0 | 0.079745 | 180000
3361 | 5 | 141 | 0 | 0 | 0 | 0.10043 | 180000
3362 | 5 | 141 | 1 | 0 | 0 | 0.12575 | 180000
3363 | 5 | 141 | 2 | 0 | 0 | 0.11828 | 180000
3364 | 5 | 141 | 3 | 0 | 0 | 0.10692 | 180000
3365 | 5 | 141 | 4 | 0 | 0 | 0.12817 | 180000
3366 | 5 | 141 | 5 | 0 | 0 | 0.12093 | 180000
3367 | 5 | 141 | 6 | 0 | 0.13224 | 0.12157 | 180000
3368 | 5 | 141 | 7 | 1 | 0.45177 | 0.19696 | 179800
3369 | 5 | 141 | 8 | 1 | 0.81062 | 0.30776 | 179600
3370 | 5 | 141 | 9 | 0 | 1 | 0.40222 | 179600
3371 | 5 | 141 | 10 | 0 | 1 | 0.3632 | 179600
3372 | 5 | 141 | 11 | 0 | 1 | 0.34329 | 179600
3373 | 5 | 141 | 12 | 0 | 1 | 0.41995 | 179600
3374 | 5 | 141 | 13 | 0 | 1 | 0.51431 | 179600
3375 | 5 | 141 | 14 | 0 | 1 | 0.39505 | 179600
3376 | 5 | 141 | 15 | 0 | 1 | 0.34525 | 179600
3377 | 5 | 141 | 16 | 0 | 0.81062 | 0.44685 | 179600
3378 | 5 | 141 | 17 | 0 | 0.45177 | 0.76189 | 179600
3379 | 5 | 141 | 18 | 0 | 0.13224 | 0.51668 | 179600
3380 | 5 | 141 | 19 | 1 | 0 | 0.67073 | 179400
3381 | 5 | 141 | 20 | 1 | 0 | 0.88714 | 179200
3382 | 5 | 141 | 21 | 0 | 0 | 0.81251 | 179200
3383 | 5 | 141 | 22 | 0 | 0 | 0.65216 | 179200
3384 | 5 | 141 | 23 | 0 | 0 | 0.51709 | 179200
3385 | 5 | 142 | 0 | 0 | 0 | 0.38027 | 179200
3386 | 5 | 142 | 1 | 0 | 0 | 0.40331 | 179200
3387 | 5 | 142 | 2 | 0 | 0 | 0.33689 | 179200
3388 | 5 | 142 | 3 | 0 | 0 | 0.33473 | 179200
3389 | 5 | 142 | 4 | 0 | 0 | 0.28752 | 179200
3390 | 5 | 142 | 5 | 0 | 0 | 0.29902 | 179200
3391 | 5 | 142 | 6 | 0 | 0.097312 | 0.25065 | 179200
3392 | 5 | 142 | 7 | 1 | 0.33245 | 0.21748 | 179000
3393 | 5 | 142 | 8 | 1 | 0.59651 | 0.32958 | 178800
3394 | 5 | 142 | 9 | 0 | 0.84646 | 0.44364 | 178800
3395 | 5 | 142 | 10 | 0 | 1 | 0.34079 | 178800
3396 | 5 | 142 | 11 | 0 | 1 | 0.41006 | 178800
3397 | 5 | 142 | 12 | 0 | 1 | 0.33231 | 178800
3398 | 5 | 142 | 13 | 0 | 1 | 0.45685 | 178800
3399 | 5 | 142 | 14 | 0 | 1 | 0.47656 | 178800
3400 | 5 | 142 | 15 | 0 | 0.84646 | 0.57515 | 178800
3401 | 5 | 142 | 16 | 0 | 0.59651 | 0.44371 | 178800
3402 | 5 | 142 | 17 | 0 | 0.33245 | 0.43354 | 178800
3403 | 5 | 142 | 18 | 0 | 0.097312 | 0.36012 | 178800
3404 | 5 | 142 | 19 | 1 | 0 | 0.40162 | 178600
3405 | 5 | 142 | 20 | 1 | 0 | 0.38067 | 178400
3406 | 5 | 142 | 21 | 0 | 0 | 0.25677 | 178400
3407 | 5 | 142 | 22 | 0 | 0 | 0.20405 | 178400
3408 | 5 | 142 | 23 | 0 | 0 | 0.19239 | 178400
3409 | 5 | 143 | 0 | 0 | 0 | 0.21062 | 178400
3410 | 5 | 143 | 1 | 0 | 0 | 0.23425 | 178400
3411 | 5 | 143 | 2 | 0 | 0 | 0.27159 | 178400
3412 | 5 | 143 | 3 | 0 | 0 | 0.21634 | 178400
3413 | 5 | 143 | 4 | 0 | 0 | 0.19561 | 178400
3414 | 5 | 143 | 5 | 0 | 0 | 0.19547 | 178400
3415 | 5 | 143 | 6 | 0 | 0.11135 | 0.25089 | 178400
3416 | 5 | 143 | 7 | 1 | 0.38041 | 0.29721 | 178200
3417 | 5 | 143 | 8 | 1 | 0.68257 | 0.17887 | 178000
3418 | 5 | 143 | 9 | 0 | 0.96858 | 0.1666 | 178000
3419 | 5 | 143 | 10 | 0 | 1 | 0.25877 | 178000
3420 | 5 | 143 | 11 | 0 | 1 | 0.45163 | 178000
3421 | 5 | 143 | 12 | 0 | 1 | 0.51501 | 178000
3422 | 5 | 143 | 13 | 0 | 1 | 0.46611 | 178000
3423 | 5 | 143 | 14 | 0 | 1 | 0.48183 | 178000
3424 | 5 | 143 | 15 | 0 | 0.96858 | 0.73747 | 178000
3425 | 5 | 143 | 16 | 0 | 0.68257 | 0.96632 | 178000
3426 | 5 | 143 | 17 | 0 | 0.38041 | 0.87355 | 178000
3427 | 5 | 143 | 18 | 0 | 0.11135 | 0.52745 | 178000
3428 | 5 | 143 | 19 | 1 | 0 | 0.62334 | 177800
3429 | 5 | 143 | 20 | 1 | 0 | 0.54075 | 177600
3430 | 5 | 143 | 21 | 0 | 0 | 0.49508 | 177600
3431 | 5 | 143 | 22 | 0 | 0 | 0.47835 | 177600
3432 | 5 | 143 | 23 | 0 | 0 | 0.41141 | 177600
3433 | 5 | 144 | 0 | 0 | 0 | 0.46089 | 177600
3434 | 5 | 144 | 1 | 0 | 0 | 0.27417 | 177600
3435 | 5 | 144 | 2 | 0 | 0 | 0.27119 | 177600
3436 | 5 | 144 | 3 | 0 | 0 | 0.34874 | 177600
3437 | 5 | 144 | 4 | 0 | 0 | 0.53561 | 177600
3438 | 5 | 144 | 5 | 0 | 0 | 0.41532 | 177600
3439 | 5 | 144 | 6 | 0 | 0.11994 | 0.62582 | 177600
3440 | 5 | 144 | 7 | 1 | 0.40975 | 0.69064 | 177400
3441 | 5 | 144 | 8 | 1 | 0.73522 | 0.61844 | 177200
3442 | 5 | 144 | 9 | 0 | 1 | 0.63406 | 177200
3443 | 5 | 144 | 10 | 0 | 1 | 0.60484 | 177200
3444 | 5 | 144 | 11 | 0 | 1 | 0.78025 | 177200
3445 | 5 | 144 | 12 | 0 | 1 | 0.90162 | 177200
3446 | 5 | 144 | 13 | 0 | 1 | 1 | 177200
3447 | 5 | 144 | 14 | 0 | 1 | 1 | 177200
3448 | 5 | 144 | 15 | 0 | 1 | 1 | 177200
3449 | 5 | 144 | 16 | 0 | 0.73522 | 0.77609 | 177200
3450 | 5 | 144 | 17 | 0 | 0.40975 | 0.67844 | 177200
3451 | 5 | 144 | 18 | 0 | 0.11994 | 0.5157 | 177200
3452 | 5 | 144 | 19 | 1 | 0 | 0.58063 | 177000
3453 | 5 | 144 | 20 | 1 | 0 | 0.55437 | 176800
3454 | 5 | 144 | 21 | 0 | 0 | 0.71125 | 176800
3455 | 5 | 144 | 22 | 0 | 0 | 1 | 176800
3456 | 5 | 144 | 23 | 0 | 0 | 0.89705 | 176800
3457 | 5 | 145 | 0 | 0 | 0 | 0.78898 | 176800
3458 | 5 | 145 | 1 | 0 | 0 | 0.92783 | 176800
3459 | 5 | 145 | 2 | 0 | 0 | 0.83756 | 176800
3460 | 5 | 145 | 3 | 0 | 0 | 0.55968 | 176800
3461 | 5 | 145 | 4 | 0 | 0 | 0.61456 | 176800
3462 | 5 | 145 | 5 | 0 | 0 | 0.61846 | 176800
3463 | 5 | 145 | 6 | 0 | 0.12224 | 0.66507 | 176800
3464 | 5 | 145 | 7 | 1 | 0.4176 | 0.56714 | 176600
3465 | 5 | 145 | 8 | 1 | 0.7493 | 0.70151 | 176400
3466 | 5 | 145 | 9 | 0 | 1 | 0.61354 | 176400
3467 | 5 | 145 | 10 | 0 | 1 | 0.55493 | 176400
3468 | 5 | 145 | 11 | 0 | 1 | 0.4286 | 176400
3469 | 5 | 145 | 12 | 0 | 1 | 0.45855 | 176400
3470 | 5 | 145 | 13 | 0 | 1 | 0.63522 | 176400
3471 | 5 | 145 | 14 | 0 | 1 | 0.60062 | 176400
3472 | 5 | 145 | 15 | 0 | 1 | 0.61605 | 176400
3473 | 5 | 145 | 16 | 0 | 0.7493 | 1 | 176400
3474 | 5 | 145 | 17 | 0 | 0.4176 | 0.79243 | 176400
3475 | 5 | 145 | 18 | 0 | 0.12224 | 0.66762 | 176400
3476 | 5 | 145 | 19 | 1 | 0 | 0.66083 | 176200
3477 | 5 | 145 | 20 | 1 | 0 | 0.62447 | 176000
3478 | 5 | 145 | 21 | 0 | 0 | 0.83921 | 176000
3479 | 5 | 145 | 22 | 0 | 0 | 0.75048 | 176000
3480 | 5 | 145 | 23 | 0 | 0 | 0.65933 | 176000
3481 | 5 | 146 | 0 | 0 | 0 | 0.56107 | 176000
3482 | 5 | 146 | 1 | 0 | 0 | 0.37611 | 176000
3483 | 5 | 146 | 2 | 0 | 0 | 0.3307 | 176000
3484 | 5 | 146 | 3 | 0 | 0 | 0.35433 | 176000
3485 | 5 | 146 | 4 | 0 | 0 | 0.34427 | 176000
3486 | 5 | 146 | 5 | 0 | 0 | 0.32954 | 176000
3487 | 5 | 146 | 6 | 0 | 0.10104 | 0.36754 | 176000
3488 | 5 | 146 | 7 | 1 | 0.34519 | 0.33811 | 175800
3489 | 5 | 146 | 8 | 1 | 0.61939 | 0.27869 | 175600
3490 | 5 | 146 | 9 | 0 | 0.87892 | 0.23433 | 175600
3491 | 5 | 146 | 10 | 0 | 1 | 0.19726 | 175600
3492 | 5 | 146 | 11 | 0 | 1 | 0.26188 | 175600
3493 | 5 | 146 | 12 | 0 | 1 | 0.17484 | 175600
3494 | 5 | 146 | 13 | 0 | 1 | 0.18218 | 175600
3495 | 5 | 146 | 14 | 0 | 1 | 0.22205 | 175600
3496 | 5 | 146 | 15 | 0 | 0.87892 | 0.27454 | 175600
3497 | 5 | 146 | 16 | 0 | 0.61939 | 0.22057 | 175600
3498 | 5 | 146 | 17 | 0 | 0.34519 | 0.33438 | 175600
3499 | 5 | 146 | 18 | 0 | 0.10104 | 0.29927 | 175600
3500 | 5 | 146 | 19 | 1 | 0 | 0.27677 | 175400
3501 | 5 | 146 | 20 | 1 | 0 | 0.32175 | 175200
3502 | 5 | 146 | 21 | 0 | 0 | 0.23023 | 175200
3503 | 5 | 146 | 22 | 0 | 0 | 0.29346 | 175200
3504 | 5 | 146 | 23 | 0 | 0 | 0.2345 | 175200
3505 | 5 | 147 | 0 | 0 | 0 | 0.21043 | 175200
3506 | 5 | 147 | 1 | 0 | 0 | 0.14466 | 175200
3507 | 5 | 147 | 2 | 0 | 0 | 0.088527 | 175200
3508 | 5 | 147 | 3 | 0 | 0 | 0.13267 | 175200
3509 | 5 | 147 | 4 | 0 | 0 | 0.1227 | 175200
3510 | 5 | 147 | 5 | 0 | 0 | 0.10168 | 175200
3511 | 5 | 147 | 6 | 0 | 0.10472 | 0.11408 | 175200
3512 | 5 | 147 | 7 | 1 | 0.35775 | 0.14378 | 175000
3513 | 5 | 147 | 8 | 1 | 0.64191 | 0.22223 | 174800
3514 | 5 | 147 | 9 | 0 | 0.91088 | 0.20925 | 174800
3515 | 5 | 147 | 10 | 0 | 1 | 0.3189 | 174800
3516 | 5 | 147 | 11 | 0 | 1 | 0.3674 | 174800
3517 | 5 | 147 | 12 | 0 | 1 | 0.36705 | 174800
3518 | 5 | 147 | 13 | 0 | 1 | 0.32355 | 174800
3519 | 5 | 147 | 14 | 0 | 1 | 0.22398 | 174800
3520 | 5 | 147 | 15 | 0 | 0.91088 | 0.32601 | 174800
3521 | 5 | 147 | 16 | 0 | 0.64191 | 0.431 | 174800
3522 | 5 | 147 | 17 | 0 | 0.35775 | 0.58509 | 174800
3523 | 5 | 147 | 18 | 0 | 0.10472 | 0.65893 | 174800
3524 | 5 | 147 | 19 | 1 | 0 | 0.64363 | 174600
3525 | 5 | 147 | 20 | 1 | 0 | 0.69846 | 174400
3526 | 5 | 147 | 21 | 0 | 0 | 1 | 174400
3527 | 5 | 147 | 22 | 0 | 0 | 0.86043 | 174400
3528 | 5 | 147 | 23 | 0 | 0 | 0.604 | 174400
3529 | 5 | 148 | 0 | 0 | 0 | 0.52426 | 174400
3530 | 5 | 148 | 1 | 0 | 0 | 0.59678 | 174400
3531 | 5 | 148 | 2 | 0 | 0 | 0.65246 | 174400
3532 | 5 | 148 | 3 | 0 | 0 | 0.53542 | 174400
3533 | 5 | 148 | 4 | 0 | 0 | 0.47734 | 174400
3534 | 5 | 148 | 5 | 0 | 0 | 0.51745 | 174400
3535 | 5 | 148 | 6 | 0 | 0.10377 | 0.49167 | 174400
3536 | 5 | 148 | 7 | 1 | 0.35452 | 0.60439 | 174200
3537 | 5 | 148 | 8 | 1 | 0.63613 | 0.53282 | 174000
3538 | 5 | 148 | 9 | 0 | 0.90268 | 0.65507 | 174000
3539 | 5 | 148 | 10 | 0 | 1 | 0.56135 | 174000
3540 | 5 | 148 | 11 | 0 | 1 | 0.65256 | 174000
3541 | 5 | 148 | 12 | 0 | 1 | 0.51658 | 174000
3542 | 5 | 148 | 13 | 0 | 1 | 0.58257 | 174000
3543 | 5 | 148 | 14 | 0 | 1 | 0.51576 | 174000
3544 | 5 | 148 | 15 | 0 | 0.90268 | 0.56458 | 174000
3545 | 5 | 148 | 16 | 0 | 0.63613 | 0.53813 | 174000
3546 | 5 | 148 | 17 | 0 | 0.35452 | 0.62194 | 174000
3547 | 5 | 148 | 18 | 0 | 0.10377 | 0.59528 | 174000
3548 | 5 | 148 | 19 | 1 | 0 | 0.71663 | 173800
3549 | 5 | 148 | 20 | 1 | 0 | 0.69546 | 173600
3550 | 5 | 148 | 21 | 0 | 0 | 0.95489 | 173600
3551 | 5 | 148 | 22 | 0 | 0 | 0.91814 | 173600
3552 | 5 | 148 | 23 | 0 | 0 | 0.70687 | 173600
3553 | 5 | 149 | 0 | 0 | 0 | 0.55618 | 173600
3554 | 5 | 149 | 1 | 0 | 0 | 0.49858 | 173600
3555 | 5 | 149 | 2 | 0 | 0 | 0.39842 | 173600
3556 | 5 | 149 | 3 | 0 | 0 | 0.34596 | 173600
3557 | 5 | 149 | 4 | 0 | 0 | 0.34003 | 173600
3558 | 5 | 149 | 5 | 0 | 0 | 0.41416 | 173600
3559 | 5 | 149 | 6 | 0 | 0.13381 | 0.33904 | 173600
3560 | 5 | 149 | 7 | 1 | 0.45714 | 0.30957 | 173400
3561 | 5 | 149 | 8 | 1 | 0.82026 | 0.38319 | 173200
3562 | 5 | 149 | 9 | 0 | 1 | 0.44126 | 173200
3563 | 5 | 149 | 10 | 0 | 1 | 0.36946 | 173200
3564 | 5 | 149 | 11 | 0 | 1 | 0.46077 | 173200
3565 | 5 | 149 | 12 | 0 | 1 | 0.35978 | 173200
3566 | 5 | 149 | 13 | 0 | 1 | 0.32655 | 173200
3567 | 5 | 149 | 14 | 0 | 1 | 0.35072 | 173200
3568 | 5 | 149 | 15 | 0 | 1 | 0.39652 | 173200
3569 | 5 | 149 | 16 | 0 | 0.82026 | 0.51031 | 173200
3570 | 5 | 149 | 17 | 0 | 0.45714 | 0.48816 | 173200
3571 | 5 | 149 | 18 | 0 | 0.13381 | 0.52257 | 173200
3572 | 5 | 149 | 19 | 1 | 0 | 0.47299 | 173000
3573 | 5 | 149 | 20 | 1 | 0 | 0.33976 | 172800
3574 | 5 | 149 | 21 | 0 | 0 | 0.40156 | 172800
3575 | 5 | 149 | 22 | 0 | 0 | 0.34802 | 172800
3576 | 5 | 149 | 23 | 0 | 0 | 0.33792 | 172800
3577 | 5 | 150 | 0 | 0 | 0 | 0.31953 | 172800
3578 | 5 | 150 | 1 | 0 | 0 | 0.28259 | 172800
3579 | 5 | 150 | 2 | 0 | 0 | 0.30563 | 172800
3580 | 5 | 150 | 3 | 0 | 0 | 0.39851 | 172800
3581 | 5 | 150 | 4 | 0 | 0 | 0.46753 | 172800
3582 | 5 | 150 | 5 | 0 | 0 | 0.50521 | 172800
3583 | 5 | 150 | 6 | 0 | 0.10608 | 0.60064 | 172800
3584 | 5 | 150 | 7 | 1 | 0.36241 | 0.51272 | 172600
3585 | 5 | 150 | 8 | 1 | 0.65028 | 0.40577 | 172400
3586 | 5 | 150 | 9 | 0 | 0.92276 | 0.33099 | 172400
3587 | 5 | 150 | 10 | 0 | 1 | 0.35082 | 172400
3588 | 5 | 150 | 11 | 0 | 1 | 0.23891 | 172400
3589 | 5 | 150 | 12 | 0 | 1 | 0.14461 | 172400
3590 | 5 | 150 | 13 | 0 | 1 | 0.10451 | 172400
3591 | 5 | 150 | 14 | 0 | 1 | 0.1243 | 172400
3592 | 5 | 150 | 15 | 0 | 0.92276 | 0.14149 | 172400
3593 | 5 | 150 | 16 | 0 | 0.65028 | 0.13483 | 172400
3594 | 5 | 150 | 17 | 0 | 0.36241 | 0.14058 | 172400
3595 | 5 | 150 | 18 | 0 | 0.10608 | 0.13748 | 172400
3596 | 5 | 150 | 19 | 1 | 0 | 0.16284 | 172200
3597 | 5 | 150 | 20 | 1 | 0 | 0.19599 | 172000
3598 | 5 | 150 | 21 | 0 | 0 | 0.24229 | 172000
3599 | 5 | 150 | 22 | 0 | 0 | 0.29389 | 172000
3600 | 5 | 150 | 23 | 0 | 0 | 0.1811 | 172000
3601 | 5 | 151 | 0 | 0 | 0 | 0.1769 | 172000
3602 | 5 | 151 | 1 | 0 | 0 | 0.1082 | 172000
3603 | 5 | 151 | 2 | 0 | 0 | 0.071817 | 172000
3604 | 5 | 151 | 3 | 0 | 0 | 0.11004 | 172000
3605 | 5 | 151 | 4 | 0 | 0 | 0.20808 | 172000
3606 | 5 | 151 | 5 | 0 | 0 | 0.20384 | 172000
3607 | 5 | 151 | 6 | 0 | 0.12057 | 0.24365 | 172000
3608 | 5 | 151 | 7 | 1 | 0.41189 | 0.25038 | 171800
3609 | 5 | 151 | 8 | 1 | 0.73906 | 0.33971 | 171600
3610 | 5 | 151 | 9 | 0 | 1 | 0.41242 | 171600
3611 | 5 | 151 | 10 | 0 | 1 | 0.4376 | 171600
3612 | 5 | 151 | 11 | 0 | 1 | 0.62072 | 171600
3613 | 5 | 151 | 12 | 0 | 1 | 0.68577 | 171600
3614 | 5 | 151 | 13 | 0 | 1 | 0.78254 | 171600
3615 | 5 | 151 | 14 | 0 | 1 | 0.85694 | 171600
3616 | 5 | 151 | 15 | 0 | 1 | 0.95239 | 171600
3617 | 5 | 151 | 16 | 0 | 0.73906 | 1 | 171600
3618 | 5 | 151 | 17 | 0 | 0.41189 | 1 | 171600
3619 | 5 | 151 | 18 | 0 | 0.12057 | 0.7032 | 171600
3620 | 5 | 151 | 19 | 1 | 0 | 0.56519 | 171400
3621 | 5 | 151 | 20 | 1 | 0 | 0.59471 | 171200
3622 | 5 | 151 | 21 | 0 | 0 | 0.32948 | 171200
3623 | 5 | 151 | 22 | 0 | 0 | 0.37748 | 171200
3624 | 5 | 151 | 23 | 0 | 0 | 0.33267 | 171200
3625 | 6 | 152 | 0 | 0 | 0 | 0.38342 | 171200
3626 | 6 | 152 | 1 | 0 | 0 | 0.41487 | 171200
3627 | 6 | 152 | 2 | 0 | 0 | 0.32257 | 171200
3628 | 6 | 152 | 3 | 0 | 0 | 0.21475 | 171200
3629 | 6 | 152 | 4 | 0 | 0 | 0.29741 | 171200
3630 | 6 | 152 | 5 | 0 | 0 | 0.35654 | 171200
3631 | 6 | 152 | 6 | 0 | 0.10467 | 0.24042 | 171200
3632 | 6 | 152 | 7 | 1 | 0.30312 | 0.29641 | 171000
3633 | 6 | 152 | 8 | 1 | 0.52021 | 0.27585 | 170800
3634 | 6 | 152 | 9 | 0 | 0.72338 | 0.37179 | 170800
3635 | 6 | 152 | 10 | 0 | 0.88752 | 0.41973 | 170800
3636 | 6 | 152 | 11 | 0 | 0.99386 | 0.43933 | 170800
3637 | 6 | 152 | 12 | 0 | 1 | 0.40179 | 170800
3638 | 6 | 152 | 13 | 0 | 0.99386 | 0.32169 | 170800
3639 | 6 | 152 | 14 | 0 | 0.88752 | 0.49687 | 170800
3640 | 6 | 152 | 15 | 0 | 0.72338 | 0.90097 | 170800
3641 | 6 | 152 | 16 | 0 | 0.52021 | 0.74119 | 170800
3642 | 6 | 152 | 17 | 0 | 0.30312 | 0.90897 | 170800
3643 | 6 | 152 | 18 | 0 | 0.10467 | 0.54222 | 170800
3644 | 6 | 152 | 19 | 1 | 0 | 0.91323 | 170600
3645 | 6 | 152 | 20 | 1 | 0 | 0.84203 | 170400
3646 | 6 | 152 | 21 | 0 | 0 | 1 | 170400
3647 | 6 | 152 | 22 | 0 | 0 | 1 | 170400
3648 | 6 | 152 | 23 | 0 | 0 | 1 | 170400
3649 | 6 | 153 | 0 | 0 | 0 | 1 | 170400
3650 | 6 | 153 | 1 | 0 | 0 | 1 | 170400
3651 | 6 | 153 | 2 | 0 | 0 | 1 | 170400
3652 | 6 | 153 | 3 | 0 | 0 | 1 | 170400
3653 | 6 | 153 | 4 | 0 | 0 | 1 | 170400
3654 | 6 | 153 | 5 | 0 | 0 | 1 | 170400
3655 | 6 | 153 | 6 | 0 | 0.11292 | 1 | 170400
3656 | 6 | 153 | 7 | 1 | 0.32701 | 1 | 170200
3657 | 6 | 153 | 8 | 1 | 0.56122 | 1 | 170000
3658 | 6 | 153 | 9 | 0 | 0.7804 | 1 | 170000
3659 | 6 | 153 | 10 | 0 | 0.95748 | 1 | 170000
3660 | 6 | 153 | 11 | 0 | 1 | 1 | 170000
3661 | 6 | 153 | 12 | 0 | 1 | 1 | 170000
3662 | 6 | 153 | 13 | 0 | 1 | 1 | 170000
3663 | 6 | 153 | 14 | 0 | 0.95748 | 1 | 170000
3664 | 6 | 153 | 15 | 0 | 0.7804 | 1 | 170000
3665 | 6 | 153 | 16 | 0 | 0.56122 | 1 | 170000
3666 | 6 | 153 | 17 | 0 | 0.32701 | 1 | 170000
3667 | 6 | 153 | 18 | 0 | 0.11292 | 0.73119 | 170000
3668 | 6 | 153 | 19 | 1 | 0 | 0.80737 | 169800
3669 | 6 | 153 | 20 | 1 | 0 | 0.90384 | 169600
3670 | 6 | 153 | 21 | 0 | 0 | 0.73015 | 169600
3671 | 6 | 153 | 22 | 0 | 0 | 0.56902 | 169600
3672 | 6 | 153 | 23 | 0 | 0 | 0.41581 | 169600
3673 | 6 | 154 | 0 | 0 | 0 | 0.27289 | 169600
3674 | 6 | 154 | 1 | 0 | 0 | 0.24319 | 169600
3675 | 6 | 154 | 2 | 0 | 0 | 0.3258 | 169600
3676 | 6 | 154 | 3 | 0 | 0 | 0.40886 | 169600
3677 | 6 | 154 | 4 | 0 | 0 | 0.48372 | 169600
3678 | 6 | 154 | 5 | 0 | 0 | 0.61996 | 169600
3679 | 6 | 154 | 6 | 0 | 0.11227 | 0.47615 | 169600
3680 | 6 | 154 | 7 | 1 | 0.32513 | 0.44859 | 169400
3681 | 6 | 154 | 8 | 1 | 0.55799 | 0.47598 | 169200
3682 | 6 | 154 | 9 | 0 | 0.77591 | 0.3822 | 169200
3683 | 6 | 154 | 10 | 0 | 0.95197 | 0.52292 | 169200
3684 | 6 | 154 | 11 | 0 | 1 | 0.57449 | 169200
3685 | 6 | 154 | 12 | 0 | 1 | 0.42675 | 169200
3686 | 6 | 154 | 13 | 0 | 1 | 0.37948 | 169200
3687 | 6 | 154 | 14 | 0 | 0.95197 | 0.28277 | 169200
3688 | 6 | 154 | 15 | 0 | 0.77591 | 0.29831 | 169200
3689 | 6 | 154 | 16 | 0 | 0.55799 | 0.20968 | 169200
3690 | 6 | 154 | 17 | 0 | 0.32513 | 0.19817 | 169200
3691 | 6 | 154 | 18 | 0 | 0.11227 | 0.28247 | 169200
3692 | 6 | 154 | 19 | 1 | 0 | 0.24451 | 169000
3693 | 6 | 154 | 20 | 1 | 0 | 0.18393 | 168800
3694 | 6 | 154 | 21 | 0 | 0 | 0.24047 | 168800
3695 | 6 | 154 | 22 | 0 | 0 | 0.2255 | 168800
3696 | 6 | 154 | 23 | 0 | 0 | 0.18508 | 168800
3697 | 6 | 155 | 0 | 0 | 0 | 0.2782 | 168800
3698 | 6 | 155 | 1 | 0 | 0 | 0.30117 | 168800
3699 | 6 | 155 | 2 | 0 | 0 | 0.40134 | 168800
3700 | 6 | 155 | 3 | 0 | 0 | 0.61226 | 168800
3701 | 6 | 155 | 4 | 0 | 0 | 0.51895 | 168800
3702 | 6 | 155 | 5 | 0 | 0 | 0.5709 | 168800
3703 | 6 | 155 | 6 | 0 | 0.10608 | 0.74072 | 168800
3704 | 6 | 155 | 7 | 1 | 0.3072 | 0.5498 | 168600
3705 | 6 | 155 | 8 | 1 | 0.52723 | 0.6876 | 168400
3706 | 6 | 155 | 9 | 0 | 0.73313 | 0.86389 | 168400
3707 | 6 | 155 | 10 | 0 | 0.89949 | 0.7006 | 168400
3708 | 6 | 155 | 11 | 0 | 1 | 0.72592 | 168400
3709 | 6 | 155 | 12 | 0 | 1 | 0.55584 | 168400
3710 | 6 | 155 | 13 | 0 | 1 | 0.43613 | 168400
3711 | 6 | 155 | 14 | 0 | 0.89949 | 0.48339 | 168400
3712 | 6 | 155 | 15 | 0 | 0.73313 | 0.36521 | 168400
3713 | 6 | 155 | 16 | 0 | 0.52723 | 0.70462 | 168400
3714 | 6 | 155 | 17 | 0 | 0.3072 | 0.39659 | 168400
3715 | 6 | 155 | 18 | 0 | 0.10608 | 0.50216 | 168400
3716 | 6 | 155 | 19 | 1 | 0 | 0.57378 | 168200
3717 | 6 | 155 | 20 | 1 | 0 | 0.67675 | 168000
3718 | 6 | 155 | 21 | 0 | 0 | 0.63845 | 168000
3719 | 6 | 155 | 22 | 0 | 0 | 0.65589 | 168000
3720 | 6 | 155 | 23 | 0 | 0 | 0.62007 | 168000
3721 | 6 | 156 | 0 | 0 | 0 | 0.44628 | 168000
3722 | 6 | 156 | 1 | 0 | 0 | 0.20314 | 168000
3723 | 6 | 156 | 2 | 0 | 0 | 0.14234 | 168000
3724 | 6 | 156 | 3 | 0 | 0 | 0.18627 | 168000
3725 | 6 | 156 | 4 | 0 | 0 | 0.16993 | 168000
3726 | 6 | 156 | 5 | 0 | 0 | 0.17977 | 168000
3727 | 6 | 156 | 6 | 0 | 0.10377 | 0.19143 | 168000
3728 | 6 | 156 | 7 | 1 | 0.30051 | 0.21769 | 167800
3729 | 6 | 156 | 8 | 1 | 0.51575 | 0.2491 | 167600
3730 | 6 | 156 | 9 | 0 | 0.71716 | 0.24002 | 167600
3731 | 6 | 156 | 10 | 0 | 0.87989 | 0.26517 | 167600
3732 | 6 | 156 | 11 | 0 | 0.98532 | 0.29443 | 167600
3733 | 6 | 156 | 12 | 0 | 1 | 0.35929 | 167600
3734 | 6 | 156 | 13 | 0 | 0.98532 | 0.51612 | 167600
3735 | 6 | 156 | 14 | 0 | 0.87989 | 0.51568 | 167600
3736 | 6 | 156 | 15 | 0 | 0.71716 | 0.54706 | 167600
3737 | 6 | 156 | 16 | 0 | 0.51575 | 0.99989 | 167600
3738 | 6 | 156 | 17 | 0 | 0.30051 | 1 | 167600
3739 | 6 | 156 | 18 | 0 | 0.10377 | 0.83211 | 167600
3740 | 6 | 156 | 19 | 1 | 0 | 0.89042 | 167400
3741 | 6 | 156 | 20 | 1 | 0 | 0.90009 | 167200
3742 | 6 | 156 | 21 | 0 | 0 | 0.73408 | 167200
3743 | 6 | 156 | 22 | 0 | 0 | 0.65551 | 167200
3744 | 6 | 156 | 23 | 0 | 0 | 0.55324 | 167200
3745 | 6 | 157 | 0 | 0 | 0 | 0.52963 | 167200
3746 | 6 | 157 | 1 | 0 | 0 | 0.61836 | 167200
3747 | 6 | 157 | 2 | 0 | 0 | 0.33191 | 167200
3748 | 6 | 157 | 3 | 0 | 0 | 0.33498 | 167200
3749 | 6 | 157 | 4 | 0 | 0 | 0.33253 | 167200
3750 | 6 | 157 | 5 | 0 | 0 | 0.36652 | 167200
3751 | 6 | 157 | 6 | 0 | 0.099674 | 0.37205 | 167200
3752 | 6 | 157 | 7 | 1 | 0.28865 | 0.4568 | 167000
3753 | 6 | 157 | 8 | 1 | 0.49539 | 0.35606 | 166800
3754 | 6 | 157 | 9 | 0 | 0.68886 | 0.42715 | 166800
3755 | 6 | 157 | 10 | 0 | 0.84518 | 0.31423 | 166800
3756 | 6 | 157 | 11 | 0 | 0.94644 | 0.38906 | 166800
3757 | 6 | 157 | 12 | 0 | 0.98147 | 0.44627 | 166800
3758 | 6 | 157 | 13 | 0 | 0.94644 | 0.67883 | 166800
3759 | 6 | 157 | 14 | 0 | 0.84518 | 1 | 166800
3760 | 6 | 157 | 15 | 0 | 0.68886 | 1 | 166800
3761 | 6 | 157 | 16 | 0 | 0.49539 | 1 | 166800
3762 | 6 | 157 | 17 | 0 | 0.28865 | 1 | 166800
3763 | 6 | 157 | 18 | 0 | 0.099674 | 1 | 166800
3764 | 6 | 157 | 19 | 1 | 0 | 1 | 166600
3765 | 6 | 157 | 20 | 1 | 0 | 0.9763 | 166400
3766 | 6 | 157 | 21 | 0 | 0 | 0.90339 | 166400
3767 | 6 | 157 | 22 | 0 | 0 | 1 | 166400
3768 | 6 | 157 | 23 | 0 | 0 | 1 | 166400
3769 | 6 | 158 | 0 | 0 | 0 | 0.79853 | 166400
3770 | 6 | 158 | 1 | 0 | 0 | 1 | 166400
3771 | 6 | 158 | 2 | 0 | 0 | 1 | 166400
3772 | 6 | 158 | 3 | 0 | 0 | 1 | 166400
3773 | 6 | 158 | 4 | 0 | 0 | 1 | 166400
3774 | 6 | 158 | 5 | 0 | 0 | 0.71157 | 166400
3775 | 6 | 158 | 6 | 0 | 0.12012 | 1 | 166400
3776 | 6 | 158 | 7 | 1 | 0.34786 | 1 | 166200
3777 | 6 | 158 | 8 | 1 | 0.59701 | 1 | 166000
3778 | 6 | 158 | 9 | 0 | 0.83016 | 1 | 166000
3779 | 6 | 158 | 10 | 0 | 1 | 1 | 166000
3780 | 6 | 158 | 11 | 0 | 1 | 1 | 166000
3781 | 6 | 158 | 12 | 0 | 1 | 1 | 166000
3782 | 6 | 158 | 13 | 0 | 1 | 0.60494 | 166000
3783 | 6 | 158 | 14 | 0 | 1 | 0.68234 | 166000
3784 | 6 | 158 | 15 | 0 | 0.83016 | 0.58834 | 166000
3785 | 6 | 158 | 16 | 0 | 0.59701 | 0.42687 | 166000
3786 | 6 | 158 | 17 | 0 | 0.34786 | 0.45607 | 166000
3787 | 6 | 158 | 18 | 0 | 0.12012 | 0.46058 | 166000
3788 | 6 | 158 | 19 | 1 | 0 | 0.42267 | 165800
3789 | 6 | 158 | 20 | 1 | 0 | 0.30769 | 165600
3790 | 6 | 158 | 21 | 0 | 0 | 0.25094 | 165600
3791 | 6 | 158 | 22 | 0 | 0 | 0.37596 | 165600
3792 | 6 | 158 | 23 | 0 | 0 | 0.38817 | 165600
3793 | 6 | 159 | 0 | 0 | 0 | 0.36461 | 165600
3794 | 6 | 159 | 1 | 0 | 0 | 0.25811 | 165600
3795 | 6 | 159 | 2 | 0 | 0 | 0.3446 | 165600
3796 | 6 | 159 | 3 | 0 | 0 | 0.38275 | 165600
3797 | 6 | 159 | 4 | 0 | 0 | 0.44349 | 165600
3798 | 6 | 159 | 5 | 0 | 0 | 0.64915 | 165600
3799 | 6 | 159 | 6 | 0 | 0.10946 | 0.47835 | 165600
3800 | 6 | 159 | 7 | 1 | 0.31699 | 0.53211 | 165400
3801 | 6 | 159 | 8 | 1 | 0.54402 | 0.4771 | 165200
3802 | 6 | 159 | 9 | 0 | 0.75647 | 0.48108 | 165200
3803 | 6 | 159 | 10 | 0 | 0.92813 | 0.71532 | 165200
3804 | 6 | 159 | 11 | 0 | 1 | 0.63545 | 165200
3805 | 6 | 159 | 12 | 0 | 1 | 0.64672 | 165200
3806 | 6 | 159 | 13 | 0 | 1 | 0.82719 | 165200
3807 | 6 | 159 | 14 | 0 | 0.92813 | 0.7873 | 165200
3808 | 6 | 159 | 15 | 0 | 0.75647 | 0.56504 | 165200
3809 | 6 | 159 | 16 | 0 | 0.54402 | 0.53903 | 165200
3810 | 6 | 159 | 17 | 0 | 0.31699 | 0.43177 | 165200
3811 | 6 | 159 | 18 | 0 | 0.10946 | 0.35483 | 165200
3812 | 6 | 159 | 19 | 1 | 0 | 0.42356 | 165000
3813 | 6 | 159 | 20 | 1 | 0 | 0.5356 | 164800
3814 | 6 | 159 | 21 | 0 | 0 | 0.45829 | 164800
3815 | 6 | 159 | 22 | 0 | 0 | 0.3103 | 164800
3816 | 6 | 159 | 23 | 0 | 0 | 0.19664 | 164800
3817 | 6 | 160 | 0 | 0 | 0 | 0.3459 | 164800
3818 | 6 | 160 | 1 | 0 | 0 | 0.37984 | 164800
3819 | 6 | 160 | 2 | 0 | 0 | 0.40174 | 164800
3820 | 6 | 160 | 3 | 0 | 0 | 0.32843 | 164800
3821 | 6 | 160 | 4 | 0 | 0 | 0.39536 | 164800
3822 | 6 | 160 | 5 | 0 | 0 | 0.46037 | 164800
3823 | 6 | 160 | 6 | 0 | 0.13184 | 0.30374 | 164800
3824 | 6 | 160 | 7 | 1 | 0.38182 | 0.29916 | 164600
3825 | 6 | 160 | 8 | 1 | 0.65528 | 0.35642 | 164400
3826 | 6 | 160 | 9 | 0 | 0.91119 | 0.47371 | 164400
3827 | 6 | 160 | 10 | 0 | 1 | 0.43701 | 164400
3828 | 6 | 160 | 11 | 0 | 1 | 0.43619 | 164400
3829 | 6 | 160 | 12 | 0 | 1 | 0.45091 | 164400
3830 | 6 | 160 | 13 | 0 | 1 | 0.45785 | 164400
3831 | 6 | 160 | 14 | 0 | 1 | 0.45674 | 164400
3832 | 6 | 160 | 15 | 0 | 0.91119 | 0.33757 | 164400
3833 | 6 | 160 | 16 | 0 | 0.65528 | 0.22095 | 164400
3834 | 6 | 160 | 17 | 0 | 0.38182 | 0.40617 | 164400
3835 | 6 | 160 | 18 | 0 | 0.13184 | 0.30158 | 164400
3836 | 6 | 160 | 19 | 1 | 0 | 0.29443 | 164200
3837 | 6 | 160 | 20 | 1 | 0 | 0.20859 | 164000
3838 | 6 | 160 | 21 | 0 | 0 | 0.28707 | 164000
3839 | 6 | 160 | 22 | 0 | 0 | 0.25604 | 164000
3840 | 6 | 160 | 23 | 0 | 0 | 0.28009 | 164000
3841 | 6 | 161 | 0 | 0 | 0 | 0.36848 | 164000
3842 | 6 | 161 | 1 | 0 | 0 | 0.3696 | 164000
3843 | 6 | 161 | 2 | 0 | 0 | 0.29973 | 164000
3844 | 6 | 161 | 3 | 0 | 0 | 0.32432 | 164000
3845 | 6 | 161 | 4 | 0 | 0 | 0.36333 | 164000
3846 | 6 | 161 | 5 | 0 | 0 | 0.35675 | 164000
3847 | 6 | 161 | 6 | 0 | 0.12671 | 0.39166 | 164000
3848 | 6 | 161 | 7 | 1 | 0.36694 | 0.52779 | 163800
3849 | 6 | 161 | 8 | 1 | 0.62976 | 0.74524 | 163600
3850 | 6 | 161 | 9 | 0 | 0.8757 | 0.88638 | 163600
3851 | 6 | 161 | 10 | 0 | 1 | 0.88546 | 163600
3852 | 6 | 161 | 11 | 0 | 1 | 1 | 163600
3853 | 6 | 161 | 12 | 0 | 1 | 0.84366 | 163600
3854 | 6 | 161 | 13 | 0 | 1 | 0.60847 | 163600
3855 | 6 | 161 | 14 | 0 | 1 | 0.81803 | 163600
3856 | 6 | 161 | 15 | 0 | 0.8757 | 0.79261 | 163600
3857 | 6 | 161 | 16 | 0 | 0.62976 | 0.87087 | 163600
3858 | 6 | 161 | 17 | 0 | 0.36694 | 1 | 163600
3859 | 6 | 161 | 18 | 0 | 0.12671 | 1 | 163600
3860 | 6 | 161 | 19 | 1 | 0 | 1 | 163400
3861 | 6 | 161 | 20 | 1 | 0 | 1 | 163200
3862 | 6 | 161 | 21 | 0 | 0 | 1 | 163200
3863 | 6 | 161 | 22 | 0 | 0 | 0.73648 | 163200
3864 | 6 | 161 | 23 | 0 | 0 | 0.77907 | 163200
3865 | 6 | 162 | 0 | 0 | 0 | 0.65565 | 163200
3866 | 6 | 162 | 1 | 0 | 0 | 0.52267 | 163200
3867 | 6 | 162 | 2 | 0 | 0 | 0.41282 | 163200
3868 | 6 | 162 | 3 | 0 | 0 | 0.541 | 163200
3869 | 6 | 162 | 4 | 0 | 0 | 0.641 | 163200
3870 | 6 | 162 | 5 | 0 | 0 | 0.55524 | 163200
3871 | 6 | 162 | 6 | 0 | 0.11554 | 0.49761 | 163200
3872 | 6 | 162 | 7 | 1 | 0.3346 | 0.38585 | 163000
3873 | 6 | 162 | 8 | 1 | 0.57425 | 0.41253 | 162800
3874 | 6 | 162 | 9 | 0 | 0.79851 | 0.50827 | 162800
3875 | 6 | 162 | 10 | 0 | 0.9797 | 0.38577 | 162800
3876 | 6 | 162 | 11 | 0 | 1 | 0.33698 | 162800
3877 | 6 | 162 | 12 | 0 | 1 | 0.33102 | 162800
3878 | 6 | 162 | 13 | 0 | 1 | 0.44762 | 162800
3879 | 6 | 162 | 14 | 0 | 0.9797 | 0.47999 | 162800
3880 | 6 | 162 | 15 | 0 | 0.79851 | 0.49288 | 162800
3881 | 6 | 162 | 16 | 0 | 0.57425 | 0.34728 | 162800
3882 | 6 | 162 | 17 | 0 | 0.3346 | 0.22318 | 162800
3883 | 6 | 162 | 18 | 0 | 0.11554 | 0.22955 | 162800
3884 | 6 | 162 | 19 | 1 | 0 | 0.30553 | 162600
3885 | 6 | 162 | 20 | 1 | 0 | 0.35575 | 162400
3886 | 6 | 162 | 21 | 0 | 0 | 0.51167 | 162400
3887 | 6 | 162 | 22 | 0 | 0 | 0.50594 | 162400
3888 | 6 | 162 | 23 | 0 | 0 | 0.46888 | 162400
3889 | 6 | 163 | 0 | 0 | 0 | 0.30628 | 162400
3890 | 6 | 163 | 1 | 0 | 0 | 0.3499 | 162400
3891 | 6 | 163 | 2 | 0 | 0 | 0.42128 | 162400
3892 | 6 | 163 | 3 | 0 | 0 | 0.37801 | 162400
3893 | 6 | 163 | 4 | 0 | 0 | 0.33626 | 162400
3894 | 6 | 163 | 5 | 0 | 0 | 0.23846 | 162400
3895 | 6 | 163 | 6 | 0 | 0.10077 | 0.15777 | 162400
3896 | 6 | 163 | 7 | 1 | 0.29183 | 0.15514 | 162200
3897 | 6 | 163 | 8 | 1 | 0.50084 | 0.21572 | 162000
3898 | 6 | 163 | 9 | 0 | 0.69644 | 0.35776 | 162000
3899 | 6 | 163 | 10 | 0 | 0.85446 | 0.52933 | 162000
3900 | 6 | 163 | 11 | 0 | 0.95684 | 0.52846 | 162000
3901 | 6 | 163 | 12 | 0 | 0.99226 | 0.55192 | 162000
3902 | 6 | 163 | 13 | 0 | 0.95684 | 0.6194 | 162000
3903 | 6 | 163 | 14 | 0 | 0.85446 | 0.70471 | 162000
3904 | 6 | 163 | 15 | 0 | 0.69644 | 0.53782 | 162000
3905 | 6 | 163 | 16 | 0 | 0.50084 | 0.5901 | 162000
3906 | 6 | 163 | 17 | 0 | 0.29183 | 0.50656 | 162000
3907 | 6 | 163 | 18 | 0 | 0.10077 | 0.332 | 162000
3908 | 6 | 163 | 19 | 1 | 0 | 0.31427 | 161800
3909 | 6 | 163 | 20 | 1 | 0 | 0.30904 | 161600
3910 | 6 | 163 | 21 | 0 | 0 | 0.21357 | 161600
3911 | 6 | 163 | 22 | 0 | 0 | 0.19113 | 161600
3912 | 6 | 163 | 23 | 0 | 0 | 0.21772 | 161600
3913 | 6 | 164 | 0 | 0 | 0 | 0.34347 | 161600
3914 | 6 | 164 | 1 | 0 | 0 | 0.29229 | 161600
3915 | 6 | 164 | 2 | 0 | 0 | 0.26891 | 161600
3916 | 6 | 164 | 3 | 0 | 0 | 0.39991 | 161600
3917 | 6 | 164 | 4 | 0 | 0 | 0.38006 | 161600
3918 | 6 | 164 | 5 | 0 | 0 | 0.34535 | 161600
3919 | 6 | 164 | 6 | 0 | 0.11959 | 0.37243 | 161600
3920 | 6 | 164 | 7 | 1 | 0.34632 | 0.37725 | 161400
3921 | 6 | 164 | 8 | 1 | 0.59437 | 0.4922 | 161200
3922 | 6 | 164 | 9 | 0 | 0.82649 | 0.44414 | 161200
3923 | 6 | 164 | 10 | 0 | 1 | 0.40894 | 161200
3924 | 6 | 164 | 11 | 0 | 1 | 0.51951 | 161200
3925 | 6 | 164 | 12 | 0 | 1 | 0.71067 | 161200
3926 | 6 | 164 | 13 | 0 | 1 | 0.72088 | 161200
3927 | 6 | 164 | 14 | 0 | 1 | 0.93592 | 161200
3928 | 6 | 164 | 15 | 0 | 0.82649 | 0.75358 | 161200
3929 | 6 | 164 | 16 | 0 | 0.59437 | 0.63859 | 161200
3930 | 6 | 164 | 17 | 0 | 0.34632 | 0.78107 | 161200
3931 | 6 | 164 | 18 | 0 | 0.11959 | 0.54875 | 161200
3932 | 6 | 164 | 19 | 1 | 0 | 0.59028 | 161000
3933 | 6 | 164 | 20 | 1 | 0 | 0.40593 | 160800
3934 | 6 | 164 | 21 | 0 | 0 | 0.40042 | 160800
3935 | 6 | 164 | 22 | 0 | 0 | 0.34105 | 160800
3936 | 6 | 164 | 23 | 0 | 0 | 0.27027 | 160800
3937 | 6 | 165 | 0 | 0 | 0 | 0.20812 | 160800
3938 | 6 | 165 | 1 | 0 | 0 | 0.17331 | 160800
3939 | 6 | 165 | 2 | 0 | 0 | 0.21113 | 160800
3940 | 6 | 165 | 3 | 0 | 0 | 0.19914 | 160800
3941 | 6 | 165 | 4 | 0 | 0 | 0.22909 | 160800
3942 | 6 | 165 | 5 | 0 | 0 | 0.20821 | 160800
3943 | 6 | 165 | 6 | 0 | 0.10659 | 0.2086 | 160800
3944 | 6 | 165 | 7 | 1 | 0.30868 | 0.19872 | 160600
3945 | 6 | 165 | 8 | 1 | 0.52975 | 0.30198 | 160400
3946 | 6 | 165 | 9 | 0 | 0.73664 | 0.43398 | 160400
3947 | 6 | 165 | 10 | 0 | 0.9038 | 0.45676 | 160400
3948 | 6 | 165 | 11 | 0 | 1 | 0.76962 | 160400
3949 | 6 | 165 | 12 | 0 | 1 | 0.84427 | 160400
3950 | 6 | 165 | 13 | 0 | 1 | 0.69223 | 160400
3951 | 6 | 165 | 14 | 0 | 0.9038 | 0.60324 | 160400
3952 | 6 | 165 | 15 | 0 | 0.73664 | 0.51952 | 160400
3953 | 6 | 165 | 16 | 0 | 0.52975 | 0.58029 | 160400
3954 | 6 | 165 | 17 | 0 | 0.30868 | 0.66362 | 160400
3955 | 6 | 165 | 18 | 0 | 0.10659 | 0.57351 | 160400
3956 | 6 | 165 | 19 | 1 | 0 | 0.65906 | 160200
3957 | 6 | 165 | 20 | 1 | 0 | 0.77534 | 160000
3958 | 6 | 165 | 21 | 0 | 0 | 0.74981 | 160000
3959 | 6 | 165 | 22 | 0 | 0 | 0.72093 | 160000
3960 | 6 | 165 | 23 | 0 | 0 | 0.69118 | 160000
3961 | 6 | 166 | 0 | 0 | 0 | 0.54225 | 160000
3962 | 6 | 166 | 1 | 0 | 0 | 0.48337 | 160000
3963 | 6 | 166 | 2 | 0 | 0 | 0.53727 | 160000
3964 | 6 | 166 | 3 | 0 | 0 | 0.72584 | 160000
3965 | 6 | 166 | 4 | 0 | 0 | 0.40266 | 160000
3966 | 6 | 166 | 5 | 0 | 0 | 0.43093 | 160000
3967 | 6 | 166 | 6 | 0 | 0.10415 | 0.43964 | 160000
3968 | 6 | 166 | 7 | 1 | 0.3016 | 0.45644 | 159800
3969 | 6 | 166 | 8 | 1 | 0.51762 | 0.42894 | 159600
3970 | 6 | 166 | 9 | 0 | 0.71976 | 0.28309 | 159600
3971 | 6 | 166 | 10 | 0 | 0.88309 | 0.38155 | 159600
3972 | 6 | 166 | 11 | 0 | 0.9889 | 0.39006 | 159600
3973 | 6 | 166 | 12 | 0 | 1 | 0.4208 | 159600
3974 | 6 | 166 | 13 | 0 | 0.9889 | 0.51241 | 159600
3975 | 6 | 166 | 14 | 0 | 0.88309 | 0.72342 | 159600
3976 | 6 | 166 | 15 | 0 | 0.71976 | 0.67462 | 159600
3977 | 6 | 166 | 16 | 0 | 0.51762 | 0.6957 | 159600
3978 | 6 | 166 | 17 | 0 | 0.3016 | 0.40004 | 159600
3979 | 6 | 166 | 18 | 0 | 0.10415 | 0.25918 | 159600
3980 | 6 | 166 | 19 | 1 | 0 | 0.31418 | 159400
3981 | 6 | 166 | 20 | 1 | 0 | 0.21807 | 159200
3982 | 6 | 166 | 21 | 0 | 0 | 0.19686 | 159200
3983 | 6 | 166 | 22 | 0 | 0 | 0.11682 | 159200
3984 | 6 | 166 | 23 | 0 | 0 | 0.13492 | 159200
3985 | 6 | 167 | 0 | 0 | 0 | 0.13181 | 159200
3986 | 6 | 167 | 1 | 0 | 0 | 0.15824 | 159200
3987 | 6 | 167 | 2 | 0 | 0 | 0.14159 | 159200
3988 | 6 | 167 | 3 | 0 | 0 | 0.0881 | 159200
3989 | 6 | 167 | 4 | 0 | 0 | 0.1283 | 159200
3990 | 6 | 167 | 5 | 0 | 0 | 0.12878 | 159200
3991 | 6 | 167 | 6 | 0 | 0.10962 | 0.092496 | 159200
3992 | 6 | 167 | 7 | 1 | 0.31747 | 0.15462 | 159000
3993 | 6 | 167 | 8 | 1 | 0.54485 | 0.10171 | 158800
3994 | 6 | 167 | 9 | 0 | 0.75763 | 0.095016 | 158800
3995 | 6 | 167 | 10 | 0 | 0.92954 | 0.14549 | 158800
3996 | 6 | 167 | 11 | 0 | 1 | 0.24911 | 158800
3997 | 6 | 167 | 12 | 0 | 1 | 0.20953 | 158800
3998 | 6 | 167 | 13 | 0 | 1 | 0.20135 | 158800
3999 | 6 | 167 | 14 | 0 | 0.92954 | 0.22608 | 158800
4000 | 6 | 167 | 15 | 0 | 0.75763 | 0.25289 | 158800
4001 | 6 | 167 | 16 | 0 | 0.54485 | 0.29313 | 158800
4002 | 6 | 167 | 17 | 0 | 0.31747 | 0.2132 | 158800
4003 | 6 | 167 | 18 | 0 | 0.10962 | 0.1505 | 158800
4004 | 6 | 167 | 19 | 1 | 0 | 0.17516 | 158600
4005 | 6 | 167 | 20 | 1 | 0 | 0.15791 | 158400
4006 | 6 | 167 | 21 | 0 | 0 | 0.14467 | 158400
4007 | 6 | 167 | 22 | 0 | 0 | 0.14085 | 158400
4008 | 6 | 167 | 23 | 0 | 0 | 0.16378 | 158400
4009 | 6 | 168 | 0 | 0 | 0 | 0.17579 | 158400
4010 | 6 | 168 | 1 | 0 | 0 | 0.20211 | 158400
4011 | 6 | 168 | 2 | 0 | 0 | 0.26244 | 158400
4012 | 6 | 168 | 3 | 0 | 0 | 0.26732 | 158400
4013 | 6 | 168 | 4 | 0 | 0 | 0.33744 | 158400
4014 | 6 | 168 | 5 | 0 | 0 | 0.39466 | 158400
4015 | 6 | 168 | 6 | 0 | 0.11311 | 0.30475 | 158400
4016 | 6 | 168 | 7 | 1 | 0.32758 | 0.26508 | 158200
4017 | 6 | 168 | 8 | 1 | 0.56219 | 0.39425 | 158000
4018 | 6 | 168 | 9 | 0 | 0.78175 | 0.33325 | 158000
4019 | 6 | 168 | 10 | 0 | 0.95913 | 0.268 | 158000
4020 | 6 | 168 | 11 | 0 | 1 | 0.37191 | 158000
4021 | 6 | 168 | 12 | 0 | 1 | 0.48927 | 158000
4022 | 6 | 168 | 13 | 0 | 1 | 0.5347 | 158000
4023 | 6 | 168 | 14 | 0 | 0.95913 | 0.39325 | 158000
4024 | 6 | 168 | 15 | 0 | 0.78175 | 0.37218 | 158000
4025 | 6 | 168 | 16 | 0 | 0.56219 | 0.34459 | 158000
4026 | 6 | 168 | 17 | 0 | 0.32758 | 0.25764 | 158000
4027 | 6 | 168 | 18 | 0 | 0.11311 | 0.29862 | 158000
4028 | 6 | 168 | 19 | 1 | 0 | 0.33473 | 157800
4029 | 6 | 168 | 20 | 1 | 0 | 0.25502 | 157600
4030 | 6 | 168 | 21 | 0 | 0 | 0.31093 | 157600
4031 | 6 | 168 | 22 | 0 | 0 | 0.31583 | 157600
4032 | 6 | 168 | 23 | 0 | 0 | 0.3874 | 157600
4033 | 6 | 169 | 0 | 0 | 0 | 0.33684 | 157600
4034 | 6 | 169 | 1 | 0 | 0 | 0.3493 | 157600
4035 | 6 | 169 | 2 | 0 | 0 | 0.25592 | 157600
4036 | 6 | 169 | 3 | 0 | 0 | 0.32836 | 157600
4037 | 6 | 169 | 4 | 0 | 0 | 0.46595 | 157600
4038 | 6 | 169 | 5 | 0 | 0 | 0.54251 | 157600
4039 | 6 | 169 | 6 | 0 | 0.11678 | 0.52734 | 157600
4040 | 6 | 169 | 7 | 1 | 0.3382 | 0.6233 | 157400
4041 | 6 | 169 | 8 | 1 | 0.58043 | 0.61065 | 157200
4042 | 6 | 169 | 9 | 0 | 0.8071 | 0.58219 | 157200
4043 | 6 | 169 | 10 | 0 | 0.99024 | 0.92744 | 157200
4044 | 6 | 169 | 11 | 0 | 1 | 0.92966 | 157200
4045 | 6 | 169 | 12 | 0 | 1 | 1 | 157200
4046 | 6 | 169 | 13 | 0 | 1 | 0.99039 | 157200
4047 | 6 | 169 | 14 | 0 | 0.99024 | 0.70692 | 157200
4048 | 6 | 169 | 15 | 0 | 0.8071 | 0.76304 | 157200
4049 | 6 | 169 | 16 | 0 | 0.58043 | 0.60555 | 157200
4050 | 6 | 169 | 17 | 0 | 0.3382 | 0.65777 | 157200
4051 | 6 | 169 | 18 | 0 | 0.11678 | 0.39105 | 157200
4052 | 6 | 169 | 19 | 1 | 0 | 0.55666 | 157000
4053 | 6 | 169 | 20 | 1 | 0 | 0.26411 | 156800
4054 | 6 | 169 | 21 | 0 | 0 | 0.31347 | 156800
4055 | 6 | 169 | 22 | 0 | 0 | 0.37657 | 156800
4056 | 6 | 169 | 23 | 0 | 0 | 0.35602 | 156800
4057 | 6 | 170 | 0 | 0 | 0 | 0.21917 | 156800
4058 | 6 | 170 | 1 | 0 | 0 | 0.23497 | 156800
4059 | 6 | 170 | 2 | 0 | 0 | 0.28752 | 156800
4060 | 6 | 170 | 3 | 0 | 0 | 0.36522 | 156800
4061 | 6 | 170 | 4 | 0 | 0 | 0.32366 | 156800
4062 | 6 | 170 | 5 | 0 | 0 | 0.41017 | 156800
4063 | 6 | 170 | 6 | 0 | 0.12326 | 0.28299 | 156800
4064 | 6 | 170 | 7 | 1 | 0.35696 | 0.29221 | 156600
4065 | 6 | 170 | 8 | 1 | 0.61263 | 0.38428 | 156400
4066 | 6 | 170 | 9 | 0 | 0.85188 | 0.4972 | 156400
4067 | 6 | 170 | 10 | 0 | 1 | 0.60258 | 156400
4068 | 6 | 170 | 11 | 0 | 1 | 0.40808 | 156400
4069 | 6 | 170 | 12 | 0 | 1 | 0.49722 | 156400
4070 | 6 | 170 | 13 | 0 | 1 | 0.39834 | 156400
4071 | 6 | 170 | 14 | 0 | 1 | 0.44783 | 156400
4072 | 6 | 170 | 15 | 0 | 0.85188 | 0.45996 | 156400
4073 | 6 | 170 | 16 | 0 | 0.61263 | 0.43757 | 156400
4074 | 6 | 170 | 17 | 0 | 0.35696 | 0.42784 | 156400
4075 | 6 | 170 | 18 | 0 | 0.12326 | 0.43704 | 156400
4076 | 6 | 170 | 19 | 1 | 0 | 0.34441 | 156200
4077 | 6 | 170 | 20 | 1 | 0 | 0.28687 | 156000
4078 | 6 | 170 | 21 | 0 | 0 | 0.23352 | 156000
4079 | 6 | 170 | 22 | 0 | 0 | 0.30035 | 156000
4080 | 6 | 170 | 23 | 0 | 0 | 0.25291 | 156000
4081 | 6 | 171 | 0 | 0 | 0 | 0.21733 | 156000
4082 | 6 | 171 | 1 | 0 | 0 | 0.21616 | 156000
4083 | 6 | 171 | 2 | 0 | 0 | 0.23775 | 156000
4084 | 6 | 171 | 3 | 0 | 0 | 0.3346 | 156000
4085 | 6 | 171 | 4 | 0 | 0 | 0.36934 | 156000
4086 | 6 | 171 | 5 | 0 | 0 | 0.45306 | 156000
4087 | 6 | 171 | 6 | 0 | 0.094821 | 0.44827 | 156000
4088 | 6 | 171 | 7 | 1 | 0.2746 | 0.42989 | 155800
4089 | 6 | 171 | 8 | 1 | 0.47127 | 0.49413 | 155600
4090 | 6 | 171 | 9 | 0 | 0.65532 | 0.49914 | 155600
4091 | 6 | 171 | 10 | 0 | 0.80402 | 0.51518 | 155600
4092 | 6 | 171 | 11 | 0 | 0.90036 | 0.59361 | 155600
4093 | 6 | 171 | 12 | 0 | 0.93368 | 0.58071 | 155600
4094 | 6 | 171 | 13 | 0 | 0.90036 | 0.78473 | 155600
4095 | 6 | 171 | 14 | 0 | 0.80402 | 0.69133 | 155600
4096 | 6 | 171 | 15 | 0 | 0.65532 | 0.78548 | 155600
4097 | 6 | 171 | 16 | 0 | 0.47127 | 0.64488 | 155600
4098 | 6 | 171 | 17 | 0 | 0.2746 | 0.51302 | 155600
4099 | 6 | 171 | 18 | 0 | 0.094821 | 0.46311 | 155600
4100 | 6 | 171 | 19 | 1 | 0 | 0.48572 | 155400
4101 | 6 | 171 | 20 | 1 | 0 | 0.78264 | 155200
4102 | 6 | 171 | 21 | 0 | 0 | 0.75935 | 155200
4103 | 6 | 171 | 22 | 0 | 0 | 0.76367 | 155200
4104 | 6 | 171 | 23 | 0 | 0 | 1 | 155200
4105 | 6 | 172 | 0 | 0 | 0 | 1 | 155200
4106 | 6 | 172 | 1 | 0 | 0 | 0.91829 | 155200
4107 | 6 | 172 | 2 | 0 | 0 | 0.86375 | 155200
4108 | 6 | 172 | 3 | 0 | 0 | 0.96759 | 155200
4109 | 6 | 172 | 4 | 0 | 0 | 1 | 155200
4110 | 6 | 172 | 5 | 0 | 0 | 1 | 155200
4111 | 6 | 172 | 6 | 0 | 0.12064 | 0.99403 | 155200
4112 | 6 | 172 | 7 | 1 | 0.34937 | 1 | 155000
4113 | 6 | 172 | 8 | 1 | 0.59959 | 1 | 154800
4114 | 6 | 172 | 9 | 0 | 0.83375 | 1 | 154800
4115 | 6 | 172 | 10 | 0 | 1 | 1 | 154800
4116 | 6 | 172 | 11 | 0 | 1 | 1 | 154800
4117 | 6 | 172 | 12 | 0 | 1 | 1 | 154800
4118 | 6 | 172 | 13 | 0 | 1 | 0.9803 | 154800
4119 | 6 | 172 | 14 | 0 | 1 | 0.58913 | 154800
4120 | 6 | 172 | 15 | 0 | 0.83375 | 0.52901 | 154800
4121 | 6 | 172 | 16 | 0 | 0.59959 | 0.43388 | 154800
4122 | 6 | 172 | 17 | 0 | 0.34937 | 0.41309 | 154800
4123 | 6 | 172 | 18 | 0 | 0.12064 | 0.51193 | 154800
4124 | 6 | 172 | 19 | 1 | 0 | 0.44105 | 154600
4125 | 6 | 172 | 20 | 1 | 0 | 0.54387 | 154400
4126 | 6 | 172 | 21 | 0 | 0 | 0.77234 | 154400
4127 | 6 | 172 | 22 | 0 | 0 | 0.74353 | 154400
4128 | 6 | 172 | 23 | 0 | 0 | 0.62728 | 154400
4129 | 6 | 173 | 0 | 0 | 0 | 0.42852 | 154400
4130 | 6 | 173 | 1 | 0 | 0 | 0.32437 | 154400
4131 | 6 | 173 | 2 | 0 | 0 | 0.3033 | 154400
4132 | 6 | 173 | 3 | 0 | 0 | 0.31893 | 154400
4133 | 6 | 173 | 4 | 0 | 0 | 0.34755 | 154400
4134 | 6 | 173 | 5 | 0 | 0 | 0.24611 | 154400
4135 | 6 | 173 | 6 | 0 | 0.11375 | 0.17485 | 154400
4136 | 6 | 173 | 7 | 1 | 0.32942 | 0.26912 | 154200
4137 | 6 | 173 | 8 | 1 | 0.56536 | 0.22941 | 154000
4138 | 6 | 173 | 9 | 0 | 0.78615 | 0.27337 | 154000
4139 | 6 | 173 | 10 | 0 | 0.96454 | 0.42043 | 154000
4140 | 6 | 173 | 11 | 0 | 1 | 0.5061 | 154000
4141 | 6 | 173 | 12 | 0 | 1 | 0.5239 | 154000
4142 | 6 | 173 | 13 | 0 | 1 | 0.39829 | 154000
4143 | 6 | 173 | 14 | 0 | 0.96454 | 0.39443 | 154000
4144 | 6 | 173 | 15 | 0 | 0.78615 | 0.31945 | 154000
4145 | 6 | 173 | 16 | 0 | 0.56536 | 0.39848 | 154000
4146 | 6 | 173 | 17 | 0 | 0.32942 | 0.3669 | 154000
4147 | 6 | 173 | 18 | 0 | 0.11375 | 0.27447 | 154000
4148 | 6 | 173 | 19 | 1 | 0 | 0.42587 | 153800
4149 | 6 | 173 | 20 | 1 | 0 | 0.43495 | 153600
4150 | 6 | 173 | 21 | 0 | 0 | 0.45953 | 153600
4151 | 6 | 173 | 22 | 0 | 0 | 0.47366 | 153600
4152 | 6 | 173 | 23 | 0 | 0 | 0.49925 | 153600
4153 | 6 | 174 | 0 | 0 | 0 | 0.61979 | 153600
4154 | 6 | 174 | 1 | 0 | 0 | 0.69251 | 153600
4155 | 6 | 174 | 2 | 0 | 0 | 1 | 153600
4156 | 6 | 174 | 3 | 0 | 0 | 1 | 153600
4157 | 6 | 174 | 4 | 0 | 0 | 1 | 153600
4158 | 6 | 174 | 5 | 0 | 0 | 1 | 153600
4159 | 6 | 174 | 6 | 0 | 0.13055 | 1 | 153600
4160 | 6 | 174 | 7 | 1 | 0.37806 | 1 | 153400
4161 | 6 | 174 | 8 | 1 | 0.64883 | 0.70078 | 153200
4162 | 6 | 174 | 9 | 0 | 0.90222 | 0.57437 | 153200
4163 | 6 | 174 | 10 | 0 | 1 | 0.53861 | 153200
4164 | 6 | 174 | 11 | 0 | 1 | 0.32594 | 153200
4165 | 6 | 174 | 12 | 0 | 1 | 0.63142 | 153200
4166 | 6 | 174 | 13 | 0 | 1 | 0.69905 | 153200
4167 | 6 | 174 | 14 | 0 | 1 | 0.71866 | 153200
4168 | 6 | 174 | 15 | 0 | 0.90222 | 1 | 153200
4169 | 6 | 174 | 16 | 0 | 0.64883 | 1 | 153200
4170 | 6 | 174 | 17 | 0 | 0.37806 | 0.97971 | 153200
4171 | 6 | 174 | 18 | 0 | 0.13055 | 0.66576 | 153200
4172 | 6 | 174 | 19 | 1 | 0 | 0.88404 | 153000
4173 | 6 | 174 | 20 | 1 | 0 | 0.61564 | 152800
4174 | 6 | 174 | 21 | 0 | 0 | 0.52805 | 152800
4175 | 6 | 174 | 22 | 0 | 0 | 0.48069 | 152800
4176 | 6 | 174 | 23 | 0 | 0 | 0.67215 | 152800
4177 | 6 | 175 | 0 | 0 | 0 | 0.61375 | 152800
4178 | 6 | 175 | 1 | 0 | 0 | 0.54542 | 152800
4179 | 6 | 175 | 2 | 0 | 0 | 0.50129 | 152800
4180 | 6 | 175 | 3 | 0 | 0 | 0.45063 | 152800
4181 | 6 | 175 | 4 | 0 | 0 | 0.67525 | 152800
4182 | 6 | 175 | 5 | 0 | 0 | 0.56105 | 152800
4183 | 6 | 175 | 6 | 0 | 0.1363 | 0.66531 | 152800
4184 | 6 | 175 | 7 | 1 | 0.39471 | 0.4807 | 152600
4185 | 6 | 175 | 8 | 1 | 0.67742 | 0.52001 | 152400
4186 | 6 | 175 | 9 | 0 | 0.94197 | 0.55788 | 152400
4187 | 6 | 175 | 10 | 0 | 1 | 0.5856 | 152400
4188 | 6 | 175 | 11 | 0 | 1 | 0.39776 | 152400
4189 | 6 | 175 | 12 | 0 | 1 | 0.38209 | 152400
4190 | 6 | 175 | 13 | 0 | 1 | 0.24733 | 152400
4191 | 6 | 175 | 14 | 0 | 1 | 0.22795 | 152400
4192 | 6 | 175 | 15 | 0 | 0.94197 | 0.24312 | 152400
4193 | 6 | 175 | 16 | 0 | 0.67742 | 0.28995 | 152400
4194 | 6 | 175 | 17 | 0 | 0.39471 | 0.15057 | 152400
4195 | 6 | 175 | 18 | 0 | 0.1363 | 0.10117 | 152400
4196 | 6 | 175 | 19 | 1 | 0 | 0.17835 | 152200
4197 | 6 | 175 | 20 | 1 | 0 | 0.20552 | 152000
4198 | 6 | 175 | 21 | 0 | 0 | 0.1791 | 152000
4199 | 6 | 175 | 22 | 0 | 0 | 0.14235 | 152000
4200 | 6 | 175 | 23 | 0 | 0 | 0.12759 | 152000
4201 | 6 | 176 | 0 | 0 | 0 | 0.12788 | 152000
4202 | 6 | 176 | 1 | 0 | 0 | 0.18702 | 152000
4203 | 6 | 176 | 2 | 0 | 0 | 0.24001 | 152000
4204 | 6 | 176 | 3 | 0 | 0 | 0.1436 | 152000
4205 | 6 | 176 | 4 | 0 | 0 | 0.14284 | 152000
4206 | 6 | 176 | 5 | 0 | 0 | 0.17121 | 152000
4207 | 6 | 176 | 6 | 0 | 0.1385 | 0.1816 | 152000
4208 | 6 | 176 | 7 | 1 | 0.40109 | 0.2352 | 151800
4209 | 6 | 176 | 8 | 1 | 0.68836 | 0.29248 | 151600
4210 | 6 | 176 | 9 | 0 | 0.95719 | 0.29108 | 151600
4211 | 6 | 176 | 10 | 0 | 1 | 0.28635 | 151600
4212 | 6 | 176 | 11 | 0 | 1 | 0.28565 | 151600
4213 | 6 | 176 | 12 | 0 | 1 | 0.27042 | 151600
4214 | 6 | 176 | 13 | 0 | 1 | 0.36997 | 151600
4215 | 6 | 176 | 14 | 0 | 1 | 0.45613 | 151600
4216 | 6 | 176 | 15 | 0 | 0.95719 | 0.41027 | 151600
4217 | 6 | 176 | 16 | 0 | 0.68836 | 0.45317 | 151600
4218 | 6 | 176 | 17 | 0 | 0.40109 | 0.56431 | 151600
4219 | 6 | 176 | 18 | 0 | 0.1385 | 0.58931 | 151600
4220 | 6 | 176 | 19 | 1 | 0 | 0.48851 | 151400
4221 | 6 | 176 | 20 | 1 | 0 | 0.65504 | 151200
4222 | 6 | 176 | 21 | 0 | 0 | 0.65729 | 151200
4223 | 6 | 176 | 22 | 0 | 0 | 0.84009 | 151200
4224 | 6 | 176 | 23 | 0 | 0 | 0.98616 | 151200
4225 | 6 | 177 | 0 | 0 | 0 | 1 | 151200
4226 | 6 | 177 | 1 | 0 | 0 | 1 | 151200
4227 | 6 | 177 | 2 | 0 | 0 | 0.97306 | 151200
4228 | 6 | 177 | 3 | 0 | 0 | 1 | 151200
4229 | 6 | 177 | 4 | 0 | 0 | 0.89096 | 151200
4230 | 6 | 177 | 5 | 0 | 0 | 0.61906 | 151200
4231 | 6 | 177 | 6 | 0 | 0.10612 | 0.39517 | 151200
4232 | 6 | 177 | 7 | 1 | 0.30731 | 0.38991 | 151000
4233 | 6 | 177 | 8 | 1 | 0.52741 | 0.3762 | 150800
4234 | 6 | 177 | 9 | 0 | 0.73338 | 0.23619 | 150800
4235 | 6 | 177 | 10 | 0 | 0.89979 | 0.14722 | 150800
4236 | 6 | 177 | 11 | 0 | 1 | 0.15354 | 150800
4237 | 6 | 177 | 12 | 0 | 1 | 0.21427 | 150800
4238 | 6 | 177 | 13 | 0 | 1 | 0.20748 | 150800
4239 | 6 | 177 | 14 | 0 | 0.89979 | 0.24092 | 150800
4240 | 6 | 177 | 15 | 0 | 0.73338 | 0.24615 | 150800
4241 | 6 | 177 | 16 | 0 | 0.52741 | 0.41317 | 150800
4242 | 6 | 177 | 17 | 0 | 0.30731 | 0.29219 | 150800
4243 | 6 | 177 | 18 | 0 | 0.10612 | 0.20783 | 150800
4244 | 6 | 177 | 19 | 1 | 0 | 0.29892 | 150600
4245 | 6 | 177 | 20 | 1 | 0 | 0.23932 | 150400
4246 | 6 | 177 | 21 | 0 | 0 | 0.17855 | 150400
4247 | 6 | 177 | 22 | 0 | 0 | 0.2088 | 150400
4248 | 6 | 177 | 23 | 0 | 0 | 0.23281 | 150400
4249 | 6 | 178 | 0 | 0 | 0 | 0.28306 | 150400
4250 | 6 | 178 | 1 | 0 | 0 | 0.29903 | 150400
4251 | 6 | 178 | 2 | 0 | 0 | 0.29679 | 150400
4252 | 6 | 178 | 3 | 0 | 0 | 0.25492 | 150400
4253 | 6 | 178 | 4 | 0 | 0 | 0.22951 | 150400
4254 | 6 | 178 | 5 | 0 | 0 | 0.2283 | 150400
4255 | 6 | 178 | 6 | 0 | 0.094749 | 0.26946 | 150400
4256 | 6 | 178 | 7 | 1 | 0.27439 | 0.39995 | 150200
4257 | 6 | 178 | 8 | 1 | 0.47091 | 0.5764 | 150000
4258 | 6 | 178 | 9 | 0 | 0.65482 | 0.48712 | 150000
4259 | 6 | 178 | 10 | 0 | 0.80341 | 0.49697 | 150000
4260 | 6 | 178 | 11 | 0 | 0.89967 | 0.45856 | 150000
4261 | 6 | 178 | 12 | 0 | 0.93297 | 0.31099 | 150000
4262 | 6 | 178 | 13 | 0 | 0.89967 | 0.45959 | 150000
4263 | 6 | 178 | 14 | 0 | 0.80341 | 0.60061 | 150000
4264 | 6 | 178 | 15 | 0 | 0.65482 | 0.6121 | 150000
4265 | 6 | 178 | 16 | 0 | 0.47091 | 0.45012 | 150000
4266 | 6 | 178 | 17 | 0 | 0.27439 | 0.30333 | 150000
4267 | 6 | 178 | 18 | 0 | 0.094749 | 0.28346 | 150000
4268 | 6 | 178 | 19 | 1 | 0 | 0.57763 | 149800
4269 | 6 | 178 | 20 | 1 | 0 | 0.74543 | 149600
4270 | 6 | 178 | 21 | 0 | 0 | 0.50249 | 149600
4271 | 6 | 178 | 22 | 0 | 0 | 0.40157 | 149600
4272 | 6 | 178 | 23 | 0 | 0 | 0.27059 | 149600
4273 | 6 | 179 | 0 | 0 | 0 | 0.23927 | 149600
4274 | 6 | 179 | 1 | 0 | 0 | 0.21739 | 149600
4275 | 6 | 179 | 2 | 0 | 0 | 0.16534 | 149600
4276 | 6 | 179 | 3 | 0 | 0 | 0.20532 | 149600
4277 | 6 | 179 | 4 | 0 | 0 | 0.31193 | 149600
4278 | 6 | 179 | 5 | 0 | 0 | 0.34221 | 149600
4279 | 6 | 179 | 6 | 0 | 0.12961 | 0.37365 | 149600
4280 | 6 | 179 | 7 | 1 | 0.37536 | 0.48788 | 149400
4281 | 6 | 179 | 8 | 1 | 0.6442 | 0.49887 | 149200
4282 | 6 | 179 | 9 | 0 | 0.89578 | 0.55843 | 149200
4283 | 6 | 179 | 10 | 0 | 1 | 0.74232 | 149200
4284 | 6 | 179 | 11 | 0 | 1 | 0.65225 | 149200
4285 | 6 | 179 | 12 | 0 | 1 | 0.61573 | 149200
4286 | 6 | 179 | 13 | 0 | 1 | 0.76126 | 149200
4287 | 6 | 179 | 14 | 0 | 1 | 1 | 149200
4288 | 6 | 179 | 15 | 0 | 0.89578 | 0.95147 | 149200
4289 | 6 | 179 | 16 | 0 | 0.6442 | 0.65281 | 149200
4290 | 6 | 179 | 17 | 0 | 0.37536 | 0.43448 | 149200
4291 | 6 | 179 | 18 | 0 | 0.12961 | 0.66606 | 149200
4292 | 6 | 179 | 19 | 1 | 0 | 0.552 | 149000
4293 | 6 | 179 | 20 | 1 | 0 | 0.47815 | 148800
4294 | 6 | 179 | 21 | 0 | 0 | 0.48144 | 148800
4295 | 6 | 179 | 22 | 0 | 0 | 0.55963 | 148800
4296 | 6 | 179 | 23 | 0 | 0 | 0.49023 | 148800
4297 | 6 | 180 | 0 | 0 | 0 | 0.43684 | 148800
4298 | 6 | 180 | 1 | 0 | 0 | 0.40351 | 148800
4299 | 6 | 180 | 2 | 0 | 0 | 0.41018 | 148800
4300 | 6 | 180 | 3 | 0 | 0 | 0.53959 | 148800
4301 | 6 | 180 | 4 | 0 | 0 | 0.49777 | 148800
4302 | 6 | 180 | 5 | 0 | 0 | 0.4987 | 148800
4303 | 6 | 180 | 6 | 0 | 0.091621 | 0.58263 | 148800
4304 | 6 | 180 | 7 | 1 | 0.26533 | 0.42702 | 148600
4305 | 6 | 180 | 8 | 1 | 0.45537 | 0.53743 | 148400
4306 | 6 | 180 | 9 | 0 | 0.6332 | 0.53829 | 148400
4307 | 6 | 180 | 10 | 0 | 0.77688 | 0.43894 | 148400
4308 | 6 | 180 | 11 | 0 | 0.86997 | 0.23964 | 148400
4309 | 6 | 180 | 12 | 0 | 0.90217 | 0.22853 | 148400
4310 | 6 | 180 | 13 | 0 | 0.86997 | 0.23 | 148400
4311 | 6 | 180 | 14 | 0 | 0.77688 | 0.23313 | 148400
4312 | 6 | 180 | 15 | 0 | 0.6332 | 0.24044 | 148400
4313 | 6 | 180 | 16 | 0 | 0.45537 | 0.20272 | 148400
4314 | 6 | 180 | 17 | 0 | 0.26533 | 0.26079 | 148400
4315 | 6 | 180 | 18 | 0 | 0.091621 | 0.31883 | 148400
4316 | 6 | 180 | 19 | 1 | 0 | 0.36129 | 148200
4317 | 6 | 180 | 20 | 1 | 0 | 0.40046 | 148000
4318 | 6 | 180 | 21 | 0 | 0 | 0.38432 | 148000
4319 | 6 | 180 | 22 | 0 | 0 | 0.37562 | 148000
4320 | 6 | 180 | 23 | 0 | 0 | 0.50849 | 148000
4321 | 6 | 181 | 0 | 0 | 0 | 0.46984 | 148000
4322 | 6 | 181 | 1 | 0 | 0 | 0.41995 | 148000
4323 | 6 | 181 | 2 | 0 | 0 | 0.43393 | 148000
4324 | 6 | 181 | 3 | 0 | 0 | 0.29149 | 148000
4325 | 6 | 181 | 4 | 0 | 0 | 0.22933 | 148000
4326 | 6 | 181 | 5 | 0 | 0 | 0.23697 | 148000
4327 | 6 | 181 | 6 | 0 | 0.10303 | 0.30496 | 148000
4328 | 6 | 181 | 7 | 1 | 0.29838 | 0.3296 | 147800
4329 | 6 | 181 | 8 | 1 | 0.51208 | 0.41528 | 147600
4330 | 6 | 181 | 9 | 0 | 0.71207 | 0.41728 | 147600
4331 | 6 | 181 | 10 | 0 | 0.87365 | 0.42818 | 147600
4332 | 6 | 181 | 11 | 0 | 0.97833 | 0.375 | 147600
4333 | 6 | 181 | 12 | 0 | 1 | 0.33691 | 147600
4334 | 6 | 181 | 13 | 0 | 0.97833 | 0.45327 | 147600
4335 | 6 | 181 | 14 | 0 | 0.87365 | 0.43727 | 147600
4336 | 6 | 181 | 15 | 0 | 0.71207 | 0.59195 | 147600
4337 | 6 | 181 | 16 | 0 | 0.51208 | 0.39083 | 147600
4338 | 6 | 181 | 17 | 0 | 0.29838 | 0.50445 | 147600
4339 | 6 | 181 | 18 | 0 | 0.10303 | 0.46299 | 147600
4340 | 6 | 181 | 19 | 1 | 0 | 0.35472 | 147400
4341 | 6 | 181 | 20 | 1 | 0 | 0.34235 | 147200
4342 | 6 | 181 | 21 | 0 | 0 | 0.30698 | 147200
4343 | 6 | 181 | 22 | 0 | 0 | 0.32777 | 147200
4344 | 6 | 181 | 23 | 0 | 0 | 0.3034 | 147200
4345 | 7 | 182 | 0 | 0 | 0 | 0.24816 | 147200
4346 | 7 | 182 | 1 | 0 | 0 | 0.55954 | 147200
4347 | 7 | 182 | 2 | 0 | 0 | 0.41303 | 147200
4348 | 7 | 182 | 3 | 0 | 0 | 0.61837 | 147200
4349 | 7 | 182 | 4 | 0 | 0 | 0.61809 | 147200
4350 | 7 | 182 | 5 | 0 | 0 | 0.51921 | 147200
4351 | 7 | 182 | 6 | 0 | 0.090864 | 0.5455 | 147200
4352 | 7 | 182 | 7 | 1 | 0.29218 | 0.4271 | 147000
4353 | 7 | 182 | 8 | 1 | 0.51617 | 0.46224 | 146800
4354 | 7 | 182 | 9 | 0 | 0.72736 | 0.52166 | 146800
4355 | 7 | 182 | 10 | 0 | 0.89871 | 0.52235 | 146800
4356 | 7 | 182 | 11 | 0 | 1 | 0.85925 | 146800
4357 | 7 | 182 | 12 | 0 | 1 | 1 | 146800
4358 | 7 | 182 | 13 | 0 | 1 | 0.86054 | 146800
4359 | 7 | 182 | 14 | 0 | 0.89871 | 0.77294 | 146800
4360 | 7 | 182 | 15 | 0 | 0.72736 | 1 | 146800
4361 | 7 | 182 | 16 | 0 | 0.51617 | 1 | 146800
4362 | 7 | 182 | 17 | 0 | 0.29218 | 0.72394 | 146800
4363 | 7 | 182 | 18 | 0 | 0.090864 | 0.37476 | 146800
4364 | 7 | 182 | 19 | 1 | 0 | 0.45118 | 146600
4365 | 7 | 182 | 20 | 1 | 0 | 0.39297 | 146400
4366 | 7 | 182 | 21 | 0 | 0 | 0.45848 | 146400
4367 | 7 | 182 | 22 | 0 | 0 | 0.56626 | 146400
4368 | 7 | 182 | 23 | 0 | 0 | 0.83055 | 146400
4369 | 7 | 183 | 0 | 0 | 0 | 0.62925 | 146400
4370 | 7 | 183 | 1 | 0 | 0 | 0.56772 | 146400
4371 | 7 | 183 | 2 | 0 | 0 | 0.61702 | 146400
4372 | 7 | 183 | 3 | 0 | 0 | 0.60645 | 146400
4373 | 7 | 183 | 4 | 0 | 0 | 0.68412 | 146400
4374 | 7 | 183 | 5 | 0 | 0 | 0.80032 | 146400
4375 | 7 | 183 | 6 | 0 | 0.079412 | 0.60041 | 146400
4376 | 7 | 183 | 7 | 1 | 0.25535 | 1 | 146200
4377 | 7 | 183 | 8 | 1 | 0.45112 | 0.83111 | 146000
4378 | 7 | 183 | 9 | 0 | 0.63569 | 0.97109 | 146000
4379 | 7 | 183 | 10 | 0 | 0.78544 | 0.96207 | 146000
4380 | 7 | 183 | 11 | 0 | 0.8827 | 0.57918 | 146000
4381 | 7 | 183 | 12 | 0 | 0.91639 | 0.45855 | 146000
4382 | 7 | 183 | 13 | 0 | 0.8827 | 0.47506 | 146000
4383 | 7 | 183 | 14 | 0 | 0.78544 | 0.54357 | 146000
4384 | 7 | 183 | 15 | 0 | 0.63569 | 0.70028 | 146000
4385 | 7 | 183 | 16 | 0 | 0.45112 | 0.55027 | 146000
4386 | 7 | 183 | 17 | 0 | 0.25535 | 0.59805 | 146000
4387 | 7 | 183 | 18 | 0 | 0.079412 | 0.51503 | 146000
4388 | 7 | 183 | 19 | 1 | 0 | 0.71488 | 145800
4389 | 7 | 183 | 20 | 1 | 0 | 1 | 145600
4390 | 7 | 183 | 21 | 0 | 0 | 1 | 145600
4391 | 7 | 183 | 22 | 0 | 0 | 1 | 145600
4392 | 7 | 183 | 23 | 0 | 0 | 1 | 145600
4393 | 7 | 184 | 0 | 0 | 0 | 0.71994 | 145600
4394 | 7 | 184 | 1 | 0 | 0 | 0.8425 | 145600
4395 | 7 | 184 | 2 | 0 | 0 | 0.58196 | 145600
4396 | 7 | 184 | 3 | 0 | 0 | 0.49525 | 145600
4397 | 7 | 184 | 4 | 0 | 0 | 0.54873 | 145600
4398 | 7 | 184 | 5 | 0 | 0 | 0.57516 | 145600
4399 | 7 | 184 | 6 | 0 | 0.08655 | 0.62141 | 145600
4400 | 7 | 184 | 7 | 1 | 0.2783 | 0.72834 | 145400
4401 | 7 | 184 | 8 | 1 | 0.49166 | 0.71689 | 145200
4402 | 7 | 184 | 9 | 0 | 0.69282 | 0.81084 | 145200
4403 | 7 | 184 | 10 | 0 | 0.85604 | 0.99015 | 145200
4404 | 7 | 184 | 11 | 0 | 0.96204 | 0.7981 | 145200
4405 | 7 | 184 | 12 | 0 | 0.99875 | 0.93528 | 145200
4406 | 7 | 184 | 13 | 0 | 0.96204 | 0.49658 | 145200
4407 | 7 | 184 | 14 | 0 | 0.85604 | 0.28293 | 145200
4408 | 7 | 184 | 15 | 0 | 0.69282 | 0.31154 | 145200
4409 | 7 | 184 | 16 | 0 | 0.49166 | 0.3165 | 145200
4410 | 7 | 184 | 17 | 0 | 0.2783 | 0.33234 | 145200
4411 | 7 | 184 | 18 | 0 | 0.08655 | 0.41789 | 145200
4412 | 7 | 184 | 19 | 1 | 0 | 0.4766 | 145000
4413 | 7 | 184 | 20 | 1 | 0 | 0.30958 | 144800
4414 | 7 | 184 | 21 | 0 | 0 | 0.35362 | 144800
4415 | 7 | 184 | 22 | 0 | 0 | 0.24843 | 144800
4416 | 7 | 184 | 23 | 0 | 0 | 0.33856 | 144800
4417 | 7 | 185 | 0 | 0 | 0 | 0.39281 | 144800
4418 | 7 | 185 | 1 | 0 | 0 | 0.43326 | 144800
4419 | 7 | 185 | 2 | 0 | 0 | 0.39738 | 144800
4420 | 7 | 185 | 3 | 0 | 0 | 0.36979 | 144800
4421 | 7 | 185 | 4 | 0 | 0 | 0.49584 | 144800
4422 | 7 | 185 | 5 | 0 | 0 | 0.43194 | 144800
4423 | 7 | 185 | 6 | 0 | 0.060595 | 0.44788 | 144800
4424 | 7 | 185 | 7 | 1 | 0.19485 | 0.49348 | 144600
4425 | 7 | 185 | 8 | 1 | 0.34422 | 0.35844 | 144400
4426 | 7 | 185 | 9 | 0 | 0.48506 | 0.37473 | 144400
4427 | 7 | 185 | 10 | 0 | 0.59933 | 0.27925 | 144400
4428 | 7 | 185 | 11 | 0 | 0.67354 | 0.31265 | 144400
4429 | 7 | 185 | 12 | 0 | 0.69925 | 0.26358 | 144400
4430 | 7 | 185 | 13 | 0 | 0.67354 | 0.54511 | 144400
4431 | 7 | 185 | 14 | 0 | 0.59933 | 0.60191 | 144400
4432 | 7 | 185 | 15 | 0 | 0.48506 | 0.71165 | 144400
4433 | 7 | 185 | 16 | 0 | 0.34422 | 0.50814 | 144400
4434 | 7 | 185 | 17 | 0 | 0.19485 | 0.61029 | 144400
4435 | 7 | 185 | 18 | 0 | 0.060595 | 0.39267 | 144400
4436 | 7 | 185 | 19 | 1 | 0 | 0.33483 | 144200
4437 | 7 | 185 | 20 | 1 | 0 | 0.43817 | 144000
4438 | 7 | 185 | 21 | 0 | 0 | 0.44176 | 144000
4439 | 7 | 185 | 22 | 0 | 0 | 0.35358 | 144000
4440 | 7 | 185 | 23 | 0 | 0 | 0.34072 | 144000
4441 | 7 | 186 | 0 | 0 | 0 | 0.29507 | 144000
4442 | 7 | 186 | 1 | 0 | 0 | 0.33325 | 144000
4443 | 7 | 186 | 2 | 0 | 0 | 0.43434 | 144000
4444 | 7 | 186 | 3 | 0 | 0 | 0.25541 | 144000
4445 | 7 | 186 | 4 | 0 | 0 | 0.28972 | 144000
4446 | 7 | 186 | 5 | 0 | 0 | 0.14027 | 144000
4447 | 7 | 186 | 6 | 0 | 0.084776 | 0.18141 | 144000
4448 | 7 | 186 | 7 | 1 | 0.2726 | 0.3138 | 143800
4449 | 7 | 186 | 8 | 1 | 0.48158 | 0.2201 | 143600
4450 | 7 | 186 | 9 | 0 | 0.67862 | 0.30172 | 143600
4451 | 7 | 186 | 10 | 0 | 0.83849 | 0.24798 | 143600
4452 | 7 | 186 | 11 | 0 | 0.94232 | 0.28081 | 143600
4453 | 7 | 186 | 12 | 0 | 0.97828 | 0.27507 | 143600
4454 | 7 | 186 | 13 | 0 | 0.94232 | 0.29603 | 143600
4455 | 7 | 186 | 14 | 0 | 0.83849 | 0.29647 | 143600
4456 | 7 | 186 | 15 | 0 | 0.67862 | 0.31965 | 143600
4457 | 7 | 186 | 16 | 0 | 0.48158 | 0.33919 | 143600
4458 | 7 | 186 | 17 | 0 | 0.2726 | 0.33469 | 143600
4459 | 7 | 186 | 18 | 0 | 0.084776 | 0.44878 | 143600
4460 | 7 | 186 | 19 | 1 | 0 | 0.33608 | 143400
4461 | 7 | 186 | 20 | 1 | 0 | 0.73574 | 143200
4462 | 7 | 186 | 21 | 0 | 0 | 0.5077 | 143200
4463 | 7 | 186 | 22 | 0 | 0 | 0.38598 | 143200
4464 | 7 | 186 | 23 | 0 | 0 | 0.39944 | 143200
4465 | 7 | 187 | 0 | 0 | 0 | 0.43252 | 143200
4466 | 7 | 187 | 1 | 0 | 0 | 0.59329 | 143200
4467 | 7 | 187 | 2 | 0 | 0 | 0.61738 | 143200
4468 | 7 | 187 | 3 | 0 | 0 | 0.55699 | 143200
4469 | 7 | 187 | 4 | 0 | 0 | 0.47887 | 143200
4470 | 7 | 187 | 5 | 0 | 0 | 0.32027 | 143200
4471 | 7 | 187 | 6 | 0 | 0.09019 | 0.23177 | 143200
4472 | 7 | 187 | 7 | 1 | 0.29001 | 0.34486 | 143000
4473 | 7 | 187 | 8 | 1 | 0.51234 | 0.30817 | 142800
4474 | 7 | 187 | 9 | 0 | 0.72196 | 0.46713 | 142800
4475 | 7 | 187 | 10 | 0 | 0.89204 | 0.42321 | 142800
4476 | 7 | 187 | 11 | 0 | 1 | 0.29477 | 142800
4477 | 7 | 187 | 12 | 0 | 1 | 0.40906 | 142800
4478 | 7 | 187 | 13 | 0 | 1 | 0.35033 | 142800
4479 | 7 | 187 | 14 | 0 | 0.89204 | 0.39024 | 142800
4480 | 7 | 187 | 15 | 0 | 0.72196 | 0.32548 | 142800
4481 | 7 | 187 | 16 | 0 | 0.51234 | 0.27481 | 142800
4482 | 7 | 187 | 17 | 0 | 0.29001 | 0.24051 | 142800
4483 | 7 | 187 | 18 | 0 | 0.09019 | 0.37877 | 142800
4484 | 7 | 187 | 19 | 1 | 0 | 0.48841 | 142600
4485 | 7 | 187 | 20 | 1 | 0 | 0.31031 | 142400
4486 | 7 | 187 | 21 | 0 | 0 | 0.47096 | 142400
4487 | 7 | 187 | 22 | 0 | 0 | 0.40126 | 142400
4488 | 7 | 187 | 23 | 0 | 0 | 0.4054 | 142400
4489 | 7 | 188 | 0 | 0 | 0 | 0.44366 | 142400
4490 | 7 | 188 | 1 | 0 | 0 | 0.46298 | 142400
4491 | 7 | 188 | 2 | 0 | 0 | 0.59879 | 142400
4492 | 7 | 188 | 3 | 0 | 0 | 0.45813 | 142400
4493 | 7 | 188 | 4 | 0 | 0 | 0.34594 | 142400
4494 | 7 | 188 | 5 | 0 | 0 | 0.3543 | 142400
4495 | 7 | 188 | 6 | 0 | 0.078194 | 0.33252 | 142400
4496 | 7 | 188 | 7 | 1 | 0.25143 | 0.34194 | 142200
4497 | 7 | 188 | 8 | 1 | 0.44419 | 0.45388 | 142000
4498 | 7 | 188 | 9 | 0 | 0.62593 | 0.42704 | 142000
4499 | 7 | 188 | 10 | 0 | 0.77339 | 0.36405 | 142000
4500 | 7 | 188 | 11 | 0 | 0.86916 | 0.5174 | 142000
4501 | 7 | 188 | 12 | 0 | 0.90232 | 0.7794 | 142000
4502 | 7 | 188 | 13 | 0 | 0.86916 | 0.97236 | 142000
4503 | 7 | 188 | 14 | 0 | 0.77339 | 1 | 142000
4504 | 7 | 188 | 15 | 0 | 0.62593 | 0.98642 | 142000
4505 | 7 | 188 | 16 | 0 | 0.44419 | 0.74708 | 142000
4506 | 7 | 188 | 17 | 0 | 0.25143 | 0.9215 | 142000
4507 | 7 | 188 | 18 | 0 | 0.078194 | 1 | 142000
4508 | 7 | 188 | 19 | 1 | 0 | 1 | 141800
4509 | 7 | 188 | 20 | 1 | 0 | 1 | 141600
4510 | 7 | 188 | 21 | 0 | 0 | 1 | 141600
4511 | 7 | 188 | 22 | 0 | 0 | 1 | 141600
4512 | 7 | 188 | 23 | 0 | 0 | 1 | 141600
4513 | 7 | 189 | 0 | 0 | 0 | 1 | 141600
4514 | 7 | 189 | 1 | 0 | 0 | 0.92504 | 141600
4515 | 7 | 189 | 2 | 0 | 0 | 0.69621 | 141600
4516 | 7 | 189 | 3 | 0 | 0 | 0.70658 | 141600
4517 | 7 | 189 | 4 | 0 | 0 | 0.62501 | 141600
4518 | 7 | 189 | 5 | 0 | 0 | 0.75204 | 141600
4519 | 7 | 189 | 6 | 0 | 0.079391 | 0.85384 | 141600
4520 | 7 | 189 | 7 | 1 | 0.25528 | 0.61244 | 141400
4521 | 7 | 189 | 8 | 1 | 0.451 | 0.68727 | 141200
4522 | 7 | 189 | 9 | 0 | 0.63552 | 0.63116 | 141200
4523 | 7 | 189 | 10 | 0 | 0.78524 | 0.70504 | 141200
4524 | 7 | 189 | 11 | 0 | 0.88247 | 0.50214 | 141200
4525 | 7 | 189 | 12 | 0 | 0.91614 | 0.5852 | 141200
4526 | 7 | 189 | 13 | 0 | 0.88247 | 0.71539 | 141200
4527 | 7 | 189 | 14 | 0 | 0.78524 | 0.61043 | 141200
4528 | 7 | 189 | 15 | 0 | 0.63552 | 0.92412 | 141200
4529 | 7 | 189 | 16 | 0 | 0.451 | 0.9978 | 141200
4530 | 7 | 189 | 17 | 0 | 0.25528 | 0.55535 | 141200
4531 | 7 | 189 | 18 | 0 | 0.079391 | 0.40542 | 141200
4532 | 7 | 189 | 19 | 1 | 0 | 0.56037 | 141000
4533 | 7 | 189 | 20 | 1 | 0 | 0.48015 | 140800
4534 | 7 | 189 | 21 | 0 | 0 | 0.49996 | 140800
4535 | 7 | 189 | 22 | 0 | 0 | 0.45345 | 140800
4536 | 7 | 189 | 23 | 0 | 0 | 0.36225 | 140800
4537 | 7 | 190 | 0 | 0 | 0 | 0.39829 | 140800
4538 | 7 | 190 | 1 | 0 | 0 | 0.46987 | 140800
4539 | 7 | 190 | 2 | 0 | 0 | 0.60325 | 140800
4540 | 7 | 190 | 3 | 0 | 0 | 0.54632 | 140800
4541 | 7 | 190 | 4 | 0 | 0 | 0.70964 | 140800
4542 | 7 | 190 | 5 | 0 | 0 | 0.5465 | 140800
4543 | 7 | 190 | 6 | 0 | 0.069602 | 0.46716 | 140800
4544 | 7 | 190 | 7 | 1 | 0.22381 | 0.57137 | 140600
4545 | 7 | 190 | 8 | 1 | 0.39539 | 0.43375 | 140400
4546 | 7 | 190 | 9 | 0 | 0.55716 | 0.48616 | 140400
4547 | 7 | 190 | 10 | 0 | 0.68842 | 0.489 | 140400
4548 | 7 | 190 | 11 | 0 | 0.77366 | 0.52367 | 140400
4549 | 7 | 190 | 12 | 0 | 0.80318 | 0.54663 | 140400
4550 | 7 | 190 | 13 | 0 | 0.77366 | 0.45579 | 140400
4551 | 7 | 190 | 14 | 0 | 0.68842 | 0.44221 | 140400
4552 | 7 | 190 | 15 | 0 | 0.55716 | 0.45699 | 140400
4553 | 7 | 190 | 16 | 0 | 0.39539 | 0.39342 | 140400
4554 | 7 | 190 | 17 | 0 | 0.22381 | 0.42212 | 140400
4555 | 7 | 190 | 18 | 0 | 0.069602 | 0.32873 | 140400
4556 | 7 | 190 | 19 | 1 | 0 | 0.47028 | 140200
4557 | 7 | 190 | 20 | 1 | 0 | 0.35508 | 140000
4558 | 7 | 190 | 21 | 0 | 0 | 0.28501 | 140000
4559 | 7 | 190 | 22 | 0 | 0 | 0.30255 | 140000
4560 | 7 | 190 | 23 | 0 | 0 | 0.29181 | 140000
4561 | 7 | 191 | 0 | 0 | 0 | 0.3224 | 140000
4562 | 7 | 191 | 1 | 0 | 0 | 0.37493 | 140000
4563 | 7 | 191 | 2 | 0 | 0 | 0.30758 | 140000
4564 | 7 | 191 | 3 | 0 | 0 | 0.35054 | 140000
4565 | 7 | 191 | 4 | 0 | 0 | 0.39815 | 140000
4566 | 7 | 191 | 5 | 0 | 0 | 0.30741 | 140000
4567 | 7 | 191 | 6 | 0 | 0.088652 | 0.30993 | 140000
4568 | 7 | 191 | 7 | 1 | 0.28506 | 0.21426 | 139800
4569 | 7 | 191 | 8 | 1 | 0.5036 | 0.24346 | 139600
4570 | 7 | 191 | 9 | 0 | 0.70965 | 0.26867 | 139600
4571 | 7 | 191 | 10 | 0 | 0.87683 | 0.21824 | 139600
4572 | 7 | 191 | 11 | 0 | 0.98541 | 0.4187 | 139600
4573 | 7 | 191 | 12 | 0 | 1 | 0.52046 | 139600
4574 | 7 | 191 | 13 | 0 | 0.98541 | 0.40405 | 139600
4575 | 7 | 191 | 14 | 0 | 0.87683 | 0.35777 | 139600
4576 | 7 | 191 | 15 | 0 | 0.70965 | 0.27033 | 139600
4577 | 7 | 191 | 16 | 0 | 0.5036 | 0.32146 | 139600
4578 | 7 | 191 | 17 | 0 | 0.28506 | 0.22369 | 139600
4579 | 7 | 191 | 18 | 0 | 0.088652 | 0.18743 | 139600
4580 | 7 | 191 | 19 | 1 | 0 | 0.11757 | 139400
4581 | 7 | 191 | 20 | 1 | 0 | 0.065437 | 139200
4582 | 7 | 191 | 21 | 0 | 0 | 0.060251 | 139200
4583 | 7 | 191 | 22 | 0 | 0 | 0.059213 | 139200
4584 | 7 | 191 | 23 | 0 | 0 | 0.060676 | 139200
4585 | 7 | 192 | 0 | 0 | 0 | 0.074749 | 139200
4586 | 7 | 192 | 1 | 0 | 0 | 0.065094 | 139200
4587 | 7 | 192 | 2 | 0 | 0 | 0.10242 | 139200
4588 | 7 | 192 | 3 | 0 | 0 | 0.16822 | 139200
4589 | 7 | 192 | 4 | 0 | 0 | 0.20011 | 139200
4590 | 7 | 192 | 5 | 0 | 0 | 0.17777 | 139200
4591 | 7 | 192 | 6 | 0 | 0.088116 | 0.36012 | 139200
4592 | 7 | 192 | 7 | 1 | 0.28334 | 0.36459 | 139000
4593 | 7 | 192 | 8 | 1 | 0.50056 | 0.47825 | 138800
4594 | 7 | 192 | 9 | 0 | 0.70536 | 0.49049 | 138800
4595 | 7 | 192 | 10 | 0 | 0.87153 | 0.32009 | 138800
4596 | 7 | 192 | 11 | 0 | 0.97945 | 0.44192 | 138800
4597 | 7 | 192 | 12 | 0 | 1 | 0.3134 | 138800
4598 | 7 | 192 | 13 | 0 | 0.97945 | 0.5677 | 138800
4599 | 7 | 192 | 14 | 0 | 0.87153 | 0.52697 | 138800
4600 | 7 | 192 | 15 | 0 | 0.70536 | 0.61215 | 138800
4601 | 7 | 192 | 16 | 0 | 0.50056 | 0.82096 | 138800
4602 | 7 | 192 | 17 | 0 | 0.28334 | 0.86238 | 138800
4603 | 7 | 192 | 18 | 0 | 0.088116 | 0.71015 | 138800
4604 | 7 | 192 | 19 | 1 | 0 | 1 | 138600
4605 | 7 | 192 | 20 | 1 | 0 | 0.87819 | 138400
4606 | 7 | 192 | 21 | 0 | 0 | 0.51688 | 138400
4607 | 7 | 192 | 22 | 0 | 0 | 0.37075 | 138400
4608 | 7 | 192 | 23 | 0 | 0 | 0.22916 | 138400
4609 | 7 | 193 | 0 | 0 | 0 | 0.27743 | 138400
4610 | 7 | 193 | 1 | 0 | 0 | 0.28213 | 138400
4611 | 7 | 193 | 2 | 0 | 0 | 0.28232 | 138400
4612 | 7 | 193 | 3 | 0 | 0 | 0.26915 | 138400
4613 | 7 | 193 | 4 | 0 | 0 | 0.27098 | 138400
4614 | 7 | 193 | 5 | 0 | 0 | 0.48908 | 138400
4615 | 7 | 193 | 6 | 0 | 0.073823 | 0.51187 | 138400
4616 | 7 | 193 | 7 | 1 | 0.23738 | 0.59368 | 138200
4617 | 7 | 193 | 8 | 1 | 0.41936 | 0.73406 | 138000
4618 | 7 | 193 | 9 | 0 | 0.59095 | 1 | 138000
4619 | 7 | 193 | 10 | 0 | 0.73016 | 1 | 138000
4620 | 7 | 193 | 11 | 0 | 0.82057 | 1 | 138000
4621 | 7 | 193 | 12 | 0 | 0.85189 | 1 | 138000
4622 | 7 | 193 | 13 | 0 | 0.82057 | 1 | 138000
4623 | 7 | 193 | 14 | 0 | 0.73016 | 1 | 138000
4624 | 7 | 193 | 15 | 0 | 0.59095 | 1 | 138000
4625 | 7 | 193 | 16 | 0 | 0.41936 | 1 | 138000
4626 | 7 | 193 | 17 | 0 | 0.23738 | 1 | 138000
4627 | 7 | 193 | 18 | 0 | 0.073823 | 1 | 138000
4628 | 7 | 193 | 19 | 1 | 0 | 1 | 137800
4629 | 7 | 193 | 20 | 1 | 0 | 1 | 137600
4630 | 7 | 193 | 21 | 0 | 0 | 1 | 137600
4631 | 7 | 193 | 22 | 0 | 0 | 0.91604 | 137600
4632 | 7 | 193 | 23 | 0 | 0 | 0.55761 | 137600
4633 | 7 | 194 | 0 | 0 | 0 | 0.50067 | 137600
4634 | 7 | 194 | 1 | 0 | 0 | 0.71611 | 137600
4635 | 7 | 194 | 2 | 0 | 0 | 0.66762 | 137600
4636 | 7 | 194 | 3 | 0 | 0 | 0.55694 | 137600
4637 | 7 | 194 | 4 | 0 | 0 | 0.50664 | 137600
4638 | 7 | 194 | 5 | 0 | 0 | 0.52592 | 137600
4639 | 7 | 194 | 6 | 0 | 0.07795 | 0.39334 | 137600
4640 | 7 | 194 | 7 | 1 | 0.25065 | 0.58052 | 137400
4641 | 7 | 194 | 8 | 1 | 0.44281 | 0.78359 | 137200
4642 | 7 | 194 | 9 | 0 | 0.62398 | 0.6489 | 137200
4643 | 7 | 194 | 10 | 0 | 0.77098 | 0.76825 | 137200
4644 | 7 | 194 | 11 | 0 | 0.86645 | 0.78058 | 137200
4645 | 7 | 194 | 12 | 0 | 0.89951 | 0.8834 | 137200
4646 | 7 | 194 | 13 | 0 | 0.86645 | 0.52468 | 137200
4647 | 7 | 194 | 14 | 0 | 0.77098 | 0.5554 | 137200
4648 | 7 | 194 | 15 | 0 | 0.62398 | 0.52583 | 137200
4649 | 7 | 194 | 16 | 0 | 0.44281 | 0.58923 | 137200
4650 | 7 | 194 | 17 | 0 | 0.25065 | 0.4884 | 137200
4651 | 7 | 194 | 18 | 0 | 0.07795 | 0.61303 | 137200
4652 | 7 | 194 | 19 | 1 | 0 | 0.5899 | 137000
4653 | 7 | 194 | 20 | 1 | 0 | 0.54199 | 136800
4654 | 7 | 194 | 21 | 0 | 0 | 1 | 136800
4655 | 7 | 194 | 22 | 0 | 0 | 1 | 136800
4656 | 7 | 194 | 23 | 0 | 0 | 1 | 136800
4657 | 7 | 195 | 0 | 0 | 0 | 0.70329 | 136800
4658 | 7 | 195 | 1 | 0 | 0 | 0.98849 | 136800
4659 | 7 | 195 | 2 | 0 | 0 | 1 | 136800
4660 | 7 | 195 | 3 | 0 | 0 | 1 | 136800
4661 | 7 | 195 | 4 | 0 | 0 | 1 | 136800
4662 | 7 | 195 | 5 | 0 | 0 | 1 | 136800
4663 | 7 | 195 | 6 | 0 | 0.079687 | 1 | 136800
4664 | 7 | 195 | 7 | 1 | 0.25624 | 1 | 136600
4665 | 7 | 195 | 8 | 1 | 0.45268 | 1 | 136400
4666 | 7 | 195 | 9 | 0 | 0.63789 | 1 | 136400
4667 | 7 | 195 | 10 | 0 | 0.78817 | 1 | 136400
4668 | 7 | 195 | 11 | 0 | 0.88576 | 1 | 136400
4669 | 7 | 195 | 12 | 0 | 0.91956 | 1 | 136400
4670 | 7 | 195 | 13 | 0 | 0.88576 | 1 | 136400
4671 | 7 | 195 | 14 | 0 | 0.78817 | 1 | 136400
4672 | 7 | 195 | 15 | 0 | 0.63789 | 1 | 136400
4673 | 7 | 195 | 16 | 0 | 0.45268 | 1 | 136400
4674 | 7 | 195 | 17 | 0 | 0.25624 | 0.83528 | 136400
4675 | 7 | 195 | 18 | 0 | 0.079687 | 0.5987 | 136400
4676 | 7 | 195 | 19 | 1 | 0 | 0.61614 | 136200
4677 | 7 | 195 | 20 | 1 | 0 | 0.75962 | 136000
4678 | 7 | 195 | 21 | 0 | 0 | 0.57396 | 136000
4679 | 7 | 195 | 22 | 0 | 0 | 0.55975 | 136000
4680 | 7 | 195 | 23 | 0 | 0 | 0.57021 | 136000
4681 | 7 | 196 | 0 | 0 | 0 | 0.47202 | 136000
4682 | 7 | 196 | 1 | 0 | 0 | 0.59879 | 136000
4683 | 7 | 196 | 2 | 0 | 0 | 0.48168 | 136000
4684 | 7 | 196 | 3 | 0 | 0 | 0.29305 | 136000
4685 | 7 | 196 | 4 | 0 | 0 | 0.30223 | 136000
4686 | 7 | 196 | 5 | 0 | 0 | 0.34563 | 136000
4687 | 7 | 196 | 6 | 0 | 0.077594 | 0.40106 | 136000
4688 | 7 | 196 | 7 | 1 | 0.24951 | 0.46142 | 135800
4689 | 7 | 196 | 8 | 1 | 0.44079 | 0.33563 | 135600
4690 | 7 | 196 | 9 | 0 | 0.62114 | 0.45108 | 135600
4691 | 7 | 196 | 10 | 0 | 0.76747 | 0.38667 | 135600
4692 | 7 | 196 | 11 | 0 | 0.8625 | 0.27899 | 135600
4693 | 7 | 196 | 12 | 0 | 0.89541 | 0.17601 | 135600
4694 | 7 | 196 | 13 | 0 | 0.8625 | 0.15725 | 135600
4695 | 7 | 196 | 14 | 0 | 0.76747 | 0.21775 | 135600
4696 | 7 | 196 | 15 | 0 | 0.62114 | 0.19391 | 135600
4697 | 7 | 196 | 16 | 0 | 0.44079 | 0.24261 | 135600
4698 | 7 | 196 | 17 | 0 | 0.24951 | 0.24709 | 135600
4699 | 7 | 196 | 18 | 0 | 0.077594 | 0.20579 | 135600
4700 | 7 | 196 | 19 | 1 | 0 | 0.19147 | 135400
4701 | 7 | 196 | 20 | 1 | 0 | 0.20744 | 135200
4702 | 7 | 196 | 21 | 0 | 0 | 0.16357 | 135200
4703 | 7 | 196 | 22 | 0 | 0 | 0.17816 | 135200
4704 | 7 | 196 | 23 | 0 | 0 | 0.15319 | 135200
4705 | 7 | 197 | 0 | 0 | 0 | 0.15986 | 135200
4706 | 7 | 197 | 1 | 0 | 0 | 0.23674 | 135200
4707 | 7 | 197 | 2 | 0 | 0 | 0.33241 | 135200
4708 | 7 | 197 | 3 | 0 | 0 | 0.36574 | 135200
4709 | 7 | 197 | 4 | 0 | 0 | 0.35049 | 135200
4710 | 7 | 197 | 5 | 0 | 0 | 0.24876 | 135200
4711 | 7 | 197 | 6 | 0 | 0.077198 | 0.29591 | 135200
4712 | 7 | 197 | 7 | 1 | 0.24823 | 0.28947 | 135000
4713 | 7 | 197 | 8 | 1 | 0.43854 | 0.42257 | 134800
4714 | 7 | 197 | 9 | 0 | 0.61797 | 0.30212 | 134800
4715 | 7 | 197 | 10 | 0 | 0.76355 | 0.24224 | 134800
4716 | 7 | 197 | 11 | 0 | 0.8581 | 0.2678 | 134800
4717 | 7 | 197 | 12 | 0 | 0.89084 | 0.2945 | 134800
4718 | 7 | 197 | 13 | 0 | 0.8581 | 0.32878 | 134800
4719 | 7 | 197 | 14 | 0 | 0.76355 | 0.51904 | 134800
4720 | 7 | 197 | 15 | 0 | 0.61797 | 0.31808 | 134800
4721 | 7 | 197 | 16 | 0 | 0.43854 | 0.32787 | 134800
4722 | 7 | 197 | 17 | 0 | 0.24823 | 0.2846 | 134800
4723 | 7 | 197 | 18 | 0 | 0.077198 | 0.35198 | 134800
4724 | 7 | 197 | 19 | 1 | 0 | 0.35815 | 134600
4725 | 7 | 197 | 20 | 1 | 0 | 0.45682 | 134400
4726 | 7 | 197 | 21 | 0 | 0 | 0.55668 | 134400
4727 | 7 | 197 | 22 | 0 | 0 | 0.51119 | 134400
4728 | 7 | 197 | 23 | 0 | 0 | 0.49954 | 134400
4729 | 7 | 198 | 0 | 0 | 0 | 0.69939 | 134400
4730 | 7 | 198 | 1 | 0 | 0 | 0.70535 | 134400
4731 | 7 | 198 | 2 | 0 | 0 | 0.69083 | 134400
4732 | 7 | 198 | 3 | 0 | 0 | 0.74418 | 134400
4733 | 7 | 198 | 4 | 0 | 0 | 0.78439 | 134400
4734 | 7 | 198 | 5 | 0 | 0 | 0.65154 | 134400
4735 | 7 | 198 | 6 | 0 | 0.068535 | 0.79458 | 134400
4736 | 7 | 198 | 7 | 1 | 0.22038 | 1 | 134200
4737 | 7 | 198 | 8 | 1 | 0.38933 | 1 | 134000
4738 | 7 | 198 | 9 | 0 | 0.54862 | 1 | 134000
4739 | 7 | 198 | 10 | 0 | 0.67787 | 1 | 134000
4740 | 7 | 198 | 11 | 0 | 0.7618 | 1 | 134000
4741 | 7 | 198 | 12 | 0 | 0.79087 | 1 | 134000
4742 | 7 | 198 | 13 | 0 | 0.7618 | 1 | 134000
4743 | 7 | 198 | 14 | 0 | 0.67787 | 1 | 134000
4744 | 7 | 198 | 15 | 0 | 0.54862 | 1 | 134000
4745 | 7 | 198 | 16 | 0 | 0.38933 | 1 | 134000
4746 | 7 | 198 | 17 | 0 | 0.22038 | 1 | 134000
4747 | 7 | 198 | 18 | 0 | 0.068535 | 1 | 134000
4748 | 7 | 198 | 19 | 1 | 0 | 1 | 133800
4749 | 7 | 198 | 20 | 1 | 0 | 1 | 133600
4750 | 7 | 198 | 21 | 0 | 0 | 1 | 133600
4751 | 7 | 198 | 22 | 0 | 0 | 1 | 133600
4752 | 7 | 198 | 23 | 0 | 0 | 1 | 133600
4753 | 7 | 199 | 0 | 0 | 0 | 1 | 133600
4754 | 7 | 199 | 1 | 0 | 0 | 1 | 133600
4755 | 7 | 199 | 2 | 0 | 0 | 1 | 133600
4756 | 7 | 199 | 3 | 0 | 0 | 1 | 133600
4757 | 7 | 199 | 4 | 0 | 0 | 1 | 133600
4758 | 7 | 199 | 5 | 0 | 0 | 1 | 133600
4759 | 7 | 199 | 6 | 0 | 0.079369 | 1 | 133600
4760 | 7 | 199 | 7 | 1 | 0.25521 | 1 | 133400
4761 | 7 | 199 | 8 | 1 | 0.45087 | 1 | 133200
4762 | 7 | 199 | 9 | 0 | 0.63535 | 1 | 133200
4763 | 7 | 199 | 10 | 0 | 0.78502 | 1 | 133200
4764 | 7 | 199 | 11 | 0 | 0.88223 | 1 | 133200
4765 | 7 | 199 | 12 | 0 | 0.91589 | 1 | 133200
4766 | 7 | 199 | 13 | 0 | 0.88223 | 1 | 133200
4767 | 7 | 199 | 14 | 0 | 0.78502 | 1 | 133200
4768 | 7 | 199 | 15 | 0 | 0.63535 | 1 | 133200
4769 | 7 | 199 | 16 | 0 | 0.45087 | 0.96955 | 133200
4770 | 7 | 199 | 17 | 0 | 0.25521 | 1 | 133200
4771 | 7 | 199 | 18 | 0 | 0.079369 | 1 | 133200
4772 | 7 | 199 | 19 | 1 | 0 | 0.99422 | 133000
4773 | 7 | 199 | 20 | 1 | 0 | 0.84647 | 132800
4774 | 7 | 199 | 21 | 0 | 0 | 0.88798 | 132800
4775 | 7 | 199 | 22 | 0 | 0 | 1 | 132800
4776 | 7 | 199 | 23 | 0 | 0 | 1 | 132800
4777 | 7 | 200 | 0 | 0 | 0 | 1 | 132800
4778 | 7 | 200 | 1 | 0 | 0 | 1 | 132800
4779 | 7 | 200 | 2 | 0 | 0 | 1 | 132800
4780 | 7 | 200 | 3 | 0 | 0 | 1 | 132800
4781 | 7 | 200 | 4 | 0 | 0 | 1 | 132800
4782 | 7 | 200 | 5 | 0 | 0 | 1 | 132800
4783 | 7 | 200 | 6 | 0 | 0.07723 | 1 | 132800
4784 | 7 | 200 | 7 | 1 | 0.24833 | 1 | 132600
4785 | 7 | 200 | 8 | 1 | 0.43872 | 1 | 132400
4786 | 7 | 200 | 9 | 0 | 0.61822 | 1 | 132400
4787 | 7 | 200 | 10 | 0 | 0.76386 | 1 | 132400
4788 | 7 | 200 | 11 | 0 | 0.85844 | 1 | 132400
4789 | 7 | 200 | 12 | 0 | 0.8912 | 1 | 132400
4790 | 7 | 200 | 13 | 0 | 0.85844 | 1 | 132400
4791 | 7 | 200 | 14 | 0 | 0.76386 | 1 | 132400
4792 | 7 | 200 | 15 | 0 | 0.61822 | 1 | 132400
4793 | 7 | 200 | 16 | 0 | 0.43872 | 0.99646 | 132400
4794 | 7 | 200 | 17 | 0 | 0.24833 | 0.69489 | 132400
4795 | 7 | 200 | 18 | 0 | 0.07723 | 0.47987 | 132400
4796 | 7 | 200 | 19 | 1 | 0 | 0.43797 | 132200
4797 | 7 | 200 | 20 | 1 | 0 | 0.38185 | 132000
4798 | 7 | 200 | 21 | 0 | 0 | 0.3733 | 132000
4799 | 7 | 200 | 22 | 0 | 0 | 0.35952 | 132000
4800 | 7 | 200 | 23 | 0 | 0 | 0.29058 | 132000
4801 | 7 | 201 | 0 | 0 | 0 | 0.17596 | 132000
4802 | 7 | 201 | 1 | 0 | 0 | 0.1509 | 132000
4803 | 7 | 201 | 2 | 0 | 0 | 0.16721 | 132000
4804 | 7 | 201 | 3 | 0 | 0 | 0.16935 | 132000
4805 | 7 | 201 | 4 | 0 | 0 | 0.25133 | 132000
4806 | 7 | 201 | 5 | 0 | 0 | 0.20359 | 132000
4807 | 7 | 201 | 6 | 0 | 0.077125 | 0.24981 | 132000
4808 | 7 | 201 | 7 | 1 | 0.248 | 0.39569 | 131800
4809 | 7 | 201 | 8 | 1 | 0.43812 | 0.51102 | 131600
4810 | 7 | 201 | 9 | 0 | 0.61738 | 0.75267 | 131600
4811 | 7 | 201 | 10 | 0 | 0.76282 | 0.95123 | 131600
4812 | 7 | 201 | 11 | 0 | 0.85728 | 0.81397 | 131600
4813 | 7 | 201 | 12 | 0 | 0.88999 | 0.84348 | 131600
4814 | 7 | 201 | 13 | 0 | 0.85728 | 0.91372 | 131600
4815 | 7 | 201 | 14 | 0 | 0.76282 | 0.99803 | 131600
4816 | 7 | 201 | 15 | 0 | 0.61738 | 0.67845 | 131600
4817 | 7 | 201 | 16 | 0 | 0.43812 | 0.88255 | 131600
4818 | 7 | 201 | 17 | 0 | 0.248 | 1 | 131600
4819 | 7 | 201 | 18 | 0 | 0.077125 | 1 | 131600
4820 | 7 | 201 | 19 | 1 | 0 | 0.86513 | 131400
4821 | 7 | 201 | 20 | 1 | 0 | 0.98496 | 131200
4822 | 7 | 201 | 21 | 0 | 0 | 1 | 131200
4823 | 7 | 201 | 22 | 0 | 0 | 1 | 131200
4824 | 7 | 201 | 23 | 0 | 0 | 0.70358 | 131200
4825 | 7 | 202 | 0 | 0 | 0 | 0.82778 | 131200
4826 | 7 | 202 | 1 | 0 | 0 | 0.37579 | 131200
4827 | 7 | 202 | 2 | 0 | 0 | 0.36338 | 131200
4828 | 7 | 202 | 3 | 0 | 0 | 0.34756 | 131200
4829 | 7 | 202 | 4 | 0 | 0 | 0.39287 | 131200
4830 | 7 | 202 | 5 | 0 | 0 | 0.41055 | 131200
4831 | 7 | 202 | 6 | 0 | 0.08922 | 0.76338 | 131200
4832 | 7 | 202 | 7 | 1 | 0.28689 | 0.96383 | 131000
4833 | 7 | 202 | 8 | 1 | 0.50683 | 1 | 130800
4834 | 7 | 202 | 9 | 0 | 0.7142 | 0.72742 | 130800
4835 | 7 | 202 | 10 | 0 | 0.88245 | 0.95542 | 130800
4836 | 7 | 202 | 11 | 0 | 0.99172 | 0.97755 | 130800
4837 | 7 | 202 | 12 | 0 | 1 | 0.79555 | 130800
4838 | 7 | 202 | 13 | 0 | 0.99172 | 0.65287 | 130800
4839 | 7 | 202 | 14 | 0 | 0.88245 | 0.70804 | 130800
4840 | 7 | 202 | 15 | 0 | 0.7142 | 0.43619 | 130800
4841 | 7 | 202 | 16 | 0 | 0.50683 | 0.39428 | 130800
4842 | 7 | 202 | 17 | 0 | 0.28689 | 0.4929 | 130800
4843 | 7 | 202 | 18 | 0 | 0.08922 | 0.58158 | 130800
4844 | 7 | 202 | 19 | 1 | 0 | 0.53573 | 130600
4845 | 7 | 202 | 20 | 1 | 0 | 0.37394 | 130400
4846 | 7 | 202 | 21 | 0 | 0 | 0.43931 | 130400
4847 | 7 | 202 | 22 | 0 | 0 | 0.3626 | 130400
4848 | 7 | 202 | 23 | 0 | 0 | 0.29277 | 130400
4849 | 7 | 203 | 0 | 0 | 0 | 0.27491 | 130400
4850 | 7 | 203 | 1 | 0 | 0 | 0.2275 | 130400
4851 | 7 | 203 | 2 | 0 | 0 | 0.25266 | 130400
4852 | 7 | 203 | 3 | 0 | 0 | 0.38641 | 130400
4853 | 7 | 203 | 4 | 0 | 0 | 0.20168 | 130400
4854 | 7 | 203 | 5 | 0 | 0 | 0.13661 | 130400
4855 | 7 | 203 | 6 | 0 | 0.084216 | 0.24405 | 130400
4856 | 7 | 203 | 7 | 1 | 0.2708 | 0.12169 | 130200
4857 | 7 | 203 | 8 | 1 | 0.4784 | 0.14663 | 130000
4858 | 7 | 203 | 9 | 0 | 0.67414 | 0.17801 | 130000
4859 | 7 | 203 | 10 | 0 | 0.83295 | 0.26543 | 130000
4860 | 7 | 203 | 11 | 0 | 0.9361 | 0.35621 | 130000
4861 | 7 | 203 | 12 | 0 | 0.97181 | 0.26576 | 130000
4862 | 7 | 203 | 13 | 0 | 0.9361 | 0.30048 | 130000
4863 | 7 | 203 | 14 | 0 | 0.83295 | 0.22257 | 130000
4864 | 7 | 203 | 15 | 0 | 0.67414 | 0.18643 | 130000
4865 | 7 | 203 | 16 | 0 | 0.4784 | 0.16324 | 130000
4866 | 7 | 203 | 17 | 0 | 0.2708 | 0.20464 | 130000
4867 | 7 | 203 | 18 | 0 | 0.084216 | 0.17625 | 130000
4868 | 7 | 203 | 19 | 1 | 0 | 0.17867 | 129800
4869 | 7 | 203 | 20 | 1 | 0 | 0.18586 | 129600
4870 | 7 | 203 | 21 | 0 | 0 | 0.16428 | 129600
4871 | 7 | 203 | 22 | 0 | 0 | 0.098228 | 129600
4872 | 7 | 203 | 23 | 0 | 0 | 0.1231 | 129600
4873 | 7 | 204 | 0 | 0 | 0 | 0.11057 | 129600
4874 | 7 | 204 | 1 | 0 | 0 | 0.096569 | 129600
4875 | 7 | 204 | 2 | 0 | 0 | 0.10623 | 129600
4876 | 7 | 204 | 3 | 0 | 0 | 0.1829 | 129600
4877 | 7 | 204 | 4 | 0 | 0 | 0.28778 | 129600
4878 | 7 | 204 | 5 | 0 | 0 | 0.23807 | 129600
4879 | 7 | 204 | 6 | 0 | 0.085505 | 0.24648 | 129600
4880 | 7 | 204 | 7 | 1 | 0.27494 | 0.2572 | 129400
4881 | 7 | 204 | 8 | 1 | 0.48573 | 0.38041 | 129200
4882 | 7 | 204 | 9 | 0 | 0.68446 | 0.36845 | 129200
4883 | 7 | 204 | 10 | 0 | 0.84571 | 0.48642 | 129200
4884 | 7 | 204 | 11 | 0 | 0.95043 | 0.50438 | 129200
4885 | 7 | 204 | 12 | 0 | 0.9867 | 0.46614 | 129200
4886 | 7 | 204 | 13 | 0 | 0.95043 | 0.61344 | 129200
4887 | 7 | 204 | 14 | 0 | 0.84571 | 0.8146 | 129200
4888 | 7 | 204 | 15 | 0 | 0.68446 | 0.82115 | 129200
4889 | 7 | 204 | 16 | 0 | 0.48573 | 0.65683 | 129200
4890 | 7 | 204 | 17 | 0 | 0.27494 | 0.45461 | 129200
4891 | 7 | 204 | 18 | 0 | 0.085505 | 0.46956 | 129200
4892 | 7 | 204 | 19 | 1 | 0 | 0.41941 | 129000
4893 | 7 | 204 | 20 | 1 | 0 | 0.39749 | 128800
4894 | 7 | 204 | 21 | 0 | 0 | 0.38861 | 128800
4895 | 7 | 204 | 22 | 0 | 0 | 0.33943 | 128800
4896 | 7 | 204 | 23 | 0 | 0 | 0.40152 | 128800
4897 | 7 | 205 | 0 | 0 | 0 | 0.42692 | 128800
4898 | 7 | 205 | 1 | 0 | 0 | 0.38753 | 128800
4899 | 7 | 205 | 2 | 0 | 0 | 0.43818 | 128800
4900 | 7 | 205 | 3 | 0 | 0 | 0.59751 | 128800
4901 | 7 | 205 | 4 | 0 | 0 | 0.50005 | 128800
4902 | 7 | 205 | 5 | 0 | 0 | 0.65896 | 128800
4903 | 7 | 205 | 6 | 0 | 0.079801 | 0.74725 | 128800
4904 | 7 | 205 | 7 | 1 | 0.2566 | 0.6435 | 128600
4905 | 7 | 205 | 8 | 1 | 0.45332 | 0.98373 | 128400
4906 | 7 | 205 | 9 | 0 | 0.6388 | 1 | 128400
4907 | 7 | 205 | 10 | 0 | 0.78929 | 1 | 128400
4908 | 7 | 205 | 11 | 0 | 0.88702 | 0.78356 | 128400
4909 | 7 | 205 | 12 | 0 | 0.92087 | 0.66105 | 128400
4910 | 7 | 205 | 13 | 0 | 0.88702 | 0.69633 | 128400
4911 | 7 | 205 | 14 | 0 | 0.78929 | 0.77951 | 128400
4912 | 7 | 205 | 15 | 0 | 0.6388 | 0.69754 | 128400
4913 | 7 | 205 | 16 | 0 | 0.45332 | 0.57841 | 128400
4914 | 7 | 205 | 17 | 0 | 0.2566 | 0.50079 | 128400
4915 | 7 | 205 | 18 | 0 | 0.079801 | 0.54665 | 128400
4916 | 7 | 205 | 19 | 1 | 0 | 0.35417 | 128200
4917 | 7 | 205 | 20 | 1 | 0 | 0.35926 | 128000
4918 | 7 | 205 | 21 | 0 | 0 | 0.34555 | 128000
4919 | 7 | 205 | 22 | 0 | 0 | 0.30095 | 128000
4920 | 7 | 205 | 23 | 0 | 0 | 0.32451 | 128000
4921 | 7 | 206 | 0 | 0 | 0 | 0.21142 | 128000
4922 | 7 | 206 | 1 | 0 | 0 | 0.26075 | 128000
4923 | 7 | 206 | 2 | 0 | 0 | 0.22004 | 128000
4924 | 7 | 206 | 3 | 0 | 0 | 0.24402 | 128000
4925 | 7 | 206 | 4 | 0 | 0 | 0.26748 | 128000
4926 | 7 | 206 | 5 | 0 | 0 | 0.25792 | 128000
4927 | 7 | 206 | 6 | 0 | 0.093275 | 0.22281 | 128000
4928 | 7 | 206 | 7 | 1 | 0.29993 | 0.34252 | 127800
4929 | 7 | 206 | 8 | 1 | 0.52987 | 0.40088 | 127600
4930 | 7 | 206 | 9 | 0 | 0.74666 | 0.46138 | 127600
4931 | 7 | 206 | 10 | 0 | 0.92256 | 0.4557 | 127600
4932 | 7 | 206 | 11 | 0 | 1 | 0.64674 | 127600
4933 | 7 | 206 | 12 | 0 | 1 | 0.87516 | 127600
4934 | 7 | 206 | 13 | 0 | 1 | 0.98276 | 127600
4935 | 7 | 206 | 14 | 0 | 0.92256 | 0.79092 | 127600
4936 | 7 | 206 | 15 | 0 | 0.74666 | 0.52125 | 127600
4937 | 7 | 206 | 16 | 0 | 0.52987 | 0.66904 | 127600
4938 | 7 | 206 | 17 | 0 | 0.29993 | 0.83274 | 127600
4939 | 7 | 206 | 18 | 0 | 0.093275 | 1 | 127600
4940 | 7 | 206 | 19 | 1 | 0 | 1 | 127400
4941 | 7 | 206 | 20 | 1 | 0 | 1 | 127200
4942 | 7 | 206 | 21 | 0 | 0 | 0.74588 | 127200
4943 | 7 | 206 | 22 | 0 | 0 | 0.72451 | 127200
4944 | 7 | 206 | 23 | 0 | 0 | 0.66816 | 127200
4945 | 7 | 207 | 0 | 0 | 0 | 0.55793 | 127200
4946 | 7 | 207 | 1 | 0 | 0 | 0.84414 | 127200
4947 | 7 | 207 | 2 | 0 | 0 | 0.78276 | 127200
4948 | 7 | 207 | 3 | 0 | 0 | 0.49757 | 127200
4949 | 7 | 207 | 4 | 0 | 0 | 0.64097 | 127200
4950 | 7 | 207 | 5 | 0 | 0 | 0.81687 | 127200
4951 | 7 | 207 | 6 | 0 | 0.067932 | 0.92631 | 127200
4952 | 7 | 207 | 7 | 1 | 0.21844 | 0.69593 | 127000
4953 | 7 | 207 | 8 | 1 | 0.3859 | 0.82799 | 126800
4954 | 7 | 207 | 9 | 0 | 0.54379 | 0.7153 | 126800
4955 | 7 | 207 | 10 | 0 | 0.67189 | 0.70546 | 126800
4956 | 7 | 207 | 11 | 0 | 0.75509 | 0.86103 | 126800
4957 | 7 | 207 | 12 | 0 | 0.7839 | 0.74418 | 126800
4958 | 7 | 207 | 13 | 0 | 0.75509 | 0.68275 | 126800
4959 | 7 | 207 | 14 | 0 | 0.67189 | 0.72896 | 126800
4960 | 7 | 207 | 15 | 0 | 0.54379 | 0.72581 | 126800
4961 | 7 | 207 | 16 | 0 | 0.3859 | 0.77779 | 126800
4962 | 7 | 207 | 17 | 0 | 0.21844 | 1 | 126800
4963 | 7 | 207 | 18 | 0 | 0.067932 | 0.85049 | 126800
4964 | 7 | 207 | 19 | 1 | 0 | 1 | 126600
4965 | 7 | 207 | 20 | 1 | 0 | 0.71138 | 126400
4966 | 7 | 207 | 21 | 0 | 0 | 0.42655 | 126400
4967 | 7 | 207 | 22 | 0 | 0 | 0.51427 | 126400
4968 | 7 | 207 | 23 | 0 | 0 | 0.68719 | 126400
4969 | 7 | 208 | 0 | 0 | 0 | 0.81587 | 126400
4970 | 7 | 208 | 1 | 0 | 0 | 0.83933 | 126400
4971 | 7 | 208 | 2 | 0 | 0 | 0.74781 | 126400
4972 | 7 | 208 | 3 | 0 | 0 | 0.75698 | 126400
4973 | 7 | 208 | 4 | 0 | 0 | 0.77436 | 126400
4974 | 7 | 208 | 5 | 0 | 0 | 0.85738 | 126400
4975 | 7 | 208 | 6 | 0 | 0.091205 | 0.95954 | 126400
4976 | 7 | 208 | 7 | 1 | 0.29327 | 0.92031 | 126200
4977 | 7 | 208 | 8 | 1 | 0.51811 | 0.53748 | 126000
4978 | 7 | 208 | 9 | 0 | 0.73009 | 0.58447 | 126000
4979 | 7 | 208 | 10 | 0 | 0.90208 | 0.73359 | 126000
4980 | 7 | 208 | 11 | 0 | 1 | 0.5645 | 126000
4981 | 7 | 208 | 12 | 0 | 1 | 0.46798 | 126000
4982 | 7 | 208 | 13 | 0 | 1 | 0.48355 | 126000
4983 | 7 | 208 | 14 | 0 | 0.90208 | 0.48277 | 126000
4984 | 7 | 208 | 15 | 0 | 0.73009 | 0.36732 | 126000
4985 | 7 | 208 | 16 | 0 | 0.51811 | 0.38572 | 126000
4986 | 7 | 208 | 17 | 0 | 0.29327 | 0.39736 | 126000
4987 | 7 | 208 | 18 | 0 | 0.091205 | 0.45002 | 126000
4988 | 7 | 208 | 19 | 1 | 0 | 0.27741 | 125800
4989 | 7 | 208 | 20 | 1 | 0 | 0.30076 | 125600
4990 | 7 | 208 | 21 | 0 | 0 | 0.35026 | 125600
4991 | 7 | 208 | 22 | 0 | 0 | 0.25007 | 125600
4992 | 7 | 208 | 23 | 0 | 0 | 0.17158 | 125600
4993 | 7 | 209 | 0 | 0 | 0 | 0.2367 | 125600
4994 | 7 | 209 | 1 | 0 | 0 | 0.22603 | 125600
4995 | 7 | 209 | 2 | 0 | 0 | 0.30266 | 125600
4996 | 7 | 209 | 3 | 0 | 0 | 0.27492 | 125600
4997 | 7 | 209 | 4 | 0 | 0 | 0.38482 | 125600
4998 | 7 | 209 | 5 | 0 | 0 | 0.59938 | 125600
4999 | 7 | 209 | 6 | 0 | 0.065072 | 0.48604 | 125600
5000 | 7 | 209 | 7 | 1 | 0.20924 | 0.52594 | 125400
5001 | 7 | 209 | 8 | 1 | 0.36966 | 0.70942 | 125200
5002 | 7 | 209 | 9 | 0 | 0.5209 | 0.66006 | 125200
5003 | 7 | 209 | 10 | 0 | 0.64361 | 0.48924 | 125200
5004 | 7 | 209 | 11 | 0 | 0.72331 | 0.61861 | 125200
5005 | 7 | 209 | 12 | 0 | 0.75091 | 0.51024 | 125200
5006 | 7 | 209 | 13 | 0 | 0.72331 | 0.53193 | 125200
5007 | 7 | 209 | 14 | 0 | 0.64361 | 0.47057 | 125200
5008 | 7 | 209 | 15 | 0 | 0.5209 | 0.43878 | 125200
5009 | 7 | 209 | 16 | 0 | 0.36966 | 0.49066 | 125200
5010 | 7 | 209 | 17 | 0 | 0.20924 | 0.49979 | 125200
5011 | 7 | 209 | 18 | 0 | 0.065072 | 0.59931 | 125200
5012 | 7 | 209 | 19 | 1 | 0 | 0.62312 | 125000
5013 | 7 | 209 | 20 | 1 | 0 | 0.61565 | 124800
5014 | 7 | 209 | 21 | 0 | 0 | 0.48248 | 124800
5015 | 7 | 209 | 22 | 0 | 0 | 0.40377 | 124800
5016 | 7 | 209 | 23 | 0 | 0 | 0.32938 | 124800
5017 | 7 | 210 | 0 | 0 | 0 | 0.40207 | 124800
5018 | 7 | 210 | 1 | 0 | 0 | 0.34133 | 124800
5019 | 7 | 210 | 2 | 0 | 0 | 0.16415 | 124800
5020 | 7 | 210 | 3 | 0 | 0 | 0.20257 | 124800
5021 | 7 | 210 | 4 | 0 | 0 | 0.18929 | 124800
5022 | 7 | 210 | 5 | 0 | 0 | 0.22539 | 124800
5023 | 7 | 210 | 6 | 0 | 0.089109 | 0.19928 | 124800
5024 | 7 | 210 | 7 | 1 | 0.28653 | 0.23807 | 124600
5025 | 7 | 210 | 8 | 1 | 0.5062 | 0.20987 | 124400
5026 | 7 | 210 | 9 | 0 | 0.71331 | 0.20241 | 124400
5027 | 7 | 210 | 10 | 0 | 0.88135 | 0.20938 | 124400
5028 | 7 | 210 | 11 | 0 | 0.99049 | 0.2138 | 124400
5029 | 7 | 210 | 12 | 0 | 1 | 0.26776 | 124400
5030 | 7 | 210 | 13 | 0 | 0.99049 | 0.30453 | 124400
5031 | 7 | 210 | 14 | 0 | 0.88135 | 0.24784 | 124400
5032 | 7 | 210 | 15 | 0 | 0.71331 | 0.29668 | 124400
5033 | 7 | 210 | 16 | 0 | 0.5062 | 0.22216 | 124400
5034 | 7 | 210 | 17 | 0 | 0.28653 | 0.32359 | 124400
5035 | 7 | 210 | 18 | 0 | 0.089109 | 0.16183 | 124400
5036 | 7 | 210 | 19 | 1 | 0 | 0.28059 | 124200
5037 | 7 | 210 | 20 | 1 | 0 | 0.38343 | 124000
5038 | 7 | 210 | 21 | 0 | 0 | 0.3607 | 124000
5039 | 7 | 210 | 22 | 0 | 0 | 0.34528 | 124000
5040 | 7 | 210 | 23 | 0 | 0 | 0.3785 | 124000
5041 | 7 | 211 | 0 | 0 | 0 | 0.35046 | 124000
5042 | 7 | 211 | 1 | 0 | 0 | 0.3044 | 124000
5043 | 7 | 211 | 2 | 0 | 0 | 0.24547 | 124000
5044 | 7 | 211 | 3 | 0 | 0 | 0.25977 | 124000
5045 | 7 | 211 | 4 | 0 | 0 | 0.18279 | 124000
5046 | 7 | 211 | 5 | 0 | 0 | 0.23329 | 124000
5047 | 7 | 211 | 6 | 0 | 0.10068 | 0.37081 | 124000
5048 | 7 | 211 | 7 | 1 | 0.32374 | 0.42596 | 123800
5049 | 7 | 211 | 8 | 1 | 0.57193 | 0.55174 | 123600
5050 | 7 | 211 | 9 | 0 | 0.80593 | 0.46036 | 123600
5051 | 7 | 211 | 10 | 0 | 0.99579 | 0.35274 | 123600
5052 | 7 | 211 | 11 | 0 | 1 | 0.46771 | 123600
5053 | 7 | 211 | 12 | 0 | 1 | 0.38784 | 123600
5054 | 7 | 211 | 13 | 0 | 1 | 0.38445 | 123600
5055 | 7 | 211 | 14 | 0 | 0.99579 | 0.45956 | 123600
5056 | 7 | 211 | 15 | 0 | 0.80593 | 0.42562 | 123600
5057 | 7 | 211 | 16 | 0 | 0.57193 | 0.38069 | 123600
5058 | 7 | 211 | 17 | 0 | 0.32374 | 0.42102 | 123600
5059 | 7 | 211 | 18 | 0 | 0.10068 | 0.56176 | 123600
5060 | 7 | 211 | 19 | 1 | 0 | 0.42804 | 123400
5061 | 7 | 211 | 20 | 1 | 0 | 0.35633 | 123200
5062 | 7 | 211 | 21 | 0 | 0 | 0.38303 | 123200
5063 | 7 | 211 | 22 | 0 | 0 | 0.33379 | 123200
5064 | 7 | 211 | 23 | 0 | 0 | 0.35157 | 123200
5065 | 7 | 212 | 0 | 0 | 0 | 0.33804 | 123200
5066 | 7 | 212 | 1 | 0 | 0 | 0.31075 | 123200
5067 | 7 | 212 | 2 | 0 | 0 | 0.42005 | 123200
5068 | 7 | 212 | 3 | 0 | 0 | 0.27609 | 123200
5069 | 7 | 212 | 4 | 0 | 0 | 0.25636 | 123200
5070 | 7 | 212 | 5 | 0 | 0 | 0.30492 | 123200
5071 | 7 | 212 | 6 | 0 | 0.08483 | 0.38794 | 123200
5072 | 7 | 212 | 7 | 1 | 0.27277 | 0.45424 | 123000
5073 | 7 | 212 | 8 | 1 | 0.4819 | 0.54613 | 122800
5074 | 7 | 212 | 9 | 0 | 0.67906 | 0.42885 | 122800
5075 | 7 | 212 | 10 | 0 | 0.83903 | 0.59593 | 122800
5076 | 7 | 212 | 11 | 0 | 0.94293 | 0.8014 | 122800
5077 | 7 | 212 | 12 | 0 | 0.97891 | 0.82502 | 122800
5078 | 7 | 212 | 13 | 0 | 0.94293 | 0.84242 | 122800
5079 | 7 | 212 | 14 | 0 | 0.83903 | 0.90321 | 122800
5080 | 7 | 212 | 15 | 0 | 0.67906 | 0.68075 | 122800
5081 | 7 | 212 | 16 | 0 | 0.4819 | 0.54177 | 122800
5082 | 7 | 212 | 17 | 0 | 0.27277 | 0.81747 | 122800
5083 | 7 | 212 | 18 | 0 | 0.08483 | 0.566 | 122800
5084 | 7 | 212 | 19 | 1 | 0 | 0.54429 | 122600
5085 | 7 | 212 | 20 | 1 | 0 | 0.45608 | 122400
5086 | 7 | 212 | 21 | 0 | 0 | 0.5348 | 122400
5087 | 7 | 212 | 22 | 0 | 0 | 0.50414 | 122400
5088 | 7 | 212 | 23 | 0 | 0 | 0.55699 | 122400
5089 | 8 | 213 | 0 | 0 | 0 | 0.46419 | 122400
5090 | 8 | 213 | 1 | 0 | 0 | 0.50823 | 122400
5091 | 8 | 213 | 2 | 0 | 0 | 0.53685 | 122400
5092 | 8 | 213 | 3 | 0 | 0 | 0.58147 | 122400
5093 | 8 | 213 | 4 | 0 | 0 | 0.75688 | 122400
5094 | 8 | 213 | 5 | 0 | 0 | 0.96748 | 122400
5095 | 8 | 213 | 6 | 0 | 0.045947 | 1 | 122400
5096 | 8 | 213 | 7 | 1 | 0.21737 | 1 | 122200
5097 | 8 | 213 | 8 | 1 | 0.41856 | 1 | 122000
5098 | 8 | 213 | 9 | 0 | 0.61231 | 1 | 122000
5099 | 8 | 213 | 10 | 0 | 0.77136 | 1 | 122000
5100 | 8 | 213 | 11 | 0 | 0.87534 | 0.87839 | 122000
5101 | 8 | 213 | 12 | 0 | 0.91146 | 0.69184 | 122000
5102 | 8 | 213 | 13 | 0 | 0.87534 | 0.79396 | 122000
5103 | 8 | 213 | 14 | 0 | 0.77136 | 0.92495 | 122000
5104 | 8 | 213 | 15 | 0 | 0.61231 | 0.7424 | 122000
5105 | 8 | 213 | 16 | 0 | 0.41856 | 0.66382 | 122000
5106 | 8 | 213 | 17 | 0 | 0.21737 | 0.66399 | 122000
5107 | 8 | 213 | 18 | 0 | 0.045947 | 0.51282 | 122000
5108 | 8 | 213 | 19 | 1 | 0 | 0.46219 | 121800
5109 | 8 | 213 | 20 | 1 | 0 | 0.52616 | 121600
5110 | 8 | 213 | 21 | 0 | 0 | 0.55578 | 121600
5111 | 8 | 213 | 22 | 0 | 0 | 0.46911 | 121600
5112 | 8 | 213 | 23 | 0 | 0 | 0.35174 | 121600
5113 | 8 | 214 | 0 | 0 | 0 | 0.33386 | 121600
5114 | 8 | 214 | 1 | 0 | 0 | 0.36723 | 121600
5115 | 8 | 214 | 2 | 0 | 0 | 0.41166 | 121600
5116 | 8 | 214 | 3 | 0 | 0 | 0.42108 | 121600
5117 | 8 | 214 | 4 | 0 | 0 | 0.32156 | 121600
5118 | 8 | 214 | 5 | 0 | 0 | 0.33424 | 121600
5119 | 8 | 214 | 6 | 0 | 0.04399 | 0.39856 | 121600
5120 | 8 | 214 | 7 | 1 | 0.20811 | 0.55056 | 121400
5121 | 8 | 214 | 8 | 1 | 0.40074 | 0.39345 | 121200
5122 | 8 | 214 | 9 | 0 | 0.58623 | 0.41375 | 121200
5123 | 8 | 214 | 10 | 0 | 0.73851 | 0.43312 | 121200
5124 | 8 | 214 | 11 | 0 | 0.83806 | 0.43438 | 121200
5125 | 8 | 214 | 12 | 0 | 0.87264 | 0.41791 | 121200
5126 | 8 | 214 | 13 | 0 | 0.83806 | 0.52189 | 121200
5127 | 8 | 214 | 14 | 0 | 0.73851 | 0.51391 | 121200
5128 | 8 | 214 | 15 | 0 | 0.58623 | 0.376 | 121200
5129 | 8 | 214 | 16 | 0 | 0.40074 | 0.34541 | 121200
5130 | 8 | 214 | 17 | 0 | 0.20811 | 0.63193 | 121200
5131 | 8 | 214 | 18 | 0 | 0.04399 | 0.50704 | 121200
5132 | 8 | 214 | 19 | 1 | 0 | 0.44207 | 121000
5133 | 8 | 214 | 20 | 1 | 0 | 0.40239 | 120800
5134 | 8 | 214 | 21 | 0 | 0 | 0.38527 | 120800
5135 | 8 | 214 | 22 | 0 | 0 | 0.34722 | 120800
5136 | 8 | 214 | 23 | 0 | 0 | 0.31176 | 120800
5137 | 8 | 215 | 0 | 0 | 0 | 0.4614 | 120800
5138 | 8 | 215 | 1 | 0 | 0 | 0.4824 | 120800
5139 | 8 | 215 | 2 | 0 | 0 | 0.40568 | 120800
5140 | 8 | 215 | 3 | 0 | 0 | 0.34805 | 120800
5141 | 8 | 215 | 4 | 0 | 0 | 0.51354 | 120800
5142 | 8 | 215 | 5 | 0 | 0 | 0.57949 | 120800
5143 | 8 | 215 | 6 | 0 | 0.053831 | 0.70936 | 120800
5144 | 8 | 215 | 7 | 1 | 0.25467 | 1 | 120600
5145 | 8 | 215 | 8 | 1 | 0.49038 | 0.56263 | 120400
5146 | 8 | 215 | 9 | 0 | 0.71737 | 0.60559 | 120400
5147 | 8 | 215 | 10 | 0 | 0.90372 | 0.71372 | 120400
5148 | 8 | 215 | 11 | 0 | 1 | 0.62001 | 120400
5149 | 8 | 215 | 12 | 0 | 1 | 0.80895 | 120400
5150 | 8 | 215 | 13 | 0 | 1 | 0.60893 | 120400
5151 | 8 | 215 | 14 | 0 | 0.90372 | 0.67794 | 120400
5152 | 8 | 215 | 15 | 0 | 0.71737 | 0.63004 | 120400
5153 | 8 | 215 | 16 | 0 | 0.49038 | 0.85352 | 120400
5154 | 8 | 215 | 17 | 0 | 0.25467 | 0.7126 | 120400
5155 | 8 | 215 | 18 | 0 | 0.053831 | 0.73572 | 120400
5156 | 8 | 215 | 19 | 1 | 0 | 0.69729 | 120200
5157 | 8 | 215 | 20 | 1 | 0 | 0.70434 | 120000
5158 | 8 | 215 | 21 | 0 | 0 | 0.59984 | 120000
5159 | 8 | 215 | 22 | 0 | 0 | 0.66907 | 120000
5160 | 8 | 215 | 23 | 0 | 0 | 0.67266 | 120000
5161 | 8 | 216 | 0 | 0 | 0 | 0.49734 | 120000
5162 | 8 | 216 | 1 | 0 | 0 | 0.6555 | 120000
5163 | 8 | 216 | 2 | 0 | 0 | 0.82717 | 120000
5164 | 8 | 216 | 3 | 0 | 0 | 0.9107 | 120000
5165 | 8 | 216 | 4 | 0 | 0 | 1 | 120000
5166 | 8 | 216 | 5 | 0 | 0 | 1 | 120000
5167 | 8 | 216 | 6 | 0 | 0.05586 | 1 | 120000
5168 | 8 | 216 | 7 | 1 | 0.26427 | 1 | 119800
5169 | 8 | 216 | 8 | 1 | 0.50887 | 1 | 119600
5170 | 8 | 216 | 9 | 0 | 0.74442 | 1 | 119600
5171 | 8 | 216 | 10 | 0 | 0.93778 | 1 | 119600
5172 | 8 | 216 | 11 | 0 | 1 | 1 | 119600
5173 | 8 | 216 | 12 | 0 | 1 | 1 | 119600
5174 | 8 | 216 | 13 | 0 | 1 | 0.68461 | 119600
5175 | 8 | 216 | 14 | 0 | 0.93778 | 0.60423 | 119600
5176 | 8 | 216 | 15 | 0 | 0.74442 | 0.88182 | 119600
5177 | 8 | 216 | 16 | 0 | 0.50887 | 0.80656 | 119600
5178 | 8 | 216 | 17 | 0 | 0.26427 | 0.88059 | 119600
5179 | 8 | 216 | 18 | 0 | 0.05586 | 1 | 119600
5180 | 8 | 216 | 19 | 1 | 0 | 1 | 119400
5181 | 8 | 216 | 20 | 1 | 0 | 1 | 119200
5182 | 8 | 216 | 21 | 0 | 0 | 0.80484 | 119200
5183 | 8 | 216 | 22 | 0 | 0 | 1 | 119200
5184 | 8 | 216 | 23 | 0 | 0 | 1 | 119200
5185 | 8 | 217 | 0 | 0 | 0 | 1 | 119200
5186 | 8 | 217 | 1 | 0 | 0 | 1 | 119200
5187 | 8 | 217 | 2 | 0 | 0 | 1 | 119200
5188 | 8 | 217 | 3 | 0 | 0 | 1 | 119200
5189 | 8 | 217 | 4 | 0 | 0 | 1 | 119200
5190 | 8 | 217 | 5 | 0 | 0 | 1 | 119200
5191 | 8 | 217 | 6 | 0 | 0.047433 | 0.87727 | 119200
5192 | 8 | 217 | 7 | 1 | 0.2244 | 0.77043 | 119000
5193 | 8 | 217 | 8 | 1 | 0.4321 | 1 | 118800
5194 | 8 | 217 | 9 | 0 | 0.63211 | 0.83792 | 118800
5195 | 8 | 217 | 10 | 0 | 0.79631 | 1 | 118800
5196 | 8 | 217 | 11 | 0 | 0.90365 | 1 | 118800
5197 | 8 | 217 | 12 | 0 | 0.94094 | 1 | 118800
5198 | 8 | 217 | 13 | 0 | 0.90365 | 1 | 118800
5199 | 8 | 217 | 14 | 0 | 0.79631 | 0.94344 | 118800
5200 | 8 | 217 | 15 | 0 | 0.63211 | 0.96815 | 118800
5201 | 8 | 217 | 16 | 0 | 0.4321 | 0.77788 | 118800
5202 | 8 | 217 | 17 | 0 | 0.2244 | 1 | 118800
5203 | 8 | 217 | 18 | 0 | 0.047433 | 1 | 118800
5204 | 8 | 217 | 19 | 1 | 0 | 0.8069 | 118600
5205 | 8 | 217 | 20 | 1 | 0 | 0.80087 | 118400
5206 | 8 | 217 | 21 | 0 | 0 | 1 | 118400
5207 | 8 | 217 | 22 | 0 | 0 | 0.95981 | 118400
5208 | 8 | 217 | 23 | 0 | 0 | 1 | 118400
5209 | 8 | 218 | 0 | 0 | 0 | 0.95988 | 118400
5210 | 8 | 218 | 1 | 0 | 0 | 1 | 118400
5211 | 8 | 218 | 2 | 0 | 0 | 0.79589 | 118400
5212 | 8 | 218 | 3 | 0 | 0 | 0.83661 | 118400
5213 | 8 | 218 | 4 | 0 | 0 | 0.70139 | 118400
5214 | 8 | 218 | 5 | 0 | 0 | 0.50691 | 118400
5215 | 8 | 218 | 6 | 0 | 0.04247 | 0.43478 | 118400
5216 | 8 | 218 | 7 | 1 | 0.20092 | 0.40424 | 118200
5217 | 8 | 218 | 8 | 1 | 0.38689 | 0.42418 | 118000
5218 | 8 | 218 | 9 | 0 | 0.56598 | 0.47868 | 118000
5219 | 8 | 218 | 10 | 0 | 0.71299 | 0.46979 | 118000
5220 | 8 | 218 | 11 | 0 | 0.80911 | 0.47137 | 118000
5221 | 8 | 218 | 12 | 0 | 0.84249 | 0.52143 | 118000
5222 | 8 | 218 | 13 | 0 | 0.80911 | 0.72418 | 118000
5223 | 8 | 218 | 14 | 0 | 0.71299 | 0.73095 | 118000
5224 | 8 | 218 | 15 | 0 | 0.56598 | 0.43036 | 118000
5225 | 8 | 218 | 16 | 0 | 0.38689 | 0.34269 | 118000
5226 | 8 | 218 | 17 | 0 | 0.20092 | 0.39325 | 118000
5227 | 8 | 218 | 18 | 0 | 0.04247 | 0.52036 | 118000
5228 | 8 | 218 | 19 | 1 | 0 | 0.48812 | 117800
5229 | 8 | 218 | 20 | 1 | 0 | 0.73846 | 117600
5230 | 8 | 218 | 21 | 0 | 0 | 0.5287 | 117600
5231 | 8 | 218 | 22 | 0 | 0 | 0.40817 | 117600
5232 | 8 | 218 | 23 | 0 | 0 | 0.52146 | 117600
5233 | 8 | 219 | 0 | 0 | 0 | 0.45503 | 117600
5234 | 8 | 219 | 1 | 0 | 0 | 0.4786 | 117600
5235 | 8 | 219 | 2 | 0 | 0 | 0.48516 | 117600
5236 | 8 | 219 | 3 | 0 | 0 | 0.60906 | 117600
5237 | 8 | 219 | 4 | 0 | 0 | 0.56197 | 117600
5238 | 8 | 219 | 5 | 0 | 0 | 0.43222 | 117600
5239 | 8 | 219 | 6 | 0 | 0.054453 | 0.49949 | 117600
5240 | 8 | 219 | 7 | 1 | 0.25761 | 0.46514 | 117400
5241 | 8 | 219 | 8 | 1 | 0.49604 | 0.52141 | 117200
5242 | 8 | 219 | 9 | 0 | 0.72566 | 0.57178 | 117200
5243 | 8 | 219 | 10 | 0 | 0.91415 | 0.56094 | 117200
5244 | 8 | 219 | 11 | 0 | 1 | 0.73985 | 117200
5245 | 8 | 219 | 12 | 0 | 1 | 0.98533 | 117200
5246 | 8 | 219 | 13 | 0 | 1 | 1 | 117200
5247 | 8 | 219 | 14 | 0 | 0.91415 | 0.90817 | 117200
5248 | 8 | 219 | 15 | 0 | 0.72566 | 0.91963 | 117200
5249 | 8 | 219 | 16 | 0 | 0.49604 | 0.93973 | 117200
5250 | 8 | 219 | 17 | 0 | 0.25761 | 0.82909 | 117200
5251 | 8 | 219 | 18 | 0 | 0.054453 | 0.98279 | 117200
5252 | 8 | 219 | 19 | 1 | 0 | 1 | 117000
5253 | 8 | 219 | 20 | 1 | 0 | 0.74633 | 116800
5254 | 8 | 219 | 21 | 0 | 0 | 0.81123 | 116800
5255 | 8 | 219 | 22 | 0 | 0 | 0.88423 | 116800
5256 | 8 | 219 | 23 | 0 | 0 | 0.96474 | 116800
5257 | 8 | 220 | 0 | 0 | 0 | 1 | 116800
5258 | 8 | 220 | 1 | 0 | 0 | 0.96656 | 116800
5259 | 8 | 220 | 2 | 0 | 0 | 0.63004 | 116800
5260 | 8 | 220 | 3 | 0 | 0 | 0.51806 | 116800
5261 | 8 | 220 | 4 | 0 | 0 | 0.43502 | 116800
5262 | 8 | 220 | 5 | 0 | 0 | 0.49673 | 116800
5263 | 8 | 220 | 6 | 0 | 0.053648 | 0.4555 | 116800
5264 | 8 | 220 | 7 | 1 | 0.25381 | 0.62096 | 116600
5265 | 8 | 220 | 8 | 1 | 0.48871 | 0.69148 | 116400
5266 | 8 | 220 | 9 | 0 | 0.71493 | 0.54658 | 116400
5267 | 8 | 220 | 10 | 0 | 0.90064 | 0.47912 | 116400
5268 | 8 | 220 | 11 | 0 | 1 | 0.46031 | 116400
5269 | 8 | 220 | 12 | 0 | 1 | 0.38416 | 116400
5270 | 8 | 220 | 13 | 0 | 1 | 0.46065 | 116400
5271 | 8 | 220 | 14 | 0 | 0.90064 | 0.58673 | 116400
5272 | 8 | 220 | 15 | 0 | 0.71493 | 0.76437 | 116400
5273 | 8 | 220 | 16 | 0 | 0.48871 | 0.79607 | 116400
5274 | 8 | 220 | 17 | 0 | 0.25381 | 1 | 116400
5275 | 8 | 220 | 18 | 0 | 0.053648 | 0.91506 | 116400
5276 | 8 | 220 | 19 | 1 | 0 | 0.81298 | 116200
5277 | 8 | 220 | 20 | 1 | 0 | 0.73723 | 116000
5278 | 8 | 220 | 21 | 0 | 0 | 0.8244 | 116000
5279 | 8 | 220 | 22 | 0 | 0 | 0.68982 | 116000
5280 | 8 | 220 | 23 | 0 | 0 | 0.51227 | 116000
5281 | 8 | 221 | 0 | 0 | 0 | 0.72779 | 116000
5282 | 8 | 221 | 1 | 0 | 0 | 0.77569 | 116000
5283 | 8 | 221 | 2 | 0 | 0 | 0.60387 | 116000
5284 | 8 | 221 | 3 | 0 | 0 | 0.4843 | 116000
5285 | 8 | 221 | 4 | 0 | 0 | 0.67622 | 116000
5286 | 8 | 221 | 5 | 0 | 0 | 0.56786 | 116000
5287 | 8 | 221 | 6 | 0 | 0.044421 | 0.55468 | 116000
5288 | 8 | 221 | 7 | 1 | 0.21015 | 0.70067 | 115800
5289 | 8 | 221 | 8 | 1 | 0.40466 | 0.88446 | 115600
5290 | 8 | 221 | 9 | 0 | 0.59197 | 0.89855 | 115600
5291 | 8 | 221 | 10 | 0 | 0.74574 | 0.72041 | 115600
5292 | 8 | 221 | 11 | 0 | 0.84627 | 0.6278 | 115600
5293 | 8 | 221 | 12 | 0 | 0.88119 | 0.9136 | 115600
5294 | 8 | 221 | 13 | 0 | 0.84627 | 0.82592 | 115600
5295 | 8 | 221 | 14 | 0 | 0.74574 | 1 | 115600
5296 | 8 | 221 | 15 | 0 | 0.59197 | 0.97424 | 115600
5297 | 8 | 221 | 16 | 0 | 0.40466 | 1 | 115600
5298 | 8 | 221 | 17 | 0 | 0.21015 | 0.95605 | 115600
5299 | 8 | 221 | 18 | 0 | 0.044421 | 0.88102 | 115600
5300 | 8 | 221 | 19 | 1 | 0 | 0.75161 | 115400
5301 | 8 | 221 | 20 | 1 | 0 | 0.93441 | 115200
5302 | 8 | 221 | 21 | 0 | 0 | 1 | 115200
5303 | 8 | 221 | 22 | 0 | 0 | 1 | 115200
5304 | 8 | 221 | 23 | 0 | 0 | 1 | 115200
5305 | 8 | 222 | 0 | 0 | 0 | 1 | 115200
5306 | 8 | 222 | 1 | 0 | 0 | 1 | 115200
5307 | 8 | 222 | 2 | 0 | 0 | 0.77274 | 115200
5308 | 8 | 222 | 3 | 0 | 0 | 0.78237 | 115200
5309 | 8 | 222 | 4 | 0 | 0 | 0.71096 | 115200
5310 | 8 | 222 | 5 | 0 | 0 | 0.58705 | 115200
5311 | 8 | 222 | 6 | 0 | 0.051384 | 0.8121 | 115200
5312 | 8 | 222 | 7 | 1 | 0.2431 | 1 | 115000
5313 | 8 | 222 | 8 | 1 | 0.46809 | 1 | 114800
5314 | 8 | 222 | 9 | 0 | 0.68476 | 1 | 114800
5315 | 8 | 222 | 10 | 0 | 0.86263 | 1 | 114800
5316 | 8 | 222 | 11 | 0 | 0.97892 | 1 | 114800
5317 | 8 | 222 | 12 | 0 | 1 | 1 | 114800
5318 | 8 | 222 | 13 | 0 | 0.97892 | 0.613 | 114800
5319 | 8 | 222 | 14 | 0 | 0.86263 | 0.79241 | 114800
5320 | 8 | 222 | 15 | 0 | 0.68476 | 0.43605 | 114800
5321 | 8 | 222 | 16 | 0 | 0.46809 | 0.5924 | 114800
5322 | 8 | 222 | 17 | 0 | 0.2431 | 0.47092 | 114800
5323 | 8 | 222 | 18 | 0 | 0.051384 | 0.57477 | 114800
5324 | 8 | 222 | 19 | 1 | 0 | 0.59358 | 114600
5325 | 8 | 222 | 20 | 1 | 0 | 0.49996 | 114400
5326 | 8 | 222 | 21 | 0 | 0 | 0.42199 | 114400
5327 | 8 | 222 | 22 | 0 | 0 | 0.44548 | 114400
5328 | 8 | 222 | 23 | 0 | 0 | 0.36784 | 114400
5329 | 8 | 223 | 0 | 0 | 0 | 0.59802 | 114400
5330 | 8 | 223 | 1 | 0 | 0 | 0.47607 | 114400
5331 | 8 | 223 | 2 | 0 | 0 | 0.42996 | 114400
5332 | 8 | 223 | 3 | 0 | 0 | 0.28661 | 114400
5333 | 8 | 223 | 4 | 0 | 0 | 0.32668 | 114400
5334 | 8 | 223 | 5 | 0 | 0 | 0.3196 | 114400
5335 | 8 | 223 | 6 | 0 | 0.047378 | 0.29418 | 114400
5336 | 8 | 223 | 7 | 1 | 0.22414 | 0.22946 | 114200
5337 | 8 | 223 | 8 | 1 | 0.4316 | 0.34469 | 114000
5338 | 8 | 223 | 9 | 0 | 0.63138 | 0.34288 | 114000
5339 | 8 | 223 | 10 | 0 | 0.79538 | 0.38324 | 114000
5340 | 8 | 223 | 11 | 0 | 0.9026 | 0.61143 | 114000
5341 | 8 | 223 | 12 | 0 | 0.93985 | 0.82669 | 114000
5342 | 8 | 223 | 13 | 0 | 0.9026 | 1 | 114000
5343 | 8 | 223 | 14 | 0 | 0.79538 | 0.66624 | 114000
5344 | 8 | 223 | 15 | 0 | 0.63138 | 1 | 114000
5345 | 8 | 223 | 16 | 0 | 0.4316 | 1 | 114000
5346 | 8 | 223 | 17 | 0 | 0.22414 | 1 | 114000
5347 | 8 | 223 | 18 | 0 | 0.047378 | 1 | 114000
5348 | 8 | 223 | 19 | 1 | 0 | 0.87806 | 113800
5349 | 8 | 223 | 20 | 1 | 0 | 0.59831 | 113600
5350 | 8 | 223 | 21 | 0 | 0 | 0.44924 | 113600
5351 | 8 | 223 | 22 | 0 | 0 | 0.22653 | 113600
5352 | 8 | 223 | 23 | 0 | 0 | 0.30185 | 113600
5353 | 8 | 224 | 0 | 0 | 0 | 0.27491 | 113600
5354 | 8 | 224 | 1 | 0 | 0 | 0.38193 | 113600
5355 | 8 | 224 | 2 | 0 | 0 | 0.47008 | 113600
5356 | 8 | 224 | 3 | 0 | 0 | 0.58735 | 113600
5357 | 8 | 224 | 4 | 0 | 0 | 0.75426 | 113600
5358 | 8 | 224 | 5 | 0 | 0 | 0.54867 | 113600
5359 | 8 | 224 | 6 | 0 | 0.0551 | 0.97886 | 113600
5360 | 8 | 224 | 7 | 1 | 0.26067 | 1 | 113400
5361 | 8 | 224 | 8 | 1 | 0.50194 | 1 | 113200
5362 | 8 | 224 | 9 | 0 | 0.73428 | 1 | 113200
5363 | 8 | 224 | 10 | 0 | 0.92501 | 1 | 113200
5364 | 8 | 224 | 11 | 0 | 1 | 1 | 113200
5365 | 8 | 224 | 12 | 0 | 1 | 1 | 113200
5366 | 8 | 224 | 13 | 0 | 1 | 1 | 113200
5367 | 8 | 224 | 14 | 0 | 0.92501 | 1 | 113200
5368 | 8 | 224 | 15 | 0 | 0.73428 | 0.84118 | 113200
5369 | 8 | 224 | 16 | 0 | 0.50194 | 0.76567 | 113200
5370 | 8 | 224 | 17 | 0 | 0.26067 | 0.68917 | 113200
5371 | 8 | 224 | 18 | 0 | 0.0551 | 0.50729 | 113200
5372 | 8 | 224 | 19 | 1 | 0 | 0.52585 | 113000
5373 | 8 | 224 | 20 | 1 | 0 | 0.73156 | 112800
5374 | 8 | 224 | 21 | 0 | 0 | 1 | 112800
5375 | 8 | 224 | 22 | 0 | 0 | 1 | 112800
5376 | 8 | 224 | 23 | 0 | 0 | 1 | 112800
5377 | 8 | 225 | 0 | 0 | 0 | 1 | 112800
5378 | 8 | 225 | 1 | 0 | 0 | 1 | 112800
5379 | 8 | 225 | 2 | 0 | 0 | 1 | 112800
5380 | 8 | 225 | 3 | 0 | 0 | 1 | 112800
5381 | 8 | 225 | 4 | 0 | 0 | 1 | 112800
5382 | 8 | 225 | 5 | 0 | 0 | 1 | 112800
5383 | 8 | 225 | 6 | 0 | 0.05093 | 1 | 112800
5384 | 8 | 225 | 7 | 1 | 0.24095 | 1 | 112600
5385 | 8 | 225 | 8 | 1 | 0.46396 | 1 | 112400
5386 | 8 | 225 | 9 | 0 | 0.67872 | 1 | 112400
5387 | 8 | 225 | 10 | 0 | 0.85502 | 1 | 112400
5388 | 8 | 225 | 11 | 0 | 0.97028 | 1 | 112400
5389 | 8 | 225 | 12 | 0 | 1 | 1 | 112400
5390 | 8 | 225 | 13 | 0 | 0.97028 | 1 | 112400
5391 | 8 | 225 | 14 | 0 | 0.85502 | 1 | 112400
5392 | 8 | 225 | 15 | 0 | 0.67872 | 1 | 112400
5393 | 8 | 225 | 16 | 0 | 0.46396 | 1 | 112400
5394 | 8 | 225 | 17 | 0 | 0.24095 | 1 | 112400
5395 | 8 | 225 | 18 | 0 | 0.05093 | 1 | 112400
5396 | 8 | 225 | 19 | 1 | 0 | 1 | 112200
5397 | 8 | 225 | 20 | 1 | 0 | 1 | 112000
5398 | 8 | 225 | 21 | 0 | 0 | 1 | 112000
5399 | 8 | 225 | 22 | 0 | 0 | 1 | 112000
5400 | 8 | 225 | 23 | 0 | 0 | 1 | 112000
5401 | 8 | 226 | 0 | 0 | 0 | 1 | 112000
5402 | 8 | 226 | 1 | 0 | 0 | 1 | 112000
5403 | 8 | 226 | 2 | 0 | 0 | 1 | 112000
5404 | 8 | 226 | 3 | 0 | 0 | 0.75796 | 112000
5405 | 8 | 226 | 4 | 0 | 0 | 0.87526 | 112000
5406 | 8 | 226 | 5 | 0 | 0 | 0.84553 | 112000
5407 | 8 | 226 | 6 | 0 | 0.05225 | 0.55575 | 112000
5408 | 8 | 226 | 7 | 1 | 0.24719 | 0.53308 | 111800
5409 | 8 | 226 | 8 | 1 | 0.47598 | 0.44993 | 111600
5410 | 8 | 226 | 9 | 0 | 0.6963 | 0.53663 | 111600
5411 | 8 | 226 | 10 | 0 | 0.87717 | 0.50112 | 111600
5412 | 8 | 226 | 11 | 0 | 0.99542 | 0.85856 | 111600
5413 | 8 | 226 | 12 | 0 | 1 | 0.95422 | 111600
5414 | 8 | 226 | 13 | 0 | 0.99542 | 1 | 111600
5415 | 8 | 226 | 14 | 0 | 0.87717 | 0.46889 | 111600
5416 | 8 | 226 | 15 | 0 | 0.6963 | 0.66251 | 111600
5417 | 8 | 226 | 16 | 0 | 0.47598 | 0.50727 | 111600
5418 | 8 | 226 | 17 | 0 | 0.24719 | 0.38811 | 111600
5419 | 8 | 226 | 18 | 0 | 0.05225 | 0.28801 | 111600
5420 | 8 | 226 | 19 | 1 | 0 | 0.25941 | 111400
5421 | 8 | 226 | 20 | 1 | 0 | 0.42883 | 111200
5422 | 8 | 226 | 21 | 0 | 0 | 0.37214 | 111200
5423 | 8 | 226 | 22 | 0 | 0 | 0.31118 | 111200
5424 | 8 | 226 | 23 | 0 | 0 | 0.20727 | 111200
5425 | 8 | 227 | 0 | 0 | 0 | 0.23584 | 111200
5426 | 8 | 227 | 1 | 0 | 0 | 0.21681 | 111200
5427 | 8 | 227 | 2 | 0 | 0 | 0.22353 | 111200
5428 | 8 | 227 | 3 | 0 | 0 | 0.19726 | 111200
5429 | 8 | 227 | 4 | 0 | 0 | 0.21216 | 111200
5430 | 8 | 227 | 5 | 0 | 0 | 0.14853 | 111200
5431 | 8 | 227 | 6 | 0 | 0.042394 | 0.17923 | 111200
5432 | 8 | 227 | 7 | 1 | 0.20056 | 0.18599 | 111000
5433 | 8 | 227 | 8 | 1 | 0.3862 | 0.25258 | 110800
5434 | 8 | 227 | 9 | 0 | 0.56496 | 0.28011 | 110800
5435 | 8 | 227 | 10 | 0 | 0.71171 | 0.42931 | 110800
5436 | 8 | 227 | 11 | 0 | 0.80765 | 0.4584 | 110800
5437 | 8 | 227 | 12 | 0 | 0.84098 | 0.61068 | 110800
5438 | 8 | 227 | 13 | 0 | 0.80765 | 0.81005 | 110800
5439 | 8 | 227 | 14 | 0 | 0.71171 | 0.6091 | 110800
5440 | 8 | 227 | 15 | 0 | 0.56496 | 0.74483 | 110800
5441 | 8 | 227 | 16 | 0 | 0.3862 | 0.70506 | 110800
5442 | 8 | 227 | 17 | 0 | 0.20056 | 0.36593 | 110800
5443 | 8 | 227 | 18 | 0 | 0.042394 | 0.56517 | 110800
5444 | 8 | 227 | 19 | 1 | 0 | 0.3904 | 110600
5445 | 8 | 227 | 20 | 1 | 0 | 0.32441 | 110400
5446 | 8 | 227 | 21 | 0 | 0 | 0.33589 | 110400
5447 | 8 | 227 | 22 | 0 | 0 | 0.29141 | 110400
5448 | 8 | 227 | 23 | 0 | 0 | 0.21654 | 110400
5449 | 8 | 228 | 0 | 0 | 0 | 0.24721 | 110400
5450 | 8 | 228 | 1 | 0 | 0 | 0.31392 | 110400
5451 | 8 | 228 | 2 | 0 | 0 | 0.24823 | 110400
5452 | 8 | 228 | 3 | 0 | 0 | 0.24199 | 110400
5453 | 8 | 228 | 4 | 0 | 0 | 0.25874 | 110400
5454 | 8 | 228 | 5 | 0 | 0 | 0.31414 | 110400
5455 | 8 | 228 | 6 | 0 | 0.055216 | 0.30693 | 110400
5456 | 8 | 228 | 7 | 1 | 0.26122 | 0.21129 | 110200
5457 | 8 | 228 | 8 | 1 | 0.503 | 0.19735 | 110000
5458 | 8 | 228 | 9 | 0 | 0.73583 | 0.25752 | 110000
5459 | 8 | 228 | 10 | 0 | 0.92696 | 0.27955 | 110000
5460 | 8 | 228 | 11 | 0 | 1 | 0.22746 | 110000
5461 | 8 | 228 | 12 | 0 | 1 | 0.26606 | 110000
5462 | 8 | 228 | 13 | 0 | 1 | 0.3112 | 110000
5463 | 8 | 228 | 14 | 0 | 0.92696 | 0.3012 | 110000
5464 | 8 | 228 | 15 | 0 | 0.73583 | 0.36695 | 110000
5465 | 8 | 228 | 16 | 0 | 0.503 | 0.40772 | 110000
5466 | 8 | 228 | 17 | 0 | 0.26122 | 0.52501 | 110000
5467 | 8 | 228 | 18 | 0 | 0.055216 | 0.49928 | 110000
5468 | 8 | 228 | 19 | 1 | 0 | 0.49752 | 109800
5469 | 8 | 228 | 20 | 1 | 0 | 0.45683 | 109600
5470 | 8 | 228 | 21 | 0 | 0 | 0.62689 | 109600
5471 | 8 | 228 | 22 | 0 | 0 | 0.44999 | 109600
5472 | 8 | 228 | 23 | 0 | 0 | 0.42707 | 109600
5473 | 8 | 229 | 0 | 0 | 0 | 0.33195 | 109600
5474 | 8 | 229 | 1 | 0 | 0 | 0.4071 | 109600
5475 | 8 | 229 | 2 | 0 | 0 | 0.29608 | 109600
5476 | 8 | 229 | 3 | 0 | 0 | 0.17429 | 109600
5477 | 8 | 229 | 4 | 0 | 0 | 0.19059 | 109600
5478 | 8 | 229 | 5 | 0 | 0 | 0.29936 | 109600
5479 | 8 | 229 | 6 | 0 | 0.052246 | 0.28335 | 109600
5480 | 8 | 229 | 7 | 1 | 0.24717 | 0.23991 | 109400
5481 | 8 | 229 | 8 | 1 | 0.47594 | 0.16338 | 109200
5482 | 8 | 229 | 9 | 0 | 0.69625 | 0.17649 | 109200
5483 | 8 | 229 | 10 | 0 | 0.8771 | 0.12654 | 109200
5484 | 8 | 229 | 11 | 0 | 0.99534 | 0.11922 | 109200
5485 | 8 | 229 | 12 | 0 | 1 | 0.11679 | 109200
5486 | 8 | 229 | 13 | 0 | 0.99534 | 0.14971 | 109200
5487 | 8 | 229 | 14 | 0 | 0.8771 | 0.13539 | 109200
5488 | 8 | 229 | 15 | 0 | 0.69625 | 0.19641 | 109200
5489 | 8 | 229 | 16 | 0 | 0.47594 | 0.18857 | 109200
5490 | 8 | 229 | 17 | 0 | 0.24717 | 0.22698 | 109200
5491 | 8 | 229 | 18 | 0 | 0.052246 | 0.31472 | 109200
5492 | 8 | 229 | 19 | 1 | 0 | 0.39989 | 109000
5493 | 8 | 229 | 20 | 1 | 0 | 0.45395 | 108800
5494 | 8 | 229 | 21 | 0 | 0 | 0.51339 | 108800
5495 | 8 | 229 | 22 | 0 | 0 | 0.51641 | 108800
5496 | 8 | 229 | 23 | 0 | 0 | 0.50733 | 108800
5497 | 8 | 230 | 0 | 0 | 0 | 0.51017 | 108800
5498 | 8 | 230 | 1 | 0 | 0 | 0.44938 | 108800
5499 | 8 | 230 | 2 | 0 | 0 | 0.33263 | 108800
5500 | 8 | 230 | 3 | 0 | 0 | 0.34373 | 108800
5501 | 8 | 230 | 4 | 0 | 0 | 0.45817 | 108800
5502 | 8 | 230 | 5 | 0 | 0 | 0.32842 | 108800
5503 | 8 | 230 | 6 | 0 | 0.040829 | 0.34767 | 108800
5504 | 8 | 230 | 7 | 1 | 0.19316 | 0.56966 | 108600
5505 | 8 | 230 | 8 | 1 | 0.37194 | 0.27405 | 108400
5506 | 8 | 230 | 9 | 0 | 0.5441 | 0.25414 | 108400
5507 | 8 | 230 | 10 | 0 | 0.68544 | 0.36723 | 108400
5508 | 8 | 230 | 11 | 0 | 0.77784 | 0.57681 | 108400
5509 | 8 | 230 | 12 | 0 | 0.80993 | 0.61123 | 108400
5510 | 8 | 230 | 13 | 0 | 0.77784 | 0.69033 | 108400
5511 | 8 | 230 | 14 | 0 | 0.68544 | 0.6217 | 108400
5512 | 8 | 230 | 15 | 0 | 0.5441 | 0.82227 | 108400
5513 | 8 | 230 | 16 | 0 | 0.37194 | 0.82697 | 108400
5514 | 8 | 230 | 17 | 0 | 0.19316 | 1 | 108400
5515 | 8 | 230 | 18 | 0 | 0.040829 | 0.95845 | 108400
5516 | 8 | 230 | 19 | 1 | 0 | 1 | 108200
5517 | 8 | 230 | 20 | 1 | 0 | 1 | 108000
5518 | 8 | 230 | 21 | 0 | 0 | 0.9854 | 108000
5519 | 8 | 230 | 22 | 0 | 0 | 1 | 108000
5520 | 8 | 230 | 23 | 0 | 0 | 1 | 108000
5521 | 8 | 231 | 0 | 0 | 0 | 1 | 108000
5522 | 8 | 231 | 1 | 0 | 0 | 1 | 108000
5523 | 8 | 231 | 2 | 0 | 0 | 0.96404 | 108000
5524 | 8 | 231 | 3 | 0 | 0 | 0.73473 | 108000
5525 | 8 | 231 | 4 | 0 | 0 | 0.91902 | 108000
5526 | 8 | 231 | 5 | 0 | 0 | 0.78587 | 108000
5527 | 8 | 231 | 6 | 0 | 0.047137 | 0.90245 | 108000
5528 | 8 | 231 | 7 | 1 | 0.223 | 0.56448 | 107800
5529 | 8 | 231 | 8 | 1 | 0.4294 | 0.64071 | 107600
5530 | 8 | 231 | 9 | 0 | 0.62817 | 0.92021 | 107600
5531 | 8 | 231 | 10 | 0 | 0.79134 | 0.55532 | 107600
5532 | 8 | 231 | 11 | 0 | 0.89801 | 0.4322 | 107600
5533 | 8 | 231 | 12 | 0 | 0.93507 | 0.43722 | 107600
5534 | 8 | 231 | 13 | 0 | 0.89801 | 0.79422 | 107600
5535 | 8 | 231 | 14 | 0 | 0.79134 | 0.72509 | 107600
5536 | 8 | 231 | 15 | 0 | 0.62817 | 0.77739 | 107600
5537 | 8 | 231 | 16 | 0 | 0.4294 | 0.75343 | 107600
5538 | 8 | 231 | 17 | 0 | 0.223 | 0.58156 | 107600
5539 | 8 | 231 | 18 | 0 | 0.047137 | 0.61405 | 107600
5540 | 8 | 231 | 19 | 1 | 0 | 0.66838 | 107400
5541 | 8 | 231 | 20 | 1 | 0 | 0.52757 | 107200
5542 | 8 | 231 | 21 | 0 | 0 | 0.50018 | 107200
5543 | 8 | 231 | 22 | 0 | 0 | 0.39443 | 107200
5544 | 8 | 231 | 23 | 0 | 0 | 0.41871 | 107200
5545 | 8 | 232 | 0 | 0 | 0 | 0.33783 | 107200
5546 | 8 | 232 | 1 | 0 | 0 | 0.37073 | 107200
5547 | 8 | 232 | 2 | 0 | 0 | 0.38245 | 107200
5548 | 8 | 232 | 3 | 0 | 0 | 0.34178 | 107200
5549 | 8 | 232 | 4 | 0 | 0 | 0.45438 | 107200
5550 | 8 | 232 | 5 | 0 | 0 | 0.41964 | 107200
5551 | 8 | 232 | 6 | 0 | 0.047307 | 0.42223 | 107200
5552 | 8 | 232 | 7 | 1 | 0.22381 | 0.38665 | 107000
5553 | 8 | 232 | 8 | 1 | 0.43095 | 0.4497 | 106800
5554 | 8 | 232 | 9 | 0 | 0.63043 | 0.36138 | 106800
5555 | 8 | 232 | 10 | 0 | 0.79419 | 0.25446 | 106800
5556 | 8 | 232 | 11 | 0 | 0.90125 | 0.44471 | 106800
5557 | 8 | 232 | 12 | 0 | 0.93844 | 0.36486 | 106800
5558 | 8 | 232 | 13 | 0 | 0.90125 | 0.32066 | 106800
5559 | 8 | 232 | 14 | 0 | 0.79419 | 0.17971 | 106800
5560 | 8 | 232 | 15 | 0 | 0.63043 | 0.15879 | 106800
5561 | 8 | 232 | 16 | 0 | 0.43095 | 0.23502 | 106800
5562 | 8 | 232 | 17 | 0 | 0.22381 | 0.19773 | 106800
5563 | 8 | 232 | 18 | 0 | 0.047307 | 0.28194 | 106800
5564 | 8 | 232 | 19 | 1 | 0 | 0.22912 | 106600
5565 | 8 | 232 | 20 | 1 | 0 | 0.33562 | 106400
5566 | 8 | 232 | 21 | 0 | 0 | 0.23702 | 106400
5567 | 8 | 232 | 22 | 0 | 0 | 0.30995 | 106400
5568 | 8 | 232 | 23 | 0 | 0 | 0.23336 | 106400
5569 | 8 | 233 | 0 | 0 | 0 | 0.29976 | 106400
5570 | 8 | 233 | 1 | 0 | 0 | 0.32624 | 106400
5571 | 8 | 233 | 2 | 0 | 0 | 0.54033 | 106400
5572 | 8 | 233 | 3 | 0 | 0 | 0.87037 | 106400
5573 | 8 | 233 | 4 | 0 | 0 | 0.83109 | 106400
5574 | 8 | 233 | 5 | 0 | 0 | 1 | 106400
5575 | 8 | 233 | 6 | 0 | 0.049815 | 1 | 106400
5576 | 8 | 233 | 7 | 1 | 0.23567 | 0.91347 | 106200
5577 | 8 | 233 | 8 | 1 | 0.4538 | 0.88993 | 106000
5578 | 8 | 233 | 9 | 0 | 0.66386 | 0.7194 | 106000
5579 | 8 | 233 | 10 | 0 | 0.8363 | 0.73276 | 106000
5580 | 8 | 233 | 11 | 0 | 0.94903 | 0.55957 | 106000
5581 | 8 | 233 | 12 | 0 | 0.9882 | 0.67591 | 106000
5582 | 8 | 233 | 13 | 0 | 0.94903 | 0.38068 | 106000
5583 | 8 | 233 | 14 | 0 | 0.8363 | 0.27764 | 106000
5584 | 8 | 233 | 15 | 0 | 0.66386 | 0.22328 | 106000
5585 | 8 | 233 | 16 | 0 | 0.4538 | 0.23836 | 106000
5586 | 8 | 233 | 17 | 0 | 0.23567 | 0.26162 | 106000
5587 | 8 | 233 | 18 | 0 | 0.049815 | 0.39807 | 106000
5588 | 8 | 233 | 19 | 1 | 0 | 0.51238 | 105800
5589 | 8 | 233 | 20 | 1 | 0 | 0.42775 | 105600
5590 | 8 | 233 | 21 | 0 | 0 | 0.44083 | 105600
5591 | 8 | 233 | 22 | 0 | 0 | 0.36952 | 105600
5592 | 8 | 233 | 23 | 0 | 0 | 0.30247 | 105600
5593 | 8 | 234 | 0 | 0 | 0 | 0.20948 | 105600
5594 | 8 | 234 | 1 | 0 | 0 | 0.16348 | 105600
5595 | 8 | 234 | 2 | 0 | 0 | 0.15739 | 105600
5596 | 8 | 234 | 3 | 0 | 0 | 0.20486 | 105600
5597 | 8 | 234 | 4 | 0 | 0 | 0.19517 | 105600
5598 | 8 | 234 | 5 | 0 | 0 | 0.24059 | 105600
5599 | 8 | 234 | 6 | 0 | 0.052005 | 0.25986 | 105600
5600 | 8 | 234 | 7 | 1 | 0.24603 | 0.36118 | 105400
5601 | 8 | 234 | 8 | 1 | 0.47375 | 0.46703 | 105200
5602 | 8 | 234 | 9 | 0 | 0.69304 | 0.52928 | 105200
5603 | 8 | 234 | 10 | 0 | 0.87306 | 0.37883 | 105200
5604 | 8 | 234 | 11 | 0 | 0.99076 | 0.53898 | 105200
5605 | 8 | 234 | 12 | 0 | 1 | 0.5304 | 105200
5606 | 8 | 234 | 13 | 0 | 0.99076 | 0.50757 | 105200
5607 | 8 | 234 | 14 | 0 | 0.87306 | 0.30108 | 105200
5608 | 8 | 234 | 15 | 0 | 0.69304 | 0.42446 | 105200
5609 | 8 | 234 | 16 | 0 | 0.47375 | 0.6791 | 105200
5610 | 8 | 234 | 17 | 0 | 0.24603 | 0.92521 | 105200
5611 | 8 | 234 | 18 | 0 | 0.052005 | 1 | 105200
5612 | 8 | 234 | 19 | 1 | 0 | 1 | 105000
5613 | 8 | 234 | 20 | 1 | 0 | 0.89515 | 104800
5614 | 8 | 234 | 21 | 0 | 0 | 0.57054 | 104800
5615 | 8 | 234 | 22 | 0 | 0 | 0.45686 | 104800
5616 | 8 | 234 | 23 | 0 | 0 | 0.4422 | 104800
5617 | 8 | 235 | 0 | 0 | 0 | 0.31382 | 104800
5618 | 8 | 235 | 1 | 0 | 0 | 0.4032 | 104800
5619 | 8 | 235 | 2 | 0 | 0 | 0.46177 | 104800
5620 | 8 | 235 | 3 | 0 | 0 | 0.4479 | 104800
5621 | 8 | 235 | 4 | 0 | 0 | 0.41122 | 104800
5622 | 8 | 235 | 5 | 0 | 0 | 0.47182 | 104800
5623 | 8 | 235 | 6 | 0 | 0.048975 | 0.44526 | 104800
5624 | 8 | 235 | 7 | 1 | 0.2317 | 0.41248 | 104600
5625 | 8 | 235 | 8 | 1 | 0.44615 | 0.53354 | 104400
5626 | 8 | 235 | 9 | 0 | 0.65266 | 0.42676 | 104400
5627 | 8 | 235 | 10 | 0 | 0.82219 | 0.47411 | 104400
5628 | 8 | 235 | 11 | 0 | 0.93303 | 0.44425 | 104400
5629 | 8 | 235 | 12 | 0 | 0.97153 | 0.50909 | 104400
5630 | 8 | 235 | 13 | 0 | 0.93303 | 0.54098 | 104400
5631 | 8 | 235 | 14 | 0 | 0.82219 | 0.54372 | 104400
5632 | 8 | 235 | 15 | 0 | 0.65266 | 0.77959 | 104400
5633 | 8 | 235 | 16 | 0 | 0.44615 | 0.55241 | 104400
5634 | 8 | 235 | 17 | 0 | 0.2317 | 0.48763 | 104400
5635 | 8 | 235 | 18 | 0 | 0.048975 | 0.45695 | 104400
5636 | 8 | 235 | 19 | 1 | 0 | 0.79799 | 104200
5637 | 8 | 235 | 20 | 1 | 0 | 0.71271 | 104000
5638 | 8 | 235 | 21 | 0 | 0 | 0.64452 | 104000
5639 | 8 | 235 | 22 | 0 | 0 | 0.6268 | 104000
5640 | 8 | 235 | 23 | 0 | 0 | 0.56989 | 104000
5641 | 8 | 236 | 0 | 0 | 0 | 0.76872 | 104000
5642 | 8 | 236 | 1 | 0 | 0 | 1 | 104000
5643 | 8 | 236 | 2 | 0 | 0 | 1 | 104000
5644 | 8 | 236 | 3 | 0 | 0 | 1 | 104000
5645 | 8 | 236 | 4 | 0 | 0 | 1 | 104000
5646 | 8 | 236 | 5 | 0 | 0 | 1 | 104000
5647 | 8 | 236 | 6 | 0 | 0.048388 | 1 | 104000
5648 | 8 | 236 | 7 | 1 | 0.22892 | 1 | 103800
5649 | 8 | 236 | 8 | 1 | 0.44079 | 1 | 103600
5650 | 8 | 236 | 9 | 0 | 0.64483 | 1 | 103600
5651 | 8 | 236 | 10 | 0 | 0.81233 | 1 | 103600
5652 | 8 | 236 | 11 | 0 | 0.92184 | 1 | 103600
5653 | 8 | 236 | 12 | 0 | 0.95988 | 1 | 103600
5654 | 8 | 236 | 13 | 0 | 0.92184 | 1 | 103600
5655 | 8 | 236 | 14 | 0 | 0.81233 | 1 | 103600
5656 | 8 | 236 | 15 | 0 | 0.64483 | 1 | 103600
5657 | 8 | 236 | 16 | 0 | 0.44079 | 1 | 103600
5658 | 8 | 236 | 17 | 0 | 0.22892 | 0.93489 | 103600
5659 | 8 | 236 | 18 | 0 | 0.048388 | 1 | 103600
5660 | 8 | 236 | 19 | 1 | 0 | 1 | 103400
5661 | 8 | 236 | 20 | 1 | 0 | 0.96069 | 103200
5662 | 8 | 236 | 21 | 0 | 0 | 0.82439 | 103200
5663 | 8 | 236 | 22 | 0 | 0 | 0.85664 | 103200
5664 | 8 | 236 | 23 | 0 | 0 | 1 | 103200
5665 | 8 | 237 | 0 | 0 | 0 | 0.92498 | 103200
5666 | 8 | 237 | 1 | 0 | 0 | 0.76699 | 103200
5667 | 8 | 237 | 2 | 0 | 0 | 0.66844 | 103200
5668 | 8 | 237 | 3 | 0 | 0 | 0.71552 | 103200
5669 | 8 | 237 | 4 | 0 | 0 | 0.9532 | 103200
5670 | 8 | 237 | 5 | 0 | 0 | 0.9236 | 103200
5671 | 8 | 237 | 6 | 0 | 0.04362 | 0.67235 | 103200
5672 | 8 | 237 | 7 | 1 | 0.20636 | 0.87037 | 103000
5673 | 8 | 237 | 8 | 1 | 0.39736 | 0.55293 | 102800
5674 | 8 | 237 | 9 | 0 | 0.58129 | 0.85586 | 102800
5675 | 8 | 237 | 10 | 0 | 0.73229 | 0.80086 | 102800
5676 | 8 | 237 | 11 | 0 | 0.831 | 0.80927 | 102800
5677 | 8 | 237 | 12 | 0 | 0.8653 | 0.58297 | 102800
5678 | 8 | 237 | 13 | 0 | 0.831 | 0.66746 | 102800
5679 | 8 | 237 | 14 | 0 | 0.73229 | 0.60752 | 102800
5680 | 8 | 237 | 15 | 0 | 0.58129 | 0.68173 | 102800
5681 | 8 | 237 | 16 | 0 | 0.39736 | 0.5581 | 102800
5682 | 8 | 237 | 17 | 0 | 0.20636 | 0.6395 | 102800
5683 | 8 | 237 | 18 | 0 | 0.04362 | 1 | 102800
5684 | 8 | 237 | 19 | 1 | 0 | 1 | 102600
5685 | 8 | 237 | 20 | 1 | 0 | 1 | 102400
5686 | 8 | 237 | 21 | 0 | 0 | 1 | 102400
5687 | 8 | 237 | 22 | 0 | 0 | 1 | 102400
5688 | 8 | 237 | 23 | 0 | 0 | 1 | 102400
5689 | 8 | 238 | 0 | 0 | 0 | 0.92433 | 102400
5690 | 8 | 238 | 1 | 0 | 0 | 1 | 102400
5691 | 8 | 238 | 2 | 0 | 0 | 1 | 102400
5692 | 8 | 238 | 3 | 0 | 0 | 0.98505 | 102400
5693 | 8 | 238 | 4 | 0 | 0 | 1 | 102400
5694 | 8 | 238 | 5 | 0 | 0 | 1 | 102400
5695 | 8 | 238 | 6 | 0 | 0.047689 | 1 | 102400
5696 | 8 | 238 | 7 | 1 | 0.22561 | 1 | 102200
5697 | 8 | 238 | 8 | 1 | 0.43443 | 1 | 102000
5698 | 8 | 238 | 9 | 0 | 0.63552 | 1 | 102000
5699 | 8 | 238 | 10 | 0 | 0.8006 | 0.81761 | 102000
5700 | 8 | 238 | 11 | 0 | 0.90853 | 0.87643 | 102000
5701 | 8 | 238 | 12 | 0 | 0.94602 | 0.67487 | 102000
5702 | 8 | 238 | 13 | 0 | 0.90853 | 0.76573 | 102000
5703 | 8 | 238 | 14 | 0 | 0.8006 | 0.85685 | 102000
5704 | 8 | 238 | 15 | 0 | 0.63552 | 0.79507 | 102000
5705 | 8 | 238 | 16 | 0 | 0.43443 | 0.61104 | 102000
5706 | 8 | 238 | 17 | 0 | 0.22561 | 0.52396 | 102000
5707 | 8 | 238 | 18 | 0 | 0.047689 | 0.37508 | 102000
5708 | 8 | 238 | 19 | 1 | 0 | 0.27984 | 101800
5709 | 8 | 238 | 20 | 1 | 0 | 0.23752 | 101600
5710 | 8 | 238 | 21 | 0 | 0 | 0.21368 | 101600
5711 | 8 | 238 | 22 | 0 | 0 | 0.19203 | 101600
5712 | 8 | 238 | 23 | 0 | 0 | 0.11812 | 101600
5713 | 8 | 239 | 0 | 0 | 0 | 0.12444 | 101600
5714 | 8 | 239 | 1 | 0 | 0 | 0.14185 | 101600
5715 | 8 | 239 | 2 | 0 | 0 | 0.097326 | 101600
5716 | 8 | 239 | 3 | 0 | 0 | 0.082866 | 101600
5717 | 8 | 239 | 4 | 0 | 0 | 0.11676 | 101600
5718 | 8 | 239 | 5 | 0 | 0 | 0.21733 | 101600
5719 | 8 | 239 | 6 | 0 | 0.048901 | 0.20725 | 101600
5720 | 8 | 239 | 7 | 1 | 0.23135 | 0.32284 | 101400
5721 | 8 | 239 | 8 | 1 | 0.44547 | 0.3489 | 101200
5722 | 8 | 239 | 9 | 0 | 0.65168 | 0.26731 | 101200
5723 | 8 | 239 | 10 | 0 | 0.82095 | 0.24478 | 101200
5724 | 8 | 239 | 11 | 0 | 0.93162 | 0.30562 | 101200
5725 | 8 | 239 | 12 | 0 | 0.97006 | 0.28186 | 101200
5726 | 8 | 239 | 13 | 0 | 0.93162 | 0.19452 | 101200
5727 | 8 | 239 | 14 | 0 | 0.82095 | 0.31091 | 101200
5728 | 8 | 239 | 15 | 0 | 0.65168 | 0.30221 | 101200
5729 | 8 | 239 | 16 | 0 | 0.44547 | 0.35797 | 101200
5730 | 8 | 239 | 17 | 0 | 0.23135 | 0.35706 | 101200
5731 | 8 | 239 | 18 | 0 | 0.048901 | 0.24997 | 101200
5732 | 8 | 239 | 19 | 1 | 0 | 0.17511 | 101000
5733 | 8 | 239 | 20 | 1 | 0 | 0.10905 | 100800
5734 | 8 | 239 | 21 | 0 | 0 | 0.13534 | 100800
5735 | 8 | 239 | 22 | 0 | 0 | 0.092664 | 100800
5736 | 8 | 239 | 23 | 0 | 0 | 0.1001 | 100800
5737 | 8 | 240 | 0 | 0 | 0 | 0.12167 | 100800
5738 | 8 | 240 | 1 | 0 | 0 | 0.1407 | 100800
5739 | 8 | 240 | 2 | 0 | 0 | 0.18628 | 100800
5740 | 8 | 240 | 3 | 0 | 0 | 0.22205 | 100800
5741 | 8 | 240 | 4 | 0 | 0 | 0.21958 | 100800
5742 | 8 | 240 | 5 | 0 | 0 | 0.2332 | 100800
5743 | 8 | 240 | 6 | 0 | 0.054837 | 0.35179 | 100800
5744 | 8 | 240 | 7 | 1 | 0.25943 | 0.53567 | 100600
5745 | 8 | 240 | 8 | 1 | 0.49954 | 0.52066 | 100400
5746 | 8 | 240 | 9 | 0 | 0.73077 | 0.5255 | 100400
5747 | 8 | 240 | 10 | 0 | 0.9206 | 0.69871 | 100400
5748 | 8 | 240 | 11 | 0 | 1 | 0.87591 | 100400
5749 | 8 | 240 | 12 | 0 | 1 | 0.7105 | 100400
5750 | 8 | 240 | 13 | 0 | 1 | 0.88323 | 100400
5751 | 8 | 240 | 14 | 0 | 0.9206 | 0.85595 | 100400
5752 | 8 | 240 | 15 | 0 | 0.73077 | 0.76014 | 100400
5753 | 8 | 240 | 16 | 0 | 0.49954 | 0.91132 | 100400
5754 | 8 | 240 | 17 | 0 | 0.25943 | 0.90262 | 100400
5755 | 8 | 240 | 18 | 0 | 0.054837 | 0.70426 | 100400
5756 | 8 | 240 | 19 | 1 | 0 | 0.76996 | 100200
5757 | 8 | 240 | 20 | 1 | 0 | 0.95279 | 100000
5758 | 8 | 240 | 21 | 0 | 0 | 1 | 100000
5759 | 8 | 240 | 22 | 0 | 0 | 0.85062 | 100000
5760 | 8 | 240 | 23 | 0 | 0 | 0.60703 | 100000
5761 | 8 | 241 | 0 | 0 | 0 | 0.61672 | 100000
5762 | 8 | 241 | 1 | 0 | 0 | 0.65723 | 100000
5763 | 8 | 241 | 2 | 0 | 0 | 0.58336 | 100000
5764 | 8 | 241 | 3 | 0 | 0 | 0.59252 | 100000
5765 | 8 | 241 | 4 | 0 | 0 | 0.5816 | 100000
5766 | 8 | 241 | 5 | 0 | 0 | 0.64628 | 100000
5767 | 8 | 241 | 6 | 0 | 0.038134 | 0.8354 | 100000
5768 | 8 | 241 | 7 | 1 | 0.18041 | 0.70927 | 99800
5769 | 8 | 241 | 8 | 1 | 0.34738 | 0.48649 | 99600
5770 | 8 | 241 | 9 | 0 | 0.50818 | 0.51085 | 99600
5771 | 8 | 241 | 10 | 0 | 0.64019 | 0.71881 | 99600
5772 | 8 | 241 | 11 | 0 | 0.72649 | 0.56128 | 99600
5773 | 8 | 241 | 12 | 0 | 0.75647 | 0.50919 | 99600
5774 | 8 | 241 | 13 | 0 | 0.72649 | 0.65881 | 99600
5775 | 8 | 241 | 14 | 0 | 0.64019 | 0.72744 | 99600
5776 | 8 | 241 | 15 | 0 | 0.50818 | 0.54309 | 99600
5777 | 8 | 241 | 16 | 0 | 0.34738 | 0.48289 | 99600
5778 | 8 | 241 | 17 | 0 | 0.18041 | 0.42667 | 99600
5779 | 8 | 241 | 18 | 0 | 0.038134 | 0.5148 | 99600
5780 | 8 | 241 | 19 | 1 | 0 | 0.47464 | 99400
5781 | 8 | 241 | 20 | 1 | 0 | 0.52455 | 99200
5782 | 8 | 241 | 21 | 0 | 0 | 0.53992 | 99200
5783 | 8 | 241 | 22 | 0 | 0 | 0.42763 | 99200
5784 | 8 | 241 | 23 | 0 | 0 | 0.44875 | 99200
5785 | 8 | 242 | 0 | 0 | 0 | 0.56708 | 99200
5786 | 8 | 242 | 1 | 0 | 0 | 0.42508 | 99200
5787 | 8 | 242 | 2 | 0 | 0 | 0.45632 | 99200
5788 | 8 | 242 | 3 | 0 | 0 | 0.3863 | 99200
5789 | 8 | 242 | 4 | 0 | 0 | 0.30862 | 99200
5790 | 8 | 242 | 5 | 0 | 0 | 0.26212 | 99200
5791 | 8 | 242 | 6 | 0 | 0.044063 | 0.2256 | 99200
5792 | 8 | 242 | 7 | 1 | 0.20846 | 0.18834 | 99000
5793 | 8 | 242 | 8 | 1 | 0.4014 | 0.36297 | 98800
5794 | 8 | 242 | 9 | 0 | 0.5872 | 0.38644 | 98800
5795 | 8 | 242 | 10 | 0 | 0.73973 | 0.31837 | 98800
5796 | 8 | 242 | 11 | 0 | 0.83945 | 0.30811 | 98800
5797 | 8 | 242 | 12 | 0 | 0.87409 | 0.44079 | 98800
5798 | 8 | 242 | 13 | 0 | 0.83945 | 0.48539 | 98800
5799 | 8 | 242 | 14 | 0 | 0.73973 | 0.64519 | 98800
5800 | 8 | 242 | 15 | 0 | 0.5872 | 0.42198 | 98800
5801 | 8 | 242 | 16 | 0 | 0.4014 | 0.41025 | 98800
5802 | 8 | 242 | 17 | 0 | 0.20846 | 0.32973 | 98800
5803 | 8 | 242 | 18 | 0 | 0.044063 | 0.25401 | 98800
5804 | 8 | 242 | 19 | 1 | 0 | 0.22379 | 98600
5805 | 8 | 242 | 20 | 1 | 0 | 0.15011 | 98400
5806 | 8 | 242 | 21 | 0 | 0 | 0.13884 | 98400
5807 | 8 | 242 | 22 | 0 | 0 | 0.17059 | 98400
5808 | 8 | 242 | 23 | 0 | 0 | 0.11969 | 98400
5809 | 8 | 243 | 0 | 0 | 0 | 0.15352 | 98400
5810 | 8 | 243 | 1 | 0 | 0 | 0.11355 | 98400
5811 | 8 | 243 | 2 | 0 | 0 | 0.15744 | 98400
5812 | 8 | 243 | 3 | 0 | 0 | 0.17409 | 98400
5813 | 8 | 243 | 4 | 0 | 0 | 0.15419 | 98400
5814 | 8 | 243 | 5 | 0 | 0 | 0.18696 | 98400
5815 | 8 | 243 | 6 | 0 | 0.045075 | 0.33627 | 98400
5816 | 8 | 243 | 7 | 1 | 0.21325 | 0.29492 | 98200
5817 | 8 | 243 | 8 | 1 | 0.41062 | 0.39141 | 98000
5818 | 8 | 243 | 9 | 0 | 0.60069 | 0.47863 | 98000
5819 | 8 | 243 | 10 | 0 | 0.75672 | 0.42901 | 98000
5820 | 8 | 243 | 11 | 0 | 0.85873 | 0.56562 | 98000
5821 | 8 | 243 | 12 | 0 | 0.89417 | 0.59731 | 98000
5822 | 8 | 243 | 13 | 0 | 0.85873 | 0.54572 | 98000
5823 | 8 | 243 | 14 | 0 | 0.75672 | 1 | 98000
5824 | 8 | 243 | 15 | 0 | 0.60069 | 1 | 98000
5825 | 8 | 243 | 16 | 0 | 0.41062 | 1 | 98000
5826 | 8 | 243 | 17 | 0 | 0.21325 | 1 | 98000
5827 | 8 | 243 | 18 | 0 | 0.045075 | 1 | 98000
5828 | 8 | 243 | 19 | 1 | 0 | 1 | 97800
5829 | 8 | 243 | 20 | 1 | 0 | 1 | 97600
5830 | 8 | 243 | 21 | 0 | 0 | 1 | 97600
5831 | 8 | 243 | 22 | 0 | 0 | 0.88784 | 97600
5832 | 8 | 243 | 23 | 0 | 0 | 0.62758 | 97600
5833 | 9 | 244 | 0 | 0 | 0 | 0.41525 | 97600
5834 | 9 | 244 | 1 | 0 | 0 | 0.31439 | 97600
5835 | 9 | 244 | 2 | 0 | 0 | 0.3052 | 97600
5836 | 9 | 244 | 3 | 0 | 0 | 0.2966 | 97600
5837 | 9 | 244 | 4 | 0 | 0 | 0.40077 | 97600
5838 | 9 | 244 | 5 | 0 | 0 | 0.40036 | 97600
5839 | 9 | 244 | 6 | 0 | 0.0084 | 0.41301 | 97600
5840 | 9 | 244 | 7 | 1 | 0.21008 | 0.5119 | 97400
5841 | 9 | 244 | 8 | 1 | 0.47919 | 0.44634 | 97200
5842 | 9 | 244 | 9 | 0 | 0.74827 | 0.45877 | 97200
5843 | 9 | 244 | 10 | 0 | 0.97352 | 0.57112 | 97200
5844 | 9 | 244 | 11 | 0 | 1 | 0.56151 | 97200
5845 | 9 | 244 | 12 | 0 | 1 | 0.4313 | 97200
5846 | 9 | 244 | 13 | 0 | 1 | 0.3621 | 97200
5847 | 9 | 244 | 14 | 0 | 0.97352 | 0.3316 | 97200
5848 | 9 | 244 | 15 | 0 | 0.74827 | 0.28761 | 97200
5849 | 9 | 244 | 16 | 0 | 0.47919 | 0.45348 | 97200
5850 | 9 | 244 | 17 | 0 | 0.21008 | 0.52755 | 97200
5851 | 9 | 244 | 18 | 0 | 0.0084 | 0.47729 | 97200
5852 | 9 | 244 | 19 | 1 | 0 | 0.35966 | 97000
5853 | 9 | 244 | 20 | 1 | 0 | 0.346 | 96800
5854 | 9 | 244 | 21 | 0 | 0 | 0.36129 | 96800
5855 | 9 | 244 | 22 | 0 | 0 | 0.24762 | 96800
5856 | 9 | 244 | 23 | 0 | 0 | 0.2406 | 96800
5857 | 9 | 245 | 0 | 0 | 0 | 0.38123 | 96800
5858 | 9 | 245 | 1 | 0 | 0 | 0.44531 | 96800
5859 | 9 | 245 | 2 | 0 | 0 | 0.4073 | 96800
5860 | 9 | 245 | 3 | 0 | 0 | 0.39571 | 96800
5861 | 9 | 245 | 4 | 0 | 0 | 0.43791 | 96800
5862 | 9 | 245 | 5 | 0 | 0 | 0.36116 | 96800
5863 | 9 | 245 | 6 | 0 | 0.007081 | 0.32829 | 96800
5864 | 9 | 245 | 7 | 1 | 0.17708 | 0.37417 | 96600
5865 | 9 | 245 | 8 | 1 | 0.40392 | 0.33473 | 96400
5866 | 9 | 245 | 9 | 0 | 0.63073 | 0.33449 | 96400
5867 | 9 | 245 | 10 | 0 | 0.8206 | 0.45857 | 96400
5868 | 9 | 245 | 11 | 0 | 0.94609 | 0.31692 | 96400
5869 | 9 | 245 | 12 | 0 | 0.98989 | 0.36077 | 96400
5870 | 9 | 245 | 13 | 0 | 0.94609 | 0.26599 | 96400
5871 | 9 | 245 | 14 | 0 | 0.8206 | 0.34196 | 96400
5872 | 9 | 245 | 15 | 0 | 0.63073 | 0.3711 | 96400
5873 | 9 | 245 | 16 | 0 | 0.40392 | 0.42141 | 96400
5874 | 9 | 245 | 17 | 0 | 0.17708 | 0.52365 | 96400
5875 | 9 | 245 | 18 | 0 | 0.007081 | 0.64475 | 96400
5876 | 9 | 245 | 19 | 1 | 0 | 0.51135 | 96200
5877 | 9 | 245 | 20 | 1 | 0 | 0.61545 | 96000
5878 | 9 | 245 | 21 | 0 | 0 | 0.75375 | 96000
5879 | 9 | 245 | 22 | 0 | 0 | 0.64698 | 96000
5880 | 9 | 245 | 23 | 0 | 0 | 0.38911 | 96000
5881 | 9 | 246 | 0 | 0 | 0 | 0.25988 | 96000
5882 | 9 | 246 | 1 | 0 | 0 | 0.28173 | 96000
5883 | 9 | 246 | 2 | 0 | 0 | 0.26187 | 96000
5884 | 9 | 246 | 3 | 0 | 0 | 0.40224 | 96000
5885 | 9 | 246 | 4 | 0 | 0 | 0.49573 | 96000
5886 | 9 | 246 | 5 | 0 | 0 | 0.38076 | 96000
5887 | 9 | 246 | 6 | 0 | 0.007394 | 0.50895 | 96000
5888 | 9 | 246 | 7 | 1 | 0.1849 | 0.65236 | 95800
5889 | 9 | 246 | 8 | 1 | 0.42175 | 0.72739 | 95600
5890 | 9 | 246 | 9 | 0 | 0.65858 | 0.84214 | 95600
5891 | 9 | 246 | 10 | 0 | 0.85683 | 1 | 95600
5892 | 9 | 246 | 11 | 0 | 0.98786 | 1 | 95600
5893 | 9 | 246 | 12 | 0 | 1 | 0.72423 | 95600
5894 | 9 | 246 | 13 | 0 | 0.98786 | 0.68036 | 95600
5895 | 9 | 246 | 14 | 0 | 0.85683 | 0.66577 | 95600
5896 | 9 | 246 | 15 | 0 | 0.65858 | 0.57956 | 95600
5897 | 9 | 246 | 16 | 0 | 0.42175 | 0.38938 | 95600
5898 | 9 | 246 | 17 | 0 | 0.1849 | 0.34622 | 95600
5899 | 9 | 246 | 18 | 0 | 0.007394 | 0.30672 | 95600
5900 | 9 | 246 | 19 | 1 | 0 | 0.24433 | 95400
5901 | 9 | 246 | 20 | 1 | 0 | 0.13561 | 95200
5902 | 9 | 246 | 21 | 0 | 0 | 0.17897 | 95200
5903 | 9 | 246 | 22 | 0 | 0 | 0.14481 | 95200
5904 | 9 | 246 | 23 | 0 | 0 | 0.1652 | 95200
5905 | 9 | 247 | 0 | 0 | 0 | 0.16704 | 95200
5906 | 9 | 247 | 1 | 0 | 0 | 0.3451 | 95200
5907 | 9 | 247 | 2 | 0 | 0 | 0.51475 | 95200
5908 | 9 | 247 | 3 | 0 | 0 | 0.56779 | 95200
5909 | 9 | 247 | 4 | 0 | 0 | 0.60829 | 95200
5910 | 9 | 247 | 5 | 0 | 0 | 0.65881 | 95200
5911 | 9 | 247 | 6 | 0 | 0.008917 | 0.56738 | 95200
5912 | 9 | 247 | 7 | 1 | 0.22299 | 0.66049 | 95000
5913 | 9 | 247 | 8 | 1 | 0.50863 | 0.67392 | 94800
5914 | 9 | 247 | 9 | 0 | 0.79426 | 0.75299 | 94800
5915 | 9 | 247 | 10 | 0 | 1 | 1 | 94800
5916 | 9 | 247 | 11 | 0 | 1 | 0.76019 | 94800
5917 | 9 | 247 | 12 | 0 | 1 | 0.54679 | 94800
5918 | 9 | 247 | 13 | 0 | 1 | 0.4555 | 94800
5919 | 9 | 247 | 14 | 0 | 1 | 0.63148 | 94800
5920 | 9 | 247 | 15 | 0 | 0.79426 | 0.70806 | 94800
5921 | 9 | 247 | 16 | 0 | 0.50863 | 0.97593 | 94800
5922 | 9 | 247 | 17 | 0 | 0.22299 | 1 | 94800
5923 | 9 | 247 | 18 | 0 | 0.008917 | 0.95181 | 94800
5924 | 9 | 247 | 19 | 1 | 0 | 1 | 94600
5925 | 9 | 247 | 20 | 1 | 0 | 1 | 94400
5926 | 9 | 247 | 21 | 0 | 0 | 1 | 94400
5927 | 9 | 247 | 22 | 0 | 0 | 1 | 94400
5928 | 9 | 247 | 23 | 0 | 0 | 1 | 94400
5929 | 9 | 248 | 0 | 0 | 0 | 1 | 94400
5930 | 9 | 248 | 1 | 0 | 0 | 1 | 94400
5931 | 9 | 248 | 2 | 0 | 0 | 1 | 94400
5932 | 9 | 248 | 3 | 0 | 0 | 1 | 94400
5933 | 9 | 248 | 4 | 0 | 0 | 1 | 94400
5934 | 9 | 248 | 5 | 0 | 0 | 1 | 94400
5935 | 9 | 248 | 6 | 0 | 0.007949 | 0.73582 | 94400
5936 | 9 | 248 | 7 | 1 | 0.1988 | 0.58692 | 94200
5937 | 9 | 248 | 8 | 1 | 0.45346 | 0.9683 | 94000
5938 | 9 | 248 | 9 | 0 | 0.7081 | 0.59478 | 94000
5939 | 9 | 248 | 10 | 0 | 0.92125 | 0.64458 | 94000
5940 | 9 | 248 | 11 | 0 | 1 | 0.59025 | 94000
5941 | 9 | 248 | 12 | 0 | 1 | 0.29899 | 94000
5942 | 9 | 248 | 13 | 0 | 1 | 0.30023 | 94000
5943 | 9 | 248 | 14 | 0 | 0.92125 | 0.20177 | 94000
5944 | 9 | 248 | 15 | 0 | 0.7081 | 0.29155 | 94000
5945 | 9 | 248 | 16 | 0 | 0.45346 | 0.28164 | 94000
5946 | 9 | 248 | 17 | 0 | 0.1988 | 0.40373 | 94000
5947 | 9 | 248 | 18 | 0 | 0.007949 | 0.31996 | 94000
5948 | 9 | 248 | 19 | 1 | 0 | 0.29278 | 93800
5949 | 9 | 248 | 20 | 1 | 0 | 0.3334 | 93600
5950 | 9 | 248 | 21 | 0 | 0 | 0.3559 | 93600
5951 | 9 | 248 | 22 | 0 | 0 | 0.37066 | 93600
5952 | 9 | 248 | 23 | 0 | 0 | 0.42237 | 93600
5953 | 9 | 249 | 0 | 0 | 0 | 0.22691 | 93600
5954 | 9 | 249 | 1 | 0 | 0 | 0.23657 | 93600
5955 | 9 | 249 | 2 | 0 | 0 | 0.25677 | 93600
5956 | 9 | 249 | 3 | 0 | 0 | 0.3113 | 93600
5957 | 9 | 249 | 4 | 0 | 0 | 0.26676 | 93600
5958 | 9 | 249 | 5 | 0 | 0 | 0.32101 | 93600
5959 | 9 | 249 | 6 | 0 | 0.007565 | 0.27512 | 93600
5960 | 9 | 249 | 7 | 1 | 0.18918 | 0.29931 | 93400
5961 | 9 | 249 | 8 | 1 | 0.43151 | 0.42887 | 93200
5962 | 9 | 249 | 9 | 0 | 0.67381 | 0.55987 | 93200
5963 | 9 | 249 | 10 | 0 | 0.87665 | 0.3516 | 93200
5964 | 9 | 249 | 11 | 0 | 1 | 0.36415 | 93200
5965 | 9 | 249 | 12 | 0 | 1 | 0.40804 | 93200
5966 | 9 | 249 | 13 | 0 | 1 | 0.46177 | 93200
5967 | 9 | 249 | 14 | 0 | 0.87665 | 0.46697 | 93200
5968 | 9 | 249 | 15 | 0 | 0.67381 | 0.42917 | 93200
5969 | 9 | 249 | 16 | 0 | 0.43151 | 0.36615 | 93200
5970 | 9 | 249 | 17 | 0 | 0.18918 | 0.34357 | 93200
5971 | 9 | 249 | 18 | 0 | 0.007565 | 0.35221 | 93200
5972 | 9 | 249 | 19 | 1 | 0 | 0.37752 | 93000
5973 | 9 | 249 | 20 | 1 | 0 | 0.26182 | 92800
5974 | 9 | 249 | 21 | 0 | 0 | 0.17696 | 92800
5975 | 9 | 249 | 22 | 0 | 0 | 0.13464 | 92800
5976 | 9 | 249 | 23 | 0 | 0 | 0.15749 | 92800
5977 | 9 | 250 | 0 | 0 | 0 | 0.20447 | 92800
5978 | 9 | 250 | 1 | 0 | 0 | 0.31199 | 92800
5979 | 9 | 250 | 2 | 0 | 0 | 0.26774 | 92800
5980 | 9 | 250 | 3 | 0 | 0 | 0.35382 | 92800
5981 | 9 | 250 | 4 | 0 | 0 | 0.331 | 92800
5982 | 9 | 250 | 5 | 0 | 0 | 0.57251 | 92800
5983 | 9 | 250 | 6 | 0 | 0.007729 | 0.46348 | 92800
5984 | 9 | 250 | 7 | 1 | 0.19328 | 0.45458 | 92600
5985 | 9 | 250 | 8 | 1 | 0.44086 | 0.40671 | 92400
5986 | 9 | 250 | 9 | 0 | 0.68842 | 0.52004 | 92400
5987 | 9 | 250 | 10 | 0 | 0.89565 | 0.88241 | 92400
5988 | 9 | 250 | 11 | 0 | 1 | 0.62037 | 92400
5989 | 9 | 250 | 12 | 0 | 1 | 0.51119 | 92400
5990 | 9 | 250 | 13 | 0 | 1 | 0.41515 | 92400
5991 | 9 | 250 | 14 | 0 | 0.89565 | 0.35188 | 92400
5992 | 9 | 250 | 15 | 0 | 0.68842 | 0.34236 | 92400
5993 | 9 | 250 | 16 | 0 | 0.44086 | 0.46768 | 92400
5994 | 9 | 250 | 17 | 0 | 0.19328 | 0.31808 | 92400
5995 | 9 | 250 | 18 | 0 | 0.007729 | 0.17652 | 92400
5996 | 9 | 250 | 19 | 1 | 0 | 0.1755 | 92200
5997 | 9 | 250 | 20 | 1 | 0 | 0.31535 | 92000
5998 | 9 | 250 | 21 | 0 | 0 | 0.33155 | 92000
5999 | 9 | 250 | 22 | 0 | 0 | 0.52325 | 92000
6000 | 9 | 250 | 23 | 0 | 0 | 0.47473 | 92000
6001 | 9 | 251 | 0 | 0 | 0 | 0.60012 | 92000
6002 | 9 | 251 | 1 | 0 | 0 | 0.52299 | 92000
6003 | 9 | 251 | 2 | 0 | 0 | 0.3713 | 92000
6004 | 9 | 251 | 3 | 0 | 0 | 0.53137 | 92000
6005 | 9 | 251 | 4 | 0 | 0 | 0.80982 | 92000
6006 | 9 | 251 | 5 | 0 | 0 | 0.91156 | 92000
6007 | 9 | 251 | 6 | 0 | 0.007665 | 0.55713 | 92000
6008 | 9 | 251 | 7 | 1 | 0.19169 | 0.38893 | 91800
6009 | 9 | 251 | 8 | 1 | 0.43723 | 0.37563 | 91600
6010 | 9 | 251 | 9 | 0 | 0.68275 | 0.41389 | 91600
6011 | 9 | 251 | 10 | 0 | 0.88828 | 0.32464 | 91600
6012 | 9 | 251 | 11 | 0 | 1 | 0.27345 | 91600
6013 | 9 | 251 | 12 | 0 | 1 | 0.30287 | 91600
6014 | 9 | 251 | 13 | 0 | 1 | 0.36269 | 91600
6015 | 9 | 251 | 14 | 0 | 0.88828 | 0.46362 | 91600
6016 | 9 | 251 | 15 | 0 | 0.68275 | 0.48746 | 91600
6017 | 9 | 251 | 16 | 0 | 0.43723 | 0.50154 | 91600
6018 | 9 | 251 | 17 | 0 | 0.19169 | 0.49704 | 91600
6019 | 9 | 251 | 18 | 0 | 0.007665 | 0.50129 | 91600
6020 | 9 | 251 | 19 | 1 | 0 | 0.45709 | 91400
6021 | 9 | 251 | 20 | 1 | 0 | 0.3995 | 91200
6022 | 9 | 251 | 21 | 0 | 0 | 0.43372 | 91200
6023 | 9 | 251 | 22 | 0 | 0 | 0.3935 | 91200
6024 | 9 | 251 | 23 | 0 | 0 | 0.52405 | 91200
6025 | 9 | 252 | 0 | 0 | 0 | 0.30756 | 91200
6026 | 9 | 252 | 1 | 0 | 0 | 0.21737 | 91200
6027 | 9 | 252 | 2 | 0 | 0 | 0.15993 | 91200
6028 | 9 | 252 | 3 | 0 | 0 | 0.19131 | 91200
6029 | 9 | 252 | 4 | 0 | 0 | 0.16684 | 91200
6030 | 9 | 252 | 5 | 0 | 0 | 0.15591 | 91200
6031 | 9 | 252 | 6 | 0 | 0.007054 | 0.15303 | 91200
6032 | 9 | 252 | 7 | 1 | 0.17641 | 0.19346 | 91000
6033 | 9 | 252 | 8 | 1 | 0.40239 | 0.25648 | 90800
6034 | 9 | 252 | 9 | 0 | 0.62835 | 0.18267 | 90800
6035 | 9 | 252 | 10 | 0 | 0.8175 | 0.21084 | 90800
6036 | 9 | 252 | 11 | 0 | 0.94251 | 0.24205 | 90800
6037 | 9 | 252 | 12 | 0 | 0.98615 | 0.2228 | 90800
6038 | 9 | 252 | 13 | 0 | 0.94251 | 0.24729 | 90800
6039 | 9 | 252 | 14 | 0 | 0.8175 | 0.29525 | 90800
6040 | 9 | 252 | 15 | 0 | 0.62835 | 0.31489 | 90800
6041 | 9 | 252 | 16 | 0 | 0.40239 | 0.34687 | 90800
6042 | 9 | 252 | 17 | 0 | 0.17641 | 0.26348 | 90800
6043 | 9 | 252 | 18 | 0 | 0.007054 | 0.34474 | 90800
6044 | 9 | 252 | 19 | 1 | 0 | 0.30349 | 90600
6045 | 9 | 252 | 20 | 1 | 0 | 0.24883 | 90400
6046 | 9 | 252 | 21 | 0 | 0 | 0.24643 | 90400
6047 | 9 | 252 | 22 | 0 | 0 | 0.23263 | 90400
6048 | 9 | 252 | 23 | 0 | 0 | 0.16134 | 90400
6049 | 9 | 253 | 0 | 0 | 0 | 0.12162 | 90400
6050 | 9 | 253 | 1 | 0 | 0 | 0.11686 | 90400
6051 | 9 | 253 | 2 | 0 | 0 | 0.12979 | 90400
6052 | 9 | 253 | 3 | 0 | 0 | 0.17852 | 90400
6053 | 9 | 253 | 4 | 0 | 0 | 0.25491 | 90400
6054 | 9 | 253 | 5 | 0 | 0 | 0.15714 | 90400
6055 | 9 | 253 | 6 | 0 | 0.008173 | 0.20828 | 90400
6056 | 9 | 253 | 7 | 1 | 0.20439 | 0.23061 | 90200
6057 | 9 | 253 | 8 | 1 | 0.4662 | 0.28179 | 90000
6058 | 9 | 253 | 9 | 0 | 0.72799 | 0.24309 | 90000
6059 | 9 | 253 | 10 | 0 | 0.94713 | 0.31894 | 90000
6060 | 9 | 253 | 11 | 0 | 1 | 0.29648 | 90000
6061 | 9 | 253 | 12 | 0 | 1 | 0.30572 | 90000
6062 | 9 | 253 | 13 | 0 | 1 | 0.26779 | 90000
6063 | 9 | 253 | 14 | 0 | 0.94713 | 0.45341 | 90000
6064 | 9 | 253 | 15 | 0 | 0.72799 | 0.37301 | 90000
6065 | 9 | 253 | 16 | 0 | 0.4662 | 0.33489 | 90000
6066 | 9 | 253 | 17 | 0 | 0.20439 | 0.35386 | 90000
6067 | 9 | 253 | 18 | 0 | 0.008173 | 0.26231 | 90000
6068 | 9 | 253 | 19 | 1 | 0 | 0.33332 | 89800
6069 | 9 | 253 | 20 | 1 | 0 | 0.21422 | 89600
6070 | 9 | 253 | 21 | 0 | 0 | 0.18014 | 89600
6071 | 9 | 253 | 22 | 0 | 0 | 0.20901 | 89600
6072 | 9 | 253 | 23 | 0 | 0 | 0.14905 | 89600
6073 | 9 | 254 | 0 | 0 | 0 | 0.19501 | 89600
6074 | 9 | 254 | 1 | 0 | 0 | 0.20596 | 89600
6075 | 9 | 254 | 2 | 0 | 0 | 0.19065 | 89600
6076 | 9 | 254 | 3 | 0 | 0 | 0.22863 | 89600
6077 | 9 | 254 | 4 | 0 | 0 | 0.28784 | 89600
6078 | 9 | 254 | 5 | 0 | 0 | 0.14329 | 89600
6079 | 9 | 254 | 6 | 0 | 0.007864 | 0.22568 | 89600
6080 | 9 | 254 | 7 | 1 | 0.19665 | 0.17538 | 89400
6081 | 9 | 254 | 8 | 1 | 0.44856 | 0.12906 | 89200
6082 | 9 | 254 | 9 | 0 | 0.70044 | 0.16214 | 89200
6083 | 9 | 254 | 10 | 0 | 0.9113 | 0.28301 | 89200
6084 | 9 | 254 | 11 | 0 | 1 | 0.51727 | 89200
6085 | 9 | 254 | 12 | 0 | 1 | 0.39644 | 89200
6086 | 9 | 254 | 13 | 0 | 1 | 0.49809 | 89200
6087 | 9 | 254 | 14 | 0 | 0.9113 | 0.7203 | 89200
6088 | 9 | 254 | 15 | 0 | 0.70044 | 1 | 89200
6089 | 9 | 254 | 16 | 0 | 0.44856 | 1 | 89200
6090 | 9 | 254 | 17 | 0 | 0.19665 | 0.72473 | 89200
6091 | 9 | 254 | 18 | 0 | 0.007864 | 0.67142 | 89200
6092 | 9 | 254 | 19 | 1 | 0 | 0.77337 | 89000
6093 | 9 | 254 | 20 | 1 | 0 | 0.81637 | 88800
6094 | 9 | 254 | 21 | 0 | 0 | 0.85714 | 88800
6095 | 9 | 254 | 22 | 0 | 0 | 1 | 88800
6096 | 9 | 254 | 23 | 0 | 0 | 1 | 88800
6097 | 9 | 255 | 0 | 0 | 0 | 1 | 88800
6098 | 9 | 255 | 1 | 0 | 0 | 1 | 88800
6099 | 9 | 255 | 2 | 0 | 0 | 1 | 88800
6100 | 9 | 255 | 3 | 0 | 0 | 0.91775 | 88800
6101 | 9 | 255 | 4 | 0 | 0 | 1 | 88800
6102 | 9 | 255 | 5 | 0 | 0 | 1 | 88800
6103 | 9 | 255 | 6 | 0 | 0.007756 | 1 | 88800
6104 | 9 | 255 | 7 | 1 | 0.19396 | 1 | 88600
6105 | 9 | 255 | 8 | 1 | 0.44242 | 1 | 88400
6106 | 9 | 255 | 9 | 0 | 0.69085 | 1 | 88400
6107 | 9 | 255 | 10 | 0 | 0.89882 | 1 | 88400
6108 | 9 | 255 | 11 | 0 | 1 | 0.94099 | 88400
6109 | 9 | 255 | 12 | 0 | 1 | 0.8634 | 88400
6110 | 9 | 255 | 13 | 0 | 1 | 0.81114 | 88400
6111 | 9 | 255 | 14 | 0 | 0.89882 | 0.87516 | 88400
6112 | 9 | 255 | 15 | 0 | 0.69085 | 0.62016 | 88400
6113 | 9 | 255 | 16 | 0 | 0.44242 | 0.45122 | 88400
6114 | 9 | 255 | 17 | 0 | 0.19396 | 0.51055 | 88400
6115 | 9 | 255 | 18 | 0 | 0.007756 | 0.42733 | 88400
6116 | 9 | 255 | 19 | 1 | 0 | 0.48794 | 88200
6117 | 9 | 255 | 20 | 1 | 0 | 0.56616 | 88000
6118 | 9 | 255 | 21 | 0 | 0 | 0.47715 | 88000
6119 | 9 | 255 | 22 | 0 | 0 | 0.41448 | 88000
6120 | 9 | 255 | 23 | 0 | 0 | 0.3348 | 88000
6121 | 9 | 256 | 0 | 0 | 0 | 0.21155 | 88000
6122 | 9 | 256 | 1 | 0 | 0 | 0.26062 | 88000
6123 | 9 | 256 | 2 | 0 | 0 | 0.29373 | 88000
6124 | 9 | 256 | 3 | 0 | 0 | 0.39342 | 88000
6125 | 9 | 256 | 4 | 0 | 0 | 0.41019 | 88000
6126 | 9 | 256 | 5 | 0 | 0 | 0.37369 | 88000
6127 | 9 | 256 | 6 | 0 | 0.008324 | 0.29254 | 88000
6128 | 9 | 256 | 7 | 1 | 0.20817 | 0.32423 | 87800
6129 | 9 | 256 | 8 | 1 | 0.47482 | 0.28191 | 87600
6130 | 9 | 256 | 9 | 0 | 0.74146 | 0.39935 | 87600
6131 | 9 | 256 | 10 | 0 | 0.96466 | 0.32402 | 87600
6132 | 9 | 256 | 11 | 0 | 1 | 0.44301 | 87600
6133 | 9 | 256 | 12 | 0 | 1 | 0.60301 | 87600
6134 | 9 | 256 | 13 | 0 | 1 | 0.74453 | 87600
6135 | 9 | 256 | 14 | 0 | 0.96466 | 0.58057 | 87600
6136 | 9 | 256 | 15 | 0 | 0.74146 | 0.58277 | 87600
6137 | 9 | 256 | 16 | 0 | 0.47482 | 0.7937 | 87600
6138 | 9 | 256 | 17 | 0 | 0.20817 | 0.67072 | 87600
6139 | 9 | 256 | 18 | 0 | 0.008324 | 0.64936 | 87600
6140 | 9 | 256 | 19 | 1 | 0 | 0.77544 | 87400
6141 | 9 | 256 | 20 | 1 | 0 | 0.92414 | 87200
6142 | 9 | 256 | 21 | 0 | 0 | 0.79413 | 87200
6143 | 9 | 256 | 22 | 0 | 0 | 0.67411 | 87200
6144 | 9 | 256 | 23 | 0 | 0 | 0.35585 | 87200
6145 | 9 | 257 | 0 | 0 | 0 | 0.38596 | 87200
6146 | 9 | 257 | 1 | 0 | 0 | 0.34838 | 87200
6147 | 9 | 257 | 2 | 0 | 0 | 0.17463 | 87200
6148 | 9 | 257 | 3 | 0 | 0 | 0.16613 | 87200
6149 | 9 | 257 | 4 | 0 | 0 | 0.17657 | 87200
6150 | 9 | 257 | 5 | 0 | 0 | 0.17746 | 87200
6151 | 9 | 257 | 6 | 0 | 0.008313 | 0.11404 | 87200
6152 | 9 | 257 | 7 | 1 | 0.2079 | 0.17139 | 87000
6153 | 9 | 257 | 8 | 1 | 0.47421 | 0.24789 | 86800
6154 | 9 | 257 | 9 | 0 | 0.7405 | 0.19704 | 86800
6155 | 9 | 257 | 10 | 0 | 0.96342 | 0.1292 | 86800
6156 | 9 | 257 | 11 | 0 | 1 | 0.14409 | 86800
6157 | 9 | 257 | 12 | 0 | 1 | 0.13004 | 86800
6158 | 9 | 257 | 13 | 0 | 1 | 0.12166 | 86800
6159 | 9 | 257 | 14 | 0 | 0.96342 | 0.12306 | 86800
6160 | 9 | 257 | 15 | 0 | 0.7405 | 0.090859 | 86800
6161 | 9 | 257 | 16 | 0 | 0.47421 | 0.09445 | 86800
6162 | 9 | 257 | 17 | 0 | 0.2079 | 0.18438 | 86800
6163 | 9 | 257 | 18 | 0 | 0.008313 | 0.253 | 86800
6164 | 9 | 257 | 19 | 1 | 0 | 0.2638 | 86600
6165 | 9 | 257 | 20 | 1 | 0 | 0.2212 | 86400
6166 | 9 | 257 | 21 | 0 | 0 | 0.23919 | 86400
6167 | 9 | 257 | 22 | 0 | 0 | 0.19044 | 86400
6168 | 9 | 257 | 23 | 0 | 0 | 0.1629 | 86400
6169 | 9 | 258 | 0 | 0 | 0 | 0.13538 | 86400
6170 | 9 | 258 | 1 | 0 | 0 | 0.13929 | 86400
6171 | 9 | 258 | 2 | 0 | 0 | 0.16497 | 86400
6172 | 9 | 258 | 3 | 0 | 0 | 0.26706 | 86400
6173 | 9 | 258 | 4 | 0 | 0 | 0.33232 | 86400
6174 | 9 | 258 | 5 | 0 | 0 | 0.33829 | 86400
6175 | 9 | 258 | 6 | 0 | 0.00715 | 0.38917 | 86400
6176 | 9 | 258 | 7 | 1 | 0.17881 | 0.3345 | 86200
6177 | 9 | 258 | 8 | 1 | 0.40786 | 0.45594 | 86000
6178 | 9 | 258 | 9 | 0 | 0.6369 | 0.49321 | 86000
6179 | 9 | 258 | 10 | 0 | 0.82862 | 0.51388 | 86000
6180 | 9 | 258 | 11 | 0 | 0.95533 | 0.32277 | 86000
6181 | 9 | 258 | 12 | 0 | 0.99957 | 0.42866 | 86000
6182 | 9 | 258 | 13 | 0 | 0.95533 | 0.53057 | 86000
6183 | 9 | 258 | 14 | 0 | 0.82862 | 0.58394 | 86000
6184 | 9 | 258 | 15 | 0 | 0.6369 | 0.56222 | 86000
6185 | 9 | 258 | 16 | 0 | 0.40786 | 0.39279 | 86000
6186 | 9 | 258 | 17 | 0 | 0.17881 | 0.26747 | 86000
6187 | 9 | 258 | 18 | 0 | 0.00715 | 0.30868 | 86000
6188 | 9 | 258 | 19 | 1 | 0 | 0.22474 | 85800
6189 | 9 | 258 | 20 | 1 | 0 | 0.31767 | 85600
6190 | 9 | 258 | 21 | 0 | 0 | 0.40255 | 85600
6191 | 9 | 258 | 22 | 0 | 0 | 0.37932 | 85600
6192 | 9 | 258 | 23 | 0 | 0 | 0.46801 | 85600
6193 | 9 | 259 | 0 | 0 | 0 | 0.4565 | 85600
6194 | 9 | 259 | 1 | 0 | 0 | 0.50703 | 85600
6195 | 9 | 259 | 2 | 0 | 0 | 0.41524 | 85600
6196 | 9 | 259 | 3 | 0 | 0 | 0.40472 | 85600
6197 | 9 | 259 | 4 | 0 | 0 | 0.41294 | 85600
6198 | 9 | 259 | 5 | 0 | 0 | 0.45999 | 85600
6199 | 9 | 259 | 6 | 0 | 0.010091 | 0.55251 | 85600
6200 | 9 | 259 | 7 | 1 | 0.25235 | 0.55458 | 85400
6201 | 9 | 259 | 8 | 1 | 0.57561 | 0.38642 | 85200
6202 | 9 | 259 | 9 | 0 | 0.89884 | 0.47331 | 85200
6203 | 9 | 259 | 10 | 0 | 1 | 0.36656 | 85200
6204 | 9 | 259 | 11 | 0 | 1 | 0.46248 | 85200
6205 | 9 | 259 | 12 | 0 | 1 | 0.61432 | 85200
6206 | 9 | 259 | 13 | 0 | 1 | 0.46851 | 85200
6207 | 9 | 259 | 14 | 0 | 1 | 0.74323 | 85200
6208 | 9 | 259 | 15 | 0 | 0.89884 | 0.6827 | 85200
6209 | 9 | 259 | 16 | 0 | 0.57561 | 0.51549 | 85200
6210 | 9 | 259 | 17 | 0 | 0.25235 | 0.53183 | 85200
6211 | 9 | 259 | 18 | 0 | 0.010091 | 0.67242 | 85200
6212 | 9 | 259 | 19 | 1 | 0 | 0.53805 | 85000
6213 | 9 | 259 | 20 | 1 | 0 | 0.35128 | 84800
6214 | 9 | 259 | 21 | 0 | 0 | 0.33639 | 84800
6215 | 9 | 259 | 22 | 0 | 0 | 0.23606 | 84800
6216 | 9 | 259 | 23 | 0 | 0 | 0.21075 | 84800
6217 | 9 | 260 | 0 | 0 | 0 | 0.2176 | 84800
6218 | 9 | 260 | 1 | 0 | 0 | 0.20748 | 84800
6219 | 9 | 260 | 2 | 0 | 0 | 0.31573 | 84800
6220 | 9 | 260 | 3 | 0 | 0 | 0.29569 | 84800
6221 | 9 | 260 | 4 | 0 | 0 | 0.45016 | 84800
6222 | 9 | 260 | 5 | 0 | 0 | 0.45576 | 84800
6223 | 9 | 260 | 6 | 0 | 0.008227 | 0.54035 | 84800
6224 | 9 | 260 | 7 | 1 | 0.20574 | 0.51683 | 84600
6225 | 9 | 260 | 8 | 1 | 0.46928 | 0.64622 | 84400
6226 | 9 | 260 | 9 | 0 | 0.7328 | 0.62457 | 84400
6227 | 9 | 260 | 10 | 0 | 0.95339 | 0.9138 | 84400
6228 | 9 | 260 | 11 | 0 | 1 | 0.8493 | 84400
6229 | 9 | 260 | 12 | 0 | 1 | 1 | 84400
6230 | 9 | 260 | 13 | 0 | 1 | 0.81554 | 84400
6231 | 9 | 260 | 14 | 0 | 0.95339 | 0.60313 | 84400
6232 | 9 | 260 | 15 | 0 | 0.7328 | 0.70935 | 84400
6233 | 9 | 260 | 16 | 0 | 0.46928 | 0.89381 | 84400
6234 | 9 | 260 | 17 | 0 | 0.20574 | 0.81801 | 84400
6235 | 9 | 260 | 18 | 0 | 0.008227 | 0.68009 | 84400
6236 | 9 | 260 | 19 | 1 | 0 | 0.69334 | 84200
6237 | 9 | 260 | 20 | 1 | 0 | 0.6464 | 84000
6238 | 9 | 260 | 21 | 0 | 0 | 0.39794 | 84000
6239 | 9 | 260 | 22 | 0 | 0 | 0.29766 | 84000
6240 | 9 | 260 | 23 | 0 | 0 | 0.23207 | 84000
6241 | 9 | 261 | 0 | 0 | 0 | 0.22394 | 84000
6242 | 9 | 261 | 1 | 0 | 0 | 0.30682 | 84000
6243 | 9 | 261 | 2 | 0 | 0 | 0.29625 | 84000
6244 | 9 | 261 | 3 | 0 | 0 | 0.47368 | 84000
6245 | 9 | 261 | 4 | 0 | 0 | 0.28023 | 84000
6246 | 9 | 261 | 5 | 0 | 0 | 0.22537 | 84000
6247 | 9 | 261 | 6 | 0 | 0.008137 | 0.22773 | 84000
6248 | 9 | 261 | 7 | 1 | 0.20348 | 0.15314 | 83800
6249 | 9 | 261 | 8 | 1 | 0.46414 | 0.16098 | 83600
6250 | 9 | 261 | 9 | 0 | 0.72478 | 0.14406 | 83600
6251 | 9 | 261 | 10 | 0 | 0.94295 | 0.12466 | 83600
6252 | 9 | 261 | 11 | 0 | 1 | 0.13376 | 83600
6253 | 9 | 261 | 12 | 0 | 1 | 0.1304 | 83600
6254 | 9 | 261 | 13 | 0 | 1 | 0.19739 | 83600
6255 | 9 | 261 | 14 | 0 | 0.94295 | 0.13853 | 83600
6256 | 9 | 261 | 15 | 0 | 0.72478 | 0.11794 | 83600
6257 | 9 | 261 | 16 | 0 | 0.46414 | 0.14202 | 83600
6258 | 9 | 261 | 17 | 0 | 0.20348 | 0.10632 | 83600
6259 | 9 | 261 | 18 | 0 | 0.008137 | 0.08824 | 83600
6260 | 9 | 261 | 19 | 1 | 0 | 0.13243 | 83400
6261 | 9 | 261 | 20 | 1 | 0 | 0.21592 | 83200
6262 | 9 | 261 | 21 | 0 | 0 | 0.23065 | 83200
6263 | 9 | 261 | 22 | 0 | 0 | 0.14087 | 83200
6264 | 9 | 261 | 23 | 0 | 0 | 0.18454 | 83200
6265 | 9 | 262 | 0 | 0 | 0 | 0.14766 | 83200
6266 | 9 | 262 | 1 | 0 | 0 | 0.15172 | 83200
6267 | 9 | 262 | 2 | 0 | 0 | 0.12034 | 83200
6268 | 9 | 262 | 3 | 0 | 0 | 0.15346 | 83200
6269 | 9 | 262 | 4 | 0 | 0 | 0.12396 | 83200
6270 | 9 | 262 | 5 | 0 | 0 | 0.10196 | 83200
6271 | 9 | 262 | 6 | 0 | 0.008336 | 0.1541 | 83200
6272 | 9 | 262 | 7 | 1 | 0.20847 | 0.21587 | 83000
6273 | 9 | 262 | 8 | 1 | 0.47552 | 0.32177 | 82800
6274 | 9 | 262 | 9 | 0 | 0.74255 | 0.49617 | 82800
6275 | 9 | 262 | 10 | 0 | 0.96607 | 0.63671 | 82800
6276 | 9 | 262 | 11 | 0 | 1 | 0.56768 | 82800
6277 | 9 | 262 | 12 | 0 | 1 | 0.51192 | 82800
6278 | 9 | 262 | 13 | 0 | 1 | 0.55619 | 82800
6279 | 9 | 262 | 14 | 0 | 0.96607 | 0.55213 | 82800
6280 | 9 | 262 | 15 | 0 | 0.74255 | 0.47199 | 82800
6281 | 9 | 262 | 16 | 0 | 0.47552 | 0.35317 | 82800
6282 | 9 | 262 | 17 | 0 | 0.20847 | 0.22961 | 82800
6283 | 9 | 262 | 18 | 0 | 0.008336 | 0.21115 | 82800
6284 | 9 | 262 | 19 | 1 | 0 | 0.38493 | 82600
6285 | 9 | 262 | 20 | 1 | 0 | 0.47378 | 82400
6286 | 9 | 262 | 21 | 0 | 0 | 0.48125 | 82400
6287 | 9 | 262 | 22 | 0 | 0 | 0.64405 | 82400
6288 | 9 | 262 | 23 | 0 | 0 | 0.51801 | 82400
6289 | 9 | 263 | 0 | 0 | 0 | 0.605 | 82400
6290 | 9 | 263 | 1 | 0 | 0 | 0.4998 | 82400
6291 | 9 | 263 | 2 | 0 | 0 | 0.32584 | 82400
6292 | 9 | 263 | 3 | 0 | 0 | 0.65189 | 82400
6293 | 9 | 263 | 4 | 0 | 0 | 0.49248 | 82400
6294 | 9 | 263 | 5 | 0 | 0 | 0.88982 | 82400
6295 | 9 | 263 | 6 | 0 | 0.007694 | 0.69893 | 82400
6296 | 9 | 263 | 7 | 1 | 0.19242 | 0.65598 | 82200
6297 | 9 | 263 | 8 | 1 | 0.4389 | 0.36083 | 82000
6298 | 9 | 263 | 9 | 0 | 0.68536 | 0.39291 | 82000
6299 | 9 | 263 | 10 | 0 | 0.89167 | 0.23533 | 82000
6300 | 9 | 263 | 11 | 0 | 1 | 0.22251 | 82000
6301 | 9 | 263 | 12 | 0 | 1 | 0.30483 | 82000
6302 | 9 | 263 | 13 | 0 | 1 | 0.43465 | 82000
6303 | 9 | 263 | 14 | 0 | 0.89167 | 0.66894 | 82000
6304 | 9 | 263 | 15 | 0 | 0.68536 | 0.52772 | 82000
6305 | 9 | 263 | 16 | 0 | 0.4389 | 0.21946 | 82000
6306 | 9 | 263 | 17 | 0 | 0.19242 | 0.17347 | 82000
6307 | 9 | 263 | 18 | 0 | 0.007694 | 0.18489 | 82000
6308 | 9 | 263 | 19 | 1 | 0 | 0.24515 | 81800
6309 | 9 | 263 | 20 | 1 | 0 | 0.17518 | 81600
6310 | 9 | 263 | 21 | 0 | 0 | 0.154 | 81600
6311 | 9 | 263 | 22 | 0 | 0 | 0.17442 | 81600
6312 | 9 | 263 | 23 | 0 | 0 | 0.18006 | 81600
6313 | 9 | 264 | 0 | 0 | 0 | 0.14261 | 81600
6314 | 9 | 264 | 1 | 0 | 0 | 0.13264 | 81600
6315 | 9 | 264 | 2 | 0 | 0 | 0.10588 | 81600
6316 | 9 | 264 | 3 | 0 | 0 | 0.091177 | 81600
6317 | 9 | 264 | 4 | 0 | 0 | 0.10814 | 81600
6318 | 9 | 264 | 5 | 0 | 0 | 0.089702 | 81600
6319 | 9 | 264 | 6 | 0 | 0.007833 | 0.13398 | 81600
6320 | 9 | 264 | 7 | 1 | 0.1959 | 0.14696 | 81400
6321 | 9 | 264 | 8 | 1 | 0.44684 | 0.17832 | 81200
6322 | 9 | 264 | 9 | 0 | 0.69776 | 0.21016 | 81200
6323 | 9 | 264 | 10 | 0 | 0.90781 | 0.16739 | 81200
6324 | 9 | 264 | 11 | 0 | 1 | 0.2491 | 81200
6325 | 9 | 264 | 12 | 0 | 1 | 0.31252 | 81200
6326 | 9 | 264 | 13 | 0 | 1 | 0.53521 | 81200
6327 | 9 | 264 | 14 | 0 | 0.90781 | 0.75727 | 81200
6328 | 9 | 264 | 15 | 0 | 0.69776 | 0.69668 | 81200
6329 | 9 | 264 | 16 | 0 | 0.44684 | 0.72671 | 81200
6330 | 9 | 264 | 17 | 0 | 0.1959 | 0.75655 | 81200
6331 | 9 | 264 | 18 | 0 | 0.007833 | 0.77585 | 81200
6332 | 9 | 264 | 19 | 1 | 0 | 0.70508 | 81000
6333 | 9 | 264 | 20 | 1 | 0 | 0.56079 | 80800
6334 | 9 | 264 | 21 | 0 | 0 | 0.5801 | 80800
6335 | 9 | 264 | 22 | 0 | 0 | 0.45353 | 80800
6336 | 9 | 264 | 23 | 0 | 0 | 0.4452 | 80800
6337 | 9 | 265 | 0 | 0 | 0 | 0.37172 | 80800
6338 | 9 | 265 | 1 | 0 | 0 | 0.26422 | 80800
6339 | 9 | 265 | 2 | 0 | 0 | 0.23762 | 80800
6340 | 9 | 265 | 3 | 0 | 0 | 0.22114 | 80800
6341 | 9 | 265 | 4 | 0 | 0 | 0.30149 | 80800
6342 | 9 | 265 | 5 | 0 | 0 | 0.35761 | 80800
6343 | 9 | 265 | 6 | 0 | 0.007234 | 0.31751 | 80800
6344 | 9 | 265 | 7 | 1 | 0.1809 | 0.24902 | 80600
6345 | 9 | 265 | 8 | 1 | 0.41262 | 0.20071 | 80400
6346 | 9 | 265 | 9 | 0 | 0.64433 | 0.20822 | 80400
6347 | 9 | 265 | 10 | 0 | 0.83829 | 0.24227 | 80400
6348 | 9 | 265 | 11 | 0 | 0.96648 | 0.2544 | 80400
6349 | 9 | 265 | 12 | 0 | 1 | 0.23536 | 80400
6350 | 9 | 265 | 13 | 0 | 0.96648 | 0.18977 | 80400
6351 | 9 | 265 | 14 | 0 | 0.83829 | 0.21886 | 80400
6352 | 9 | 265 | 15 | 0 | 0.64433 | 0.3541 | 80400
6353 | 9 | 265 | 16 | 0 | 0.41262 | 0.51004 | 80400
6354 | 9 | 265 | 17 | 0 | 0.1809 | 0.45768 | 80400
6355 | 9 | 265 | 18 | 0 | 0.007234 | 0.35866 | 80400
6356 | 9 | 265 | 19 | 1 | 0 | 0.32523 | 80200
6357 | 9 | 265 | 20 | 1 | 0 | 0.25033 | 80000
6358 | 9 | 265 | 21 | 0 | 0 | 0.2365 | 80000
6359 | 9 | 265 | 22 | 0 | 0 | 0.2177 | 80000
6360 | 9 | 265 | 23 | 0 | 0 | 0.2793 | 80000
6361 | 9 | 266 | 0 | 0 | 0 | 0.40046 | 80000
6362 | 9 | 266 | 1 | 0 | 0 | 0.42248 | 80000
6363 | 9 | 266 | 2 | 0 | 0 | 0.51376 | 80000
6364 | 9 | 266 | 3 | 0 | 0 | 0.73045 | 80000
6365 | 9 | 266 | 4 | 0 | 0 | 0.91346 | 80000
6366 | 9 | 266 | 5 | 0 | 0 | 0.69476 | 80000
6367 | 9 | 266 | 6 | 0 | 0.009671 | 0.85303 | 80000
6368 | 9 | 266 | 7 | 1 | 0.24185 | 0.74077 | 79800
6369 | 9 | 266 | 8 | 1 | 0.55164 | 0.47941 | 79600
6370 | 9 | 266 | 9 | 0 | 0.86142 | 0.46714 | 79600
6371 | 9 | 266 | 10 | 0 | 1 | 0.42589 | 79600
6372 | 9 | 266 | 11 | 0 | 1 | 0.41293 | 79600
6373 | 9 | 266 | 12 | 0 | 1 | 0.40354 | 79600
6374 | 9 | 266 | 13 | 0 | 1 | 0.46392 | 79600
6375 | 9 | 266 | 14 | 0 | 1 | 0.58662 | 79600
6376 | 9 | 266 | 15 | 0 | 0.86142 | 0.5227 | 79600
6377 | 9 | 266 | 16 | 0 | 0.55164 | 0.57157 | 79600
6378 | 9 | 266 | 17 | 0 | 0.24185 | 0.65242 | 79600
6379 | 9 | 266 | 18 | 0 | 0.009671 | 0.59011 | 79600
6380 | 9 | 266 | 19 | 1 | 0 | 0.46893 | 79400
6381 | 9 | 266 | 20 | 1 | 0 | 0.40318 | 79200
6382 | 9 | 266 | 21 | 0 | 0 | 0.53054 | 79200
6383 | 9 | 266 | 22 | 0 | 0 | 0.54911 | 79200
6384 | 9 | 266 | 23 | 0 | 0 | 0.62998 | 79200
6385 | 9 | 267 | 0 | 0 | 0 | 0.81439 | 79200
6386 | 9 | 267 | 1 | 0 | 0 | 0.65444 | 79200
6387 | 9 | 267 | 2 | 0 | 0 | 0.45394 | 79200
6388 | 9 | 267 | 3 | 0 | 0 | 0.4792 | 79200
6389 | 9 | 267 | 4 | 0 | 0 | 0.24214 | 79200
6390 | 9 | 267 | 5 | 0 | 0 | 0.29712 | 79200
6391 | 9 | 267 | 6 | 0 | 0.007628 | 0.2736 | 79200
6392 | 9 | 267 | 7 | 1 | 0.19076 | 0.3657 | 79000
6393 | 9 | 267 | 8 | 1 | 0.43513 | 0.24961 | 78800
6394 | 9 | 267 | 9 | 0 | 0.67947 | 0.29546 | 78800
6395 | 9 | 267 | 10 | 0 | 0.88401 | 0.30906 | 78800
6396 | 9 | 267 | 11 | 0 | 1 | 0.33038 | 78800
6397 | 9 | 267 | 12 | 0 | 1 | 0.40008 | 78800
6398 | 9 | 267 | 13 | 0 | 1 | 0.69218 | 78800
6399 | 9 | 267 | 14 | 0 | 0.88401 | 0.58853 | 78800
6400 | 9 | 267 | 15 | 0 | 0.67947 | 0.47508 | 78800
6401 | 9 | 267 | 16 | 0 | 0.43513 | 0.47467 | 78800
6402 | 9 | 267 | 17 | 0 | 0.19076 | 0.59296 | 78800
6403 | 9 | 267 | 18 | 0 | 0.007628 | 0.83889 | 78800
6404 | 9 | 267 | 19 | 1 | 0 | 0.69766 | 78600
6405 | 9 | 267 | 20 | 1 | 0 | 0.84203 | 78400
6406 | 9 | 267 | 21 | 0 | 0 | 0.53368 | 78400
6407 | 9 | 267 | 22 | 0 | 0 | 0.51283 | 78400
6408 | 9 | 267 | 23 | 0 | 0 | 0.47941 | 78400
6409 | 9 | 268 | 0 | 0 | 0 | 0.4067 | 78400
6410 | 9 | 268 | 1 | 0 | 0 | 0.39495 | 78400
6411 | 9 | 268 | 2 | 0 | 0 | 0.44517 | 78400
6412 | 9 | 268 | 3 | 0 | 0 | 0.50569 | 78400
6413 | 9 | 268 | 4 | 0 | 0 | 0.41608 | 78400
6414 | 9 | 268 | 5 | 0 | 0 | 0.60166 | 78400
6415 | 9 | 268 | 6 | 0 | 0.009657 | 0.46647 | 78400
6416 | 9 | 268 | 7 | 1 | 0.2415 | 0.3727 | 78200
6417 | 9 | 268 | 8 | 1 | 0.55085 | 0.41279 | 78000
6418 | 9 | 268 | 9 | 0 | 0.86017 | 0.37108 | 78000
6419 | 9 | 268 | 10 | 0 | 1 | 0.28926 | 78000
6420 | 9 | 268 | 11 | 0 | 1 | 0.20814 | 78000
6421 | 9 | 268 | 12 | 0 | 1 | 0.20182 | 78000
6422 | 9 | 268 | 13 | 0 | 1 | 0.20893 | 78000
6423 | 9 | 268 | 14 | 0 | 1 | 0.29097 | 78000
6424 | 9 | 268 | 15 | 0 | 0.86017 | 0.34155 | 78000
6425 | 9 | 268 | 16 | 0 | 0.55085 | 0.26727 | 78000
6426 | 9 | 268 | 17 | 0 | 0.2415 | 0.30179 | 78000
6427 | 9 | 268 | 18 | 0 | 0.009657 | 0.2642 | 78000
6428 | 9 | 268 | 19 | 1 | 0 | 0.28588 | 77800
6429 | 9 | 268 | 20 | 1 | 0 | 0.25789 | 77600
6430 | 9 | 268 | 21 | 0 | 0 | 0.28504 | 77600
6431 | 9 | 268 | 22 | 0 | 0 | 0.34736 | 77600
6432 | 9 | 268 | 23 | 0 | 0 | 0.39339 | 77600
6433 | 9 | 269 | 0 | 0 | 0 | 0.38687 | 77600
6434 | 9 | 269 | 1 | 0 | 0 | 0.30844 | 77600
6435 | 9 | 269 | 2 | 0 | 0 | 0.26769 | 77600
6436 | 9 | 269 | 3 | 0 | 0 | 0.42845 | 77600
6437 | 9 | 269 | 4 | 0 | 0 | 0.34015 | 77600
6438 | 9 | 269 | 5 | 0 | 0 | 0.34472 | 77600
6439 | 9 | 269 | 6 | 0 | 0.008466 | 0.40655 | 77600
6440 | 9 | 269 | 7 | 1 | 0.21173 | 0.52354 | 77400
6441 | 9 | 269 | 8 | 1 | 0.48295 | 0.6773 | 77200
6442 | 9 | 269 | 9 | 0 | 0.75415 | 0.87663 | 77200
6443 | 9 | 269 | 10 | 0 | 0.98117 | 0.80724 | 77200
6444 | 9 | 269 | 11 | 0 | 1 | 1 | 77200
6445 | 9 | 269 | 12 | 0 | 1 | 1 | 77200
6446 | 9 | 269 | 13 | 0 | 1 | 1 | 77200
6447 | 9 | 269 | 14 | 0 | 0.98117 | 1 | 77200
6448 | 9 | 269 | 15 | 0 | 0.75415 | 1 | 77200
6449 | 9 | 269 | 16 | 0 | 0.48295 | 1 | 77200
6450 | 9 | 269 | 17 | 0 | 0.21173 | 0.76223 | 77200
6451 | 9 | 269 | 18 | 0 | 0.008466 | 0.77818 | 77200
6452 | 9 | 269 | 19 | 1 | 0 | 0.9677 | 77000
6453 | 9 | 269 | 20 | 1 | 0 | 0.91772 | 76800
6454 | 9 | 269 | 21 | 0 | 0 | 1 | 76800
6455 | 9 | 269 | 22 | 0 | 0 | 1 | 76800
6456 | 9 | 269 | 23 | 0 | 0 | 1 | 76800
6457 | 9 | 270 | 0 | 0 | 0 | 1 | 76800
6458 | 9 | 270 | 1 | 0 | 0 | 0.83433 | 76800
6459 | 9 | 270 | 2 | 0 | 0 | 0.84888 | 76800
6460 | 9 | 270 | 3 | 0 | 0 | 1 | 76800
6461 | 9 | 270 | 4 | 0 | 0 | 1 | 76800
6462 | 9 | 270 | 5 | 0 | 0 | 1 | 76800
6463 | 9 | 270 | 6 | 0 | 0.008525 | 1 | 76800
6464 | 9 | 270 | 7 | 1 | 0.21319 | 1 | 76600
6465 | 9 | 270 | 8 | 1 | 0.48629 | 0.90948 | 76400
6466 | 9 | 270 | 9 | 0 | 0.75936 | 0.84214 | 76400
6467 | 9 | 270 | 10 | 0 | 0.98794 | 0.73405 | 76400
6468 | 9 | 270 | 11 | 0 | 1 | 0.52036 | 76400
6469 | 9 | 270 | 12 | 0 | 1 | 0.60395 | 76400
6470 | 9 | 270 | 13 | 0 | 1 | 0.51111 | 76400
6471 | 9 | 270 | 14 | 0 | 0.98794 | 0.57291 | 76400
6472 | 9 | 270 | 15 | 0 | 0.75936 | 0.48993 | 76400
6473 | 9 | 270 | 16 | 0 | 0.48629 | 0.42008 | 76400
6474 | 9 | 270 | 17 | 0 | 0.21319 | 0.56703 | 76400
6475 | 9 | 270 | 18 | 0 | 0.008525 | 0.39951 | 76400
6476 | 9 | 270 | 19 | 1 | 0 | 0.45602 | 76200
6477 | 9 | 270 | 20 | 1 | 0 | 0.45912 | 76000
6478 | 9 | 270 | 21 | 0 | 0 | 0.74097 | 76000
6479 | 9 | 270 | 22 | 0 | 0 | 0.58101 | 76000
6480 | 9 | 270 | 23 | 0 | 0 | 0.54592 | 76000
6481 | 9 | 271 | 0 | 0 | 0 | 0.44599 | 76000
6482 | 9 | 271 | 1 | 0 | 0 | 0.32543 | 76000
6483 | 9 | 271 | 2 | 0 | 0 | 0.32088 | 76000
6484 | 9 | 271 | 3 | 0 | 0 | 0.47593 | 76000
6485 | 9 | 271 | 4 | 0 | 0 | 0.46457 | 76000
6486 | 9 | 271 | 5 | 0 | 0 | 0.8502 | 76000
6487 | 9 | 271 | 6 | 0 | 0.007057 | 0.85609 | 76000
6488 | 9 | 271 | 7 | 1 | 0.17648 | 0.94286 | 75800
6489 | 9 | 271 | 8 | 1 | 0.40255 | 0.50119 | 75600
6490 | 9 | 271 | 9 | 0 | 0.6286 | 0.32316 | 75600
6491 | 9 | 271 | 10 | 0 | 0.81783 | 0.27002 | 75600
6492 | 9 | 271 | 11 | 0 | 0.9429 | 0.23452 | 75600
6493 | 9 | 271 | 12 | 0 | 0.98655 | 0.19214 | 75600
6494 | 9 | 271 | 13 | 0 | 0.9429 | 0.35976 | 75600
6495 | 9 | 271 | 14 | 0 | 0.81783 | 0.31927 | 75600
6496 | 9 | 271 | 15 | 0 | 0.6286 | 0.27532 | 75600
6497 | 9 | 271 | 16 | 0 | 0.40255 | 0.30381 | 75600
6498 | 9 | 271 | 17 | 0 | 0.17648 | 0.36031 | 75600
6499 | 9 | 271 | 18 | 0 | 0.007057 | 0.42636 | 75600
6500 | 9 | 271 | 19 | 1 | 0 | 0.32303 | 75400
6501 | 9 | 271 | 20 | 1 | 0 | 0.47341 | 75200
6502 | 9 | 271 | 21 | 0 | 0 | 0.44286 | 75200
6503 | 9 | 271 | 22 | 0 | 0 | 1 | 75200
6504 | 9 | 271 | 23 | 0 | 0 | 1 | 75200
6505 | 9 | 272 | 0 | 0 | 0 | 0.66141 | 75200
6506 | 9 | 272 | 1 | 0 | 0 | 0.66559 | 75200
6507 | 9 | 272 | 2 | 0 | 0 | 0.7399 | 75200
6508 | 9 | 272 | 3 | 0 | 0 | 0.87865 | 75200
6509 | 9 | 272 | 4 | 0 | 0 | 0.90502 | 75200
6510 | 9 | 272 | 5 | 0 | 0 | 1 | 75200
6511 | 9 | 272 | 6 | 0 | 0.008254 | 1 | 75200
6512 | 9 | 272 | 7 | 1 | 0.20641 | 1 | 75000
6513 | 9 | 272 | 8 | 1 | 0.47082 | 1 | 74800
6514 | 9 | 272 | 9 | 0 | 0.7352 | 1 | 74800
6515 | 9 | 272 | 10 | 0 | 0.95651 | 1 | 74800
6516 | 9 | 272 | 11 | 0 | 1 | 1 | 74800
6517 | 9 | 272 | 12 | 0 | 1 | 0.94792 | 74800
6518 | 9 | 272 | 13 | 0 | 1 | 0.83216 | 74800
6519 | 9 | 272 | 14 | 0 | 0.95651 | 1 | 74800
6520 | 9 | 272 | 15 | 0 | 0.7352 | 0.91604 | 74800
6521 | 9 | 272 | 16 | 0 | 0.47082 | 1 | 74800
6522 | 9 | 272 | 17 | 0 | 0.20641 | 1 | 74800
6523 | 9 | 272 | 18 | 0 | 0.008254 | 0.90599 | 74800
6524 | 9 | 272 | 19 | 1 | 0 | 0.54236 | 74600
6525 | 9 | 272 | 20 | 1 | 0 | 0.51101 | 74400
6526 | 9 | 272 | 21 | 0 | 0 | 0.45228 | 74400
6527 | 9 | 272 | 22 | 0 | 0 | 0.29354 | 74400
6528 | 9 | 272 | 23 | 0 | 0 | 0.5379 | 74400
6529 | 9 | 273 | 0 | 0 | 0 | 0.46895 | 74400
6530 | 9 | 273 | 1 | 0 | 0 | 0.36242 | 74400
6531 | 9 | 273 | 2 | 0 | 0 | 0.64888 | 74400
6532 | 9 | 273 | 3 | 0 | 0 | 0.93835 | 74400
6533 | 9 | 273 | 4 | 0 | 0 | 0.99674 | 74400
6534 | 9 | 273 | 5 | 0 | 0 | 0.85595 | 74400
6535 | 9 | 273 | 6 | 0 | 0.008843 | 0.90396 | 74400
6536 | 9 | 273 | 7 | 1 | 0.22114 | 0.79041 | 74200
6537 | 9 | 273 | 8 | 1 | 0.5044 | 0.34053 | 74000
6538 | 9 | 273 | 9 | 0 | 0.78765 | 0.42294 | 74000
6539 | 9 | 273 | 10 | 0 | 1 | 0.49434 | 74000
6540 | 9 | 273 | 11 | 0 | 1 | 0.36793 | 74000
6541 | 9 | 273 | 12 | 0 | 1 | 0.4139 | 74000
6542 | 9 | 273 | 13 | 0 | 1 | 0.32437 | 74000
6543 | 9 | 273 | 14 | 0 | 1 | 0.3422 | 74000
6544 | 9 | 273 | 15 | 0 | 0.78765 | 0.24339 | 74000
6545 | 9 | 273 | 16 | 0 | 0.5044 | 0.30136 | 74000
6546 | 9 | 273 | 17 | 0 | 0.22114 | 0.33075 | 74000
6547 | 9 | 273 | 18 | 0 | 0.008843 | 0.26236 | 74000
6548 | 9 | 273 | 19 | 1 | 0 | 0.15461 | 73800
6549 | 9 | 273 | 20 | 1 | 0 | 0.12673 | 73600
6550 | 9 | 273 | 21 | 0 | 0 | 0.1518 | 73600
6551 | 9 | 273 | 22 | 0 | 0 | 0.16464 | 73600
6552 | 9 | 273 | 23 | 0 | 0 | 0.15266 | 73600
6553 | 10 | 274 | 0 | 0 | 0 | 0.13247 | 73600
6554 | 10 | 274 | 1 | 0 | 0 | 0.20644 | 73600
6555 | 10 | 274 | 2 | 0 | 0 | 0.23099 | 73600
6556 | 10 | 274 | 3 | 0 | 0 | 0.12597 | 73600
6557 | 10 | 274 | 4 | 0 | 0 | 0.18346 | 73600
6558 | 10 | 274 | 5 | 0 | 0 | 0.16324 | 73600
6559 | 10 | 274 | 6 | 0 | 0 | 0.15581 | 73600
6560 | 10 | 274 | 7 | 1 | 0.15191 | 0.22319 | 73400
6561 | 10 | 274 | 8 | 1 | 0.45704 | 0.2678 | 73200
6562 | 10 | 274 | 9 | 0 | 0.77845 | 0.19641 | 73200
6563 | 10 | 274 | 10 | 0 | 1 | 0.28676 | 73200
6564 | 10 | 274 | 11 | 0 | 1 | 0.27892 | 73200
6565 | 10 | 274 | 12 | 0 | 1 | 0.42723 | 73200
6566 | 10 | 274 | 13 | 0 | 1 | 0.52042 | 73200
6567 | 10 | 274 | 14 | 0 | 1 | 0.43171 | 73200
6568 | 10 | 274 | 15 | 0 | 0.77845 | 0.38563 | 73200
6569 | 10 | 274 | 16 | 0 | 0.45704 | 0.29459 | 73200
6570 | 10 | 274 | 17 | 0 | 0.15191 | 0.33495 | 73200
6571 | 10 | 274 | 18 | 0 | 0 | 0.42642 | 73200
6572 | 10 | 274 | 19 | 1 | 0 | 0.39708 | 73000
6573 | 10 | 274 | 20 | 1 | 0 | 0.21898 | 72800
6574 | 10 | 274 | 21 | 0 | 0 | 0.12127 | 72800
6575 | 10 | 274 | 22 | 0 | 0 | 0.1188 | 72800
6576 | 10 | 274 | 23 | 0 | 0 | 0.15935 | 72800
6577 | 10 | 275 | 0 | 0 | 0 | 0.13724 | 72800
6578 | 10 | 275 | 1 | 0 | 0 | 0.14294 | 72800
6579 | 10 | 275 | 2 | 0 | 0 | 0.12075 | 72800
6580 | 10 | 275 | 3 | 0 | 0 | 0.080861 | 72800
6581 | 10 | 275 | 4 | 0 | 0 | 0.054493 | 72800
6582 | 10 | 275 | 5 | 0 | 0 | 0.069149 | 72800
6583 | 10 | 275 | 6 | 0 | 0 | 0.075702 | 72800
6584 | 10 | 275 | 7 | 1 | 0.16847 | 0.10209 | 72600
6585 | 10 | 275 | 8 | 1 | 0.50688 | 0.10058 | 72400
6586 | 10 | 275 | 9 | 0 | 0.86334 | 0.17499 | 72400
6587 | 10 | 275 | 10 | 0 | 1 | 0.25574 | 72400
6588 | 10 | 275 | 11 | 0 | 1 | 0.46269 | 72400
6589 | 10 | 275 | 12 | 0 | 1 | 0.65757 | 72400
6590 | 10 | 275 | 13 | 0 | 1 | 0.45064 | 72400
6591 | 10 | 275 | 14 | 0 | 1 | 0.82784 | 72400
6592 | 10 | 275 | 15 | 0 | 0.86334 | 0.64687 | 72400
6593 | 10 | 275 | 16 | 0 | 0.50688 | 0.48328 | 72400
6594 | 10 | 275 | 17 | 0 | 0.16847 | 0.6416 | 72400
6595 | 10 | 275 | 18 | 0 | 0 | 0.55063 | 72400
6596 | 10 | 275 | 19 | 1 | 0 | 0.57767 | 72200
6597 | 10 | 275 | 20 | 1 | 0 | 0.52144 | 72000
6598 | 10 | 275 | 21 | 0 | 0 | 0.63226 | 72000
6599 | 10 | 275 | 22 | 0 | 0 | 0.59116 | 72000
6600 | 10 | 275 | 23 | 0 | 0 | 0.3908 | 72000
6601 | 10 | 276 | 0 | 0 | 0 | 0.22381 | 72000
6602 | 10 | 276 | 1 | 0 | 0 | 0.18754 | 72000
6603 | 10 | 276 | 2 | 0 | 0 | 0.16302 | 72000
6604 | 10 | 276 | 3 | 0 | 0 | 0.25849 | 72000
6605 | 10 | 276 | 4 | 0 | 0 | 0.27689 | 72000
6606 | 10 | 276 | 5 | 0 | 0 | 0.27048 | 72000
6607 | 10 | 276 | 6 | 0 | 0 | 0.39728 | 72000
6608 | 10 | 276 | 7 | 1 | 0.15775 | 0.37431 | 71800
6609 | 10 | 276 | 8 | 1 | 0.47461 | 0.2583 | 71600
6610 | 10 | 276 | 9 | 0 | 0.80838 | 0.28536 | 71600
6611 | 10 | 276 | 10 | 0 | 1 | 0.21413 | 71600
6612 | 10 | 276 | 11 | 0 | 1 | 0.34146 | 71600
6613 | 10 | 276 | 12 | 0 | 1 | 0.43397 | 71600
6614 | 10 | 276 | 13 | 0 | 1 | 0.36883 | 71600
6615 | 10 | 276 | 14 | 0 | 1 | 0.28742 | 71600
6616 | 10 | 276 | 15 | 0 | 0.80838 | 0.31099 | 71600
6617 | 10 | 276 | 16 | 0 | 0.47461 | 0.35482 | 71600
6618 | 10 | 276 | 17 | 0 | 0.15775 | 0.27695 | 71600
6619 | 10 | 276 | 18 | 0 | 0 | 0.19347 | 71600
6620 | 10 | 276 | 19 | 1 | 0 | 0.14127 | 71400
6621 | 10 | 276 | 20 | 1 | 0 | 0.22447 | 71200
6622 | 10 | 276 | 21 | 0 | 0 | 0.3045 | 71200
6623 | 10 | 276 | 22 | 0 | 0 | 0.32293 | 71200
6624 | 10 | 276 | 23 | 0 | 0 | 0.38927 | 71200
6625 | 10 | 277 | 0 | 0 | 0 | 0.39318 | 71200
6626 | 10 | 277 | 1 | 0 | 0 | 0.27339 | 71200
6627 | 10 | 277 | 2 | 0 | 0 | 0.33514 | 71200
6628 | 10 | 277 | 3 | 0 | 0 | 0.28216 | 71200
6629 | 10 | 277 | 4 | 0 | 0 | 0.20743 | 71200
6630 | 10 | 277 | 5 | 0 | 0 | 0.17439 | 71200
6631 | 10 | 277 | 6 | 0 | 0 | 0.18056 | 71200
6632 | 10 | 277 | 7 | 1 | 0.1608 | 0.16956 | 71000
6633 | 10 | 277 | 8 | 1 | 0.48378 | 0.17958 | 70800
6634 | 10 | 277 | 9 | 0 | 0.824 | 0.2011 | 70800
6635 | 10 | 277 | 10 | 0 | 1 | 0.12405 | 70800
6636 | 10 | 277 | 11 | 0 | 1 | 0.10172 | 70800
6637 | 10 | 277 | 12 | 0 | 1 | 0.13977 | 70800
6638 | 10 | 277 | 13 | 0 | 1 | 0.22336 | 70800
6639 | 10 | 277 | 14 | 0 | 1 | 0.19548 | 70800
6640 | 10 | 277 | 15 | 0 | 0.824 | 0.31652 | 70800
6641 | 10 | 277 | 16 | 0 | 0.48378 | 0.29814 | 70800
6642 | 10 | 277 | 17 | 0 | 0.1608 | 0.30345 | 70800
6643 | 10 | 277 | 18 | 0 | 0 | 0.34571 | 70800
6644 | 10 | 277 | 19 | 1 | 0 | 0.33445 | 70600
6645 | 10 | 277 | 20 | 1 | 0 | 0.43259 | 70400
6646 | 10 | 277 | 21 | 0 | 0 | 0.3807 | 70400
6647 | 10 | 277 | 22 | 0 | 0 | 0.4956 | 70400
6648 | 10 | 277 | 23 | 0 | 0 | 0.59461 | 70400
6649 | 10 | 278 | 0 | 0 | 0 | 0.81175 | 70400
6650 | 10 | 278 | 1 | 0 | 0 | 0.73641 | 70400
6651 | 10 | 278 | 2 | 0 | 0 | 0.84066 | 70400
6652 | 10 | 278 | 3 | 0 | 0 | 0.78885 | 70400
6653 | 10 | 278 | 4 | 0 | 0 | 0.39011 | 70400
6654 | 10 | 278 | 5 | 0 | 0 | 0.32981 | 70400
6655 | 10 | 278 | 6 | 0 | 0 | 0.30688 | 70400
6656 | 10 | 278 | 7 | 1 | 0.13567 | 0.45062 | 70200
6657 | 10 | 278 | 8 | 1 | 0.40819 | 0.5184 | 70000
6658 | 10 | 278 | 9 | 0 | 0.69524 | 0.43287 | 70000
6659 | 10 | 278 | 10 | 0 | 0.94147 | 0.41426 | 70000
6660 | 10 | 278 | 11 | 0 | 1 | 0.54789 | 70000
6661 | 10 | 278 | 12 | 0 | 1 | 0.63522 | 70000
6662 | 10 | 278 | 13 | 0 | 1 | 0.37311 | 70000
6663 | 10 | 278 | 14 | 0 | 0.94147 | 0.46808 | 70000
6664 | 10 | 278 | 15 | 0 | 0.69524 | 0.48601 | 70000
6665 | 10 | 278 | 16 | 0 | 0.40819 | 0.33057 | 70000
6666 | 10 | 278 | 17 | 0 | 0.13567 | 0.38968 | 70000
6667 | 10 | 278 | 18 | 0 | 0 | 0.44589 | 70000
6668 | 10 | 278 | 19 | 1 | 0 | 0.34328 | 69800
6669 | 10 | 278 | 20 | 1 | 0 | 0.48287 | 69600
6670 | 10 | 278 | 21 | 0 | 0 | 0.39802 | 69600
6671 | 10 | 278 | 22 | 0 | 0 | 0.24757 | 69600
6672 | 10 | 278 | 23 | 0 | 0 | 0.24145 | 69600
6673 | 10 | 279 | 0 | 0 | 0 | 0.28078 | 69600
6674 | 10 | 279 | 1 | 0 | 0 | 0.37899 | 69600
6675 | 10 | 279 | 2 | 0 | 0 | 0.38888 | 69600
6676 | 10 | 279 | 3 | 0 | 0 | 0.40204 | 69600
6677 | 10 | 279 | 4 | 0 | 0 | 0.34128 | 69600
6678 | 10 | 279 | 5 | 0 | 0 | 0.25562 | 69600
6679 | 10 | 279 | 6 | 0 | 0 | 0.23829 | 69600
6680 | 10 | 279 | 7 | 1 | 0.14788 | 0.23635 | 69400
6681 | 10 | 279 | 8 | 1 | 0.44491 | 0.4895 | 69200
6682 | 10 | 279 | 9 | 0 | 0.75779 | 0.6192 | 69200
6683 | 10 | 279 | 10 | 0 | 1 | 0.7379 | 69200
6684 | 10 | 279 | 11 | 0 | 1 | 1 | 69200
6685 | 10 | 279 | 12 | 0 | 1 | 0.61268 | 69200
6686 | 10 | 279 | 13 | 0 | 1 | 0.79485 | 69200
6687 | 10 | 279 | 14 | 0 | 1 | 0.47081 | 69200
6688 | 10 | 279 | 15 | 0 | 0.75779 | 0.60126 | 69200
6689 | 10 | 279 | 16 | 0 | 0.44491 | 0.62964 | 69200
6690 | 10 | 279 | 17 | 0 | 0.14788 | 0.52952 | 69200
6691 | 10 | 279 | 18 | 0 | 0 | 0.43977 | 69200
6692 | 10 | 279 | 19 | 1 | 0 | 0.47308 | 69000
6693 | 10 | 279 | 20 | 1 | 0 | 0.42393 | 68800
6694 | 10 | 279 | 21 | 0 | 0 | 0.35617 | 68800
6695 | 10 | 279 | 22 | 0 | 0 | 0.30624 | 68800
6696 | 10 | 279 | 23 | 0 | 0 | 0.35165 | 68800
6697 | 10 | 280 | 0 | 0 | 0 | 0.264 | 68800
6698 | 10 | 280 | 1 | 0 | 0 | 0.18024 | 68800
6699 | 10 | 280 | 2 | 0 | 0 | 0.18618 | 68800
6700 | 10 | 280 | 3 | 0 | 0 | 0.20679 | 68800
6701 | 10 | 280 | 4 | 0 | 0 | 0.16459 | 68800
6702 | 10 | 280 | 5 | 0 | 0 | 0.16389 | 68800
6703 | 10 | 280 | 6 | 0 | 0 | 0.13826 | 68800
6704 | 10 | 280 | 7 | 1 | 0.15545 | 0.2152 | 68600
6705 | 10 | 280 | 8 | 1 | 0.4677 | 0.22087 | 68400
6706 | 10 | 280 | 9 | 0 | 0.7966 | 0.26664 | 68400
6707 | 10 | 280 | 10 | 0 | 1 | 0.27995 | 68400
6708 | 10 | 280 | 11 | 0 | 1 | 0.23672 | 68400
6709 | 10 | 280 | 12 | 0 | 1 | 0.17739 | 68400
6710 | 10 | 280 | 13 | 0 | 1 | 0.15678 | 68400
6711 | 10 | 280 | 14 | 0 | 1 | 0.17348 | 68400
6712 | 10 | 280 | 15 | 0 | 0.7966 | 0.13376 | 68400
6713 | 10 | 280 | 16 | 0 | 0.4677 | 0.13524 | 68400
6714 | 10 | 280 | 17 | 0 | 0.15545 | 0.096832 | 68400
6715 | 10 | 280 | 18 | 0 | 0 | 0.0907 | 68400
6716 | 10 | 280 | 19 | 1 | 0 | 0.16717 | 68200
6717 | 10 | 280 | 20 | 1 | 0 | 0.19108 | 68000
6718 | 10 | 280 | 21 | 0 | 0 | 0.31595 | 68000
6719 | 10 | 280 | 22 | 0 | 0 | 0.23925 | 68000
6720 | 10 | 280 | 23 | 0 | 0 | 0.2944 | 68000
6721 | 10 | 281 | 0 | 0 | 0 | 0.24284 | 68000
6722 | 10 | 281 | 1 | 0 | 0 | 0.21272 | 68000
6723 | 10 | 281 | 2 | 0 | 0 | 0.22147 | 68000
6724 | 10 | 281 | 3 | 0 | 0 | 0.20135 | 68000
6725 | 10 | 281 | 4 | 0 | 0 | 0.21466 | 68000
6726 | 10 | 281 | 5 | 0 | 0 | 0.25856 | 68000
6727 | 10 | 281 | 6 | 0 | 0 | 0.22642 | 68000
6728 | 10 | 281 | 7 | 1 | 0.13768 | 0.27103 | 67800
6729 | 10 | 281 | 8 | 1 | 0.41424 | 0.26254 | 67600
6730 | 10 | 281 | 9 | 0 | 0.70555 | 0.45509 | 67600
6731 | 10 | 281 | 10 | 0 | 0.95543 | 0.56384 | 67600
6732 | 10 | 281 | 11 | 0 | 1 | 0.60145 | 67600
6733 | 10 | 281 | 12 | 0 | 1 | 0.44975 | 67600
6734 | 10 | 281 | 13 | 0 | 1 | 0.57635 | 67600
6735 | 10 | 281 | 14 | 0 | 0.95543 | 0.45615 | 67600
6736 | 10 | 281 | 15 | 0 | 0.70555 | 0.37956 | 67600
6737 | 10 | 281 | 16 | 0 | 0.41424 | 0.35179 | 67600
6738 | 10 | 281 | 17 | 0 | 0.13768 | 0.25308 | 67600
6739 | 10 | 281 | 18 | 0 | 0 | 0.2365 | 67600
6740 | 10 | 281 | 19 | 1 | 0 | 0.26516 | 67400
6741 | 10 | 281 | 20 | 1 | 0 | 0.16942 | 67200
6742 | 10 | 281 | 21 | 0 | 0 | 0.13788 | 67200
6743 | 10 | 281 | 22 | 0 | 0 | 0.16873 | 67200
6744 | 10 | 281 | 23 | 0 | 0 | 0.19738 | 67200
6745 | 10 | 282 | 0 | 0 | 0 | 0.1731 | 67200
6746 | 10 | 282 | 1 | 0 | 0 | 0.17471 | 67200
6747 | 10 | 282 | 2 | 0 | 0 | 0.25836 | 67200
6748 | 10 | 282 | 3 | 0 | 0 | 0.28063 | 67200
6749 | 10 | 282 | 4 | 0 | 0 | 0.41164 | 67200
6750 | 10 | 282 | 5 | 0 | 0 | 0.49718 | 67200
6751 | 10 | 282 | 6 | 0 | 0 | 0.3596 | 67200
6752 | 10 | 282 | 7 | 1 | 0.15188 | 0.34763 | 67000
6753 | 10 | 282 | 8 | 1 | 0.45696 | 0.45905 | 66800
6754 | 10 | 282 | 9 | 0 | 0.77832 | 0.38399 | 66800
6755 | 10 | 282 | 10 | 0 | 1 | 0.51812 | 66800
6756 | 10 | 282 | 11 | 0 | 1 | 0.5144 | 66800
6757 | 10 | 282 | 12 | 0 | 1 | 0.42081 | 66800
6758 | 10 | 282 | 13 | 0 | 1 | 0.49761 | 66800
6759 | 10 | 282 | 14 | 0 | 1 | 0.47717 | 66800
6760 | 10 | 282 | 15 | 0 | 0.77832 | 0.53273 | 66800
6761 | 10 | 282 | 16 | 0 | 0.45696 | 0.34896 | 66800
6762 | 10 | 282 | 17 | 0 | 0.15188 | 0.38022 | 66800
6763 | 10 | 282 | 18 | 0 | 0 | 0.32347 | 66800
6764 | 10 | 282 | 19 | 1 | 0 | 0.39345 | 66600
6765 | 10 | 282 | 20 | 1 | 0 | 0.2843 | 66400
6766 | 10 | 282 | 21 | 0 | 0 | 0.1967 | 66400
6767 | 10 | 282 | 22 | 0 | 0 | 0.13443 | 66400
6768 | 10 | 282 | 23 | 0 | 0 | 0.086797 | 66400
6769 | 10 | 283 | 0 | 0 | 0 | 0.080316 | 66400
6770 | 10 | 283 | 1 | 0 | 0 | 0.097083 | 66400
6771 | 10 | 283 | 2 | 0 | 0 | 0.11742 | 66400
6772 | 10 | 283 | 3 | 0 | 0 | 0.10775 | 66400
6773 | 10 | 283 | 4 | 0 | 0 | 0.15396 | 66400
6774 | 10 | 283 | 5 | 0 | 0 | 0.16295 | 66400
6775 | 10 | 283 | 6 | 0 | 0 | 0.19509 | 66400
6776 | 10 | 283 | 7 | 1 | 0.15209 | 0.16008 | 66200
6777 | 10 | 283 | 8 | 1 | 0.45757 | 0.11352 | 66000
6778 | 10 | 283 | 9 | 0 | 0.77936 | 0.1394 | 66000
6779 | 10 | 283 | 10 | 0 | 1 | 0.10611 | 66000
6780 | 10 | 283 | 11 | 0 | 1 | 0.11101 | 66000
6781 | 10 | 283 | 12 | 0 | 1 | 0.1663 | 66000
6782 | 10 | 283 | 13 | 0 | 1 | 0.13806 | 66000
6783 | 10 | 283 | 14 | 0 | 1 | 0.15989 | 66000
6784 | 10 | 283 | 15 | 0 | 0.77936 | 0.27636 | 66000
6785 | 10 | 283 | 16 | 0 | 0.45757 | 0.37596 | 66000
6786 | 10 | 283 | 17 | 0 | 0.15209 | 0.45054 | 66000
6787 | 10 | 283 | 18 | 0 | 0 | 0.4449 | 66000
6788 | 10 | 283 | 19 | 1 | 0 | 0.4277 | 65800
6789 | 10 | 283 | 20 | 1 | 0 | 0.35051 | 65600
6790 | 10 | 283 | 21 | 0 | 0 | 0.50944 | 65600
6791 | 10 | 283 | 22 | 0 | 0 | 0.41802 | 65600
6792 | 10 | 283 | 23 | 0 | 0 | 0.40643 | 65600
6793 | 10 | 284 | 0 | 0 | 0 | 0.46317 | 65600
6794 | 10 | 284 | 1 | 0 | 0 | 0.48452 | 65600
6795 | 10 | 284 | 2 | 0 | 0 | 0.46823 | 65600
6796 | 10 | 284 | 3 | 0 | 0 | 0.42896 | 65600
6797 | 10 | 284 | 4 | 0 | 0 | 0.4854 | 65600
6798 | 10 | 284 | 5 | 0 | 0 | 0.62359 | 65600
6799 | 10 | 284 | 6 | 0 | 0 | 0.70958 | 65600
6800 | 10 | 284 | 7 | 1 | 0.15969 | 1 | 65400
6801 | 10 | 284 | 8 | 1 | 0.48044 | 1 | 65200
6802 | 10 | 284 | 9 | 0 | 0.81831 | 1 | 65200
6803 | 10 | 284 | 10 | 0 | 1 | 0.97273 | 65200
6804 | 10 | 284 | 11 | 0 | 1 | 0.79761 | 65200
6805 | 10 | 284 | 12 | 0 | 1 | 0.78299 | 65200
6806 | 10 | 284 | 13 | 0 | 1 | 0.78146 | 65200
6807 | 10 | 284 | 14 | 0 | 1 | 0.58343 | 65200
6808 | 10 | 284 | 15 | 0 | 0.81831 | 0.4034 | 65200
6809 | 10 | 284 | 16 | 0 | 0.48044 | 0.34062 | 65200
6810 | 10 | 284 | 17 | 0 | 0.15969 | 0.24449 | 65200
6811 | 10 | 284 | 18 | 0 | 0 | 0.3253 | 65200
6812 | 10 | 284 | 19 | 1 | 0 | 0.22914 | 65000
6813 | 10 | 284 | 20 | 1 | 0 | 0.23495 | 64800
6814 | 10 | 284 | 21 | 0 | 0 | 0.2155 | 64800
6815 | 10 | 284 | 22 | 0 | 0 | 0.19989 | 64800
6816 | 10 | 284 | 23 | 0 | 0 | 0.22508 | 64800
6817 | 10 | 285 | 0 | 0 | 0 | 0.19383 | 64800
6818 | 10 | 285 | 1 | 0 | 0 | 0.17968 | 64800
6819 | 10 | 285 | 2 | 0 | 0 | 0.29502 | 64800
6820 | 10 | 285 | 3 | 0 | 0 | 0.24285 | 64800
6821 | 10 | 285 | 4 | 0 | 0 | 0.24857 | 64800
6822 | 10 | 285 | 5 | 0 | 0 | 0.24348 | 64800
6823 | 10 | 285 | 6 | 0 | 0 | 0.33354 | 64800
6824 | 10 | 285 | 7 | 1 | 0.15625 | 0.33185 | 64600
6825 | 10 | 285 | 8 | 1 | 0.47009 | 0.30117 | 64400
6826 | 10 | 285 | 9 | 0 | 0.80068 | 0.43418 | 64400
6827 | 10 | 285 | 10 | 0 | 1 | 0.54002 | 64400
6828 | 10 | 285 | 11 | 0 | 1 | 0.55612 | 64400
6829 | 10 | 285 | 12 | 0 | 1 | 0.65596 | 64400
6830 | 10 | 285 | 13 | 0 | 1 | 0.52967 | 64400
6831 | 10 | 285 | 14 | 0 | 1 | 0.45871 | 64400
6832 | 10 | 285 | 15 | 0 | 0.80068 | 0.53833 | 64400
6833 | 10 | 285 | 16 | 0 | 0.47009 | 0.43397 | 64400
6834 | 10 | 285 | 17 | 0 | 0.15625 | 0.65986 | 64400
6835 | 10 | 285 | 18 | 0 | 0 | 0.4709 | 64400
6836 | 10 | 285 | 19 | 1 | 0 | 0.47246 | 64200
6837 | 10 | 285 | 20 | 1 | 0 | 0.43588 | 64000
6838 | 10 | 285 | 21 | 0 | 0 | 0.49132 | 64000
6839 | 10 | 285 | 22 | 0 | 0 | 0.6376 | 64000
6840 | 10 | 285 | 23 | 0 | 0 | 0.37511 | 64000
6841 | 10 | 286 | 0 | 0 | 0 | 0.41758 | 64000
6842 | 10 | 286 | 1 | 0 | 0 | 0.42396 | 64000
6843 | 10 | 286 | 2 | 0 | 0 | 0.56296 | 64000
6844 | 10 | 286 | 3 | 0 | 0 | 0.68581 | 64000
6845 | 10 | 286 | 4 | 0 | 0 | 0.50735 | 64000
6846 | 10 | 286 | 5 | 0 | 0 | 0.46591 | 64000
6847 | 10 | 286 | 6 | 0 | 0 | 0.42725 | 64000
6848 | 10 | 286 | 7 | 1 | 0.1761 | 0.58459 | 63800
6849 | 10 | 286 | 8 | 1 | 0.52983 | 0.65142 | 63600
6850 | 10 | 286 | 9 | 0 | 0.90243 | 0.57187 | 63600
6851 | 10 | 286 | 10 | 0 | 1 | 0.65381 | 63600
6852 | 10 | 286 | 11 | 0 | 1 | 0.68268 | 63600
6853 | 10 | 286 | 12 | 0 | 1 | 0.71443 | 63600
6854 | 10 | 286 | 13 | 0 | 1 | 0.7244 | 63600
6855 | 10 | 286 | 14 | 0 | 1 | 0.58029 | 63600
6856 | 10 | 286 | 15 | 0 | 0.90243 | 0.56066 | 63600
6857 | 10 | 286 | 16 | 0 | 0.52983 | 0.71677 | 63600
6858 | 10 | 286 | 17 | 0 | 0.1761 | 0.54861 | 63600
6859 | 10 | 286 | 18 | 0 | 0 | 0.64946 | 63600
6860 | 10 | 286 | 19 | 1 | 0 | 0.52171 | 63400
6861 | 10 | 286 | 20 | 1 | 0 | 0.5058 | 63200
6862 | 10 | 286 | 21 | 0 | 0 | 0.30013 | 63200
6863 | 10 | 286 | 22 | 0 | 0 | 0.34933 | 63200
6864 | 10 | 286 | 23 | 0 | 0 | 0.29596 | 63200
6865 | 10 | 287 | 0 | 0 | 0 | 0.35525 | 63200
6866 | 10 | 287 | 1 | 0 | 0 | 0.35364 | 63200
6867 | 10 | 287 | 2 | 0 | 0 | 0.51833 | 63200
6868 | 10 | 287 | 3 | 0 | 0 | 0.41163 | 63200
6869 | 10 | 287 | 4 | 0 | 0 | 0.49341 | 63200
6870 | 10 | 287 | 5 | 0 | 0 | 0.50004 | 63200
6871 | 10 | 287 | 6 | 0 | 0 | 0.48244 | 63200
6872 | 10 | 287 | 7 | 1 | 0.15476 | 0.69283 | 63000
6873 | 10 | 287 | 8 | 1 | 0.4656 | 0.51658 | 62800
6874 | 10 | 287 | 9 | 0 | 0.79304 | 0.59789 | 62800
6875 | 10 | 287 | 10 | 0 | 1 | 0.49705 | 62800
6876 | 10 | 287 | 11 | 0 | 1 | 0.81924 | 62800
6877 | 10 | 287 | 12 | 0 | 1 | 0.96272 | 62800
6878 | 10 | 287 | 13 | 0 | 1 | 0.76314 | 62800
6879 | 10 | 287 | 14 | 0 | 1 | 0.76829 | 62800
6880 | 10 | 287 | 15 | 0 | 0.79304 | 0.58742 | 62800
6881 | 10 | 287 | 16 | 0 | 0.4656 | 0.47576 | 62800
6882 | 10 | 287 | 17 | 0 | 0.15476 | 0.50687 | 62800
6883 | 10 | 287 | 18 | 0 | 0 | 0.48669 | 62800
6884 | 10 | 287 | 19 | 1 | 0 | 0.40794 | 62600
6885 | 10 | 287 | 20 | 1 | 0 | 0.40725 | 62400
6886 | 10 | 287 | 21 | 0 | 0 | 0.34713 | 62400
6887 | 10 | 287 | 22 | 0 | 0 | 0.36518 | 62400
6888 | 10 | 287 | 23 | 0 | 0 | 0.31744 | 62400
6889 | 10 | 288 | 0 | 0 | 0 | 0.1884 | 62400
6890 | 10 | 288 | 1 | 0 | 0 | 0.21389 | 62400
6891 | 10 | 288 | 2 | 0 | 0 | 0.25655 | 62400
6892 | 10 | 288 | 3 | 0 | 0 | 0.22428 | 62400
6893 | 10 | 288 | 4 | 0 | 0 | 0.17098 | 62400
6894 | 10 | 288 | 5 | 0 | 0 | 0.1508 | 62400
6895 | 10 | 288 | 6 | 0 | 0 | 0.20872 | 62400
6896 | 10 | 288 | 7 | 1 | 0.17633 | 0.20628 | 62200
6897 | 10 | 288 | 8 | 1 | 0.53052 | 0.31208 | 62000
6898 | 10 | 288 | 9 | 0 | 0.90361 | 0.31182 | 62000
6899 | 10 | 288 | 10 | 0 | 1 | 0.30848 | 62000
6900 | 10 | 288 | 11 | 0 | 1 | 0.25823 | 62000
6901 | 10 | 288 | 12 | 0 | 1 | 0.35094 | 62000
6902 | 10 | 288 | 13 | 0 | 1 | 0.42766 | 62000
6903 | 10 | 288 | 14 | 0 | 1 | 0.46284 | 62000
6904 | 10 | 288 | 15 | 0 | 0.90361 | 0.44662 | 62000
6905 | 10 | 288 | 16 | 0 | 0.53052 | 0.44012 | 62000
6906 | 10 | 288 | 17 | 0 | 0.17633 | 0.37349 | 62000
6907 | 10 | 288 | 18 | 0 | 0 | 0.33909 | 62000
6908 | 10 | 288 | 19 | 1 | 0 | 0.32162 | 61800
6909 | 10 | 288 | 20 | 1 | 0 | 0.26403 | 61600
6910 | 10 | 288 | 21 | 0 | 0 | 0.38541 | 61600
6911 | 10 | 288 | 22 | 0 | 0 | 0.35597 | 61600
6912 | 10 | 288 | 23 | 0 | 0 | 0.36467 | 61600
6913 | 10 | 289 | 0 | 0 | 0 | 0.3203 | 61600
6914 | 10 | 289 | 1 | 0 | 0 | 0.41108 | 61600
6915 | 10 | 289 | 2 | 0 | 0 | 0.51905 | 61600
6916 | 10 | 289 | 3 | 0 | 0 | 0.64766 | 61600
6917 | 10 | 289 | 4 | 0 | 0 | 0.66438 | 61600
6918 | 10 | 289 | 5 | 0 | 0 | 0.48098 | 61600
6919 | 10 | 289 | 6 | 0 | 0 | 0.74139 | 61600
6920 | 10 | 289 | 7 | 1 | 0.15137 | 0.84836 | 61400
6921 | 10 | 289 | 8 | 1 | 0.45542 | 1 | 61200
6922 | 10 | 289 | 9 | 0 | 0.77569 | 0.98905 | 61200
6923 | 10 | 289 | 10 | 0 | 1 | 1 | 61200
6924 | 10 | 289 | 11 | 0 | 1 | 1 | 61200
6925 | 10 | 289 | 12 | 0 | 1 | 0.73324 | 61200
6926 | 10 | 289 | 13 | 0 | 1 | 0.75765 | 61200
6927 | 10 | 289 | 14 | 0 | 1 | 0.82702 | 61200
6928 | 10 | 289 | 15 | 0 | 0.77569 | 0.4215 | 61200
6929 | 10 | 289 | 16 | 0 | 0.45542 | 0.77401 | 61200
6930 | 10 | 289 | 17 | 0 | 0.15137 | 0.67252 | 61200
6931 | 10 | 289 | 18 | 0 | 0 | 0.39533 | 61200
6932 | 10 | 289 | 19 | 1 | 0 | 0.3358 | 61000
6933 | 10 | 289 | 20 | 1 | 0 | 0.37049 | 60800
6934 | 10 | 289 | 21 | 0 | 0 | 0.25519 | 60800
6935 | 10 | 289 | 22 | 0 | 0 | 0.3066 | 60800
6936 | 10 | 289 | 23 | 0 | 0 | 0.27145 | 60800
6937 | 10 | 290 | 0 | 0 | 0 | 0.162 | 60800
6938 | 10 | 290 | 1 | 0 | 0 | 0.1439 | 60800
6939 | 10 | 290 | 2 | 0 | 0 | 0.15049 | 60800
6940 | 10 | 290 | 3 | 0 | 0 | 0.16185 | 60800
6941 | 10 | 290 | 4 | 0 | 0 | 0.17605 | 60800
6942 | 10 | 290 | 5 | 0 | 0 | 0.13504 | 60800
6943 | 10 | 290 | 6 | 0 | 0 | 0.17935 | 60800
6944 | 10 | 290 | 7 | 1 | 0.15591 | 0.17183 | 60600
6945 | 10 | 290 | 8 | 1 | 0.46908 | 0.18725 | 60400
6946 | 10 | 290 | 9 | 0 | 0.79895 | 0.19909 | 60400
6947 | 10 | 290 | 10 | 0 | 1 | 0.15684 | 60400
6948 | 10 | 290 | 11 | 0 | 1 | 0.22224 | 60400
6949 | 10 | 290 | 12 | 0 | 1 | 0.22846 | 60400
6950 | 10 | 290 | 13 | 0 | 1 | 0.2301 | 60400
6951 | 10 | 290 | 14 | 0 | 1 | 0.21738 | 60400
6952 | 10 | 290 | 15 | 0 | 0.79895 | 0.2193 | 60400
6953 | 10 | 290 | 16 | 0 | 0.46908 | 0.20249 | 60400
6954 | 10 | 290 | 17 | 0 | 0.15591 | 0.15684 | 60400
6955 | 10 | 290 | 18 | 0 | 0 | 0.18509 | 60400
6956 | 10 | 290 | 19 | 1 | 0 | 0.21074 | 60200
6957 | 10 | 290 | 20 | 1 | 0 | 0.22005 | 60000
6958 | 10 | 290 | 21 | 0 | 0 | 0.18386 | 60000
6959 | 10 | 290 | 22 | 0 | 0 | 0.28932 | 60000
6960 | 10 | 290 | 23 | 0 | 0 | 0.26085 | 60000
6961 | 10 | 291 | 0 | 0 | 0 | 0.38117 | 60000
6962 | 10 | 291 | 1 | 0 | 0 | 0.35575 | 60000
6963 | 10 | 291 | 2 | 0 | 0 | 0.27414 | 60000
6964 | 10 | 291 | 3 | 0 | 0 | 0.33391 | 60000
6965 | 10 | 291 | 4 | 0 | 0 | 0.34057 | 60000
6966 | 10 | 291 | 5 | 0 | 0 | 0.46981 | 60000
6967 | 10 | 291 | 6 | 0 | 0 | 0.44055 | 60000
6968 | 10 | 291 | 7 | 1 | 0.15719 | 0.44861 | 59800
6969 | 10 | 291 | 8 | 1 | 0.47292 | 0.36201 | 59600
6970 | 10 | 291 | 9 | 0 | 0.80551 | 0.45409 | 59600
6971 | 10 | 291 | 10 | 0 | 1 | 0.7065 | 59600
6972 | 10 | 291 | 11 | 0 | 1 | 0.83094 | 59600
6973 | 10 | 291 | 12 | 0 | 1 | 0.8101 | 59600
6974 | 10 | 291 | 13 | 0 | 1 | 0.97395 | 59600
6975 | 10 | 291 | 14 | 0 | 1 | 0.73808 | 59600
6976 | 10 | 291 | 15 | 0 | 0.80551 | 0.46289 | 59600
6977 | 10 | 291 | 16 | 0 | 0.47292 | 0.54562 | 59600
6978 | 10 | 291 | 17 | 0 | 0.15719 | 0.42178 | 59600
6979 | 10 | 291 | 18 | 0 | 0 | 0.38351 | 59600
6980 | 10 | 291 | 19 | 1 | 0 | 0.55276 | 59400
6981 | 10 | 291 | 20 | 1 | 0 | 0.31875 | 59200
6982 | 10 | 291 | 21 | 0 | 0 | 0.29729 | 59200
6983 | 10 | 291 | 22 | 0 | 0 | 0.40853 | 59200
6984 | 10 | 291 | 23 | 0 | 0 | 0.4495 | 59200
6985 | 10 | 292 | 0 | 0 | 0 | 0.59005 | 59200
6986 | 10 | 292 | 1 | 0 | 0 | 0.54796 | 59200
6987 | 10 | 292 | 2 | 0 | 0 | 0.54076 | 59200
6988 | 10 | 292 | 3 | 0 | 0 | 0.61266 | 59200
6989 | 10 | 292 | 4 | 0 | 0 | 0.50746 | 59200
6990 | 10 | 292 | 5 | 0 | 0 | 0.39752 | 59200
6991 | 10 | 292 | 6 | 0 | 0 | 0.4664 | 59200
6992 | 10 | 292 | 7 | 1 | 0.16855 | 0.45883 | 59000
6993 | 10 | 292 | 8 | 1 | 0.50709 | 0.34795 | 58800
6994 | 10 | 292 | 9 | 0 | 0.8637 | 0.34047 | 58800
6995 | 10 | 292 | 10 | 0 | 1 | 0.28262 | 58800
6996 | 10 | 292 | 11 | 0 | 1 | 0.39209 | 58800
6997 | 10 | 292 | 12 | 0 | 1 | 0.33267 | 58800
6998 | 10 | 292 | 13 | 0 | 1 | 0.3944 | 58800
6999 | 10 | 292 | 14 | 0 | 1 | 0.44588 | 58800
7000 | 10 | 292 | 15 | 0 | 0.8637 | 0.49906 | 58800
7001 | 10 | 292 | 16 | 0 | 0.50709 | 0.44835 | 58800
7002 | 10 | 292 | 17 | 0 | 0.16855 | 0.48977 | 58800
7003 | 10 | 292 | 18 | 0 | 0 | 0.33504 | 58800
7004 | 10 | 292 | 19 | 1 | 0 | 0.53133 | 58600
7005 | 10 | 292 | 20 | 1 | 0 | 0.57899 | 58400
7006 | 10 | 292 | 21 | 0 | 0 | 0.49109 | 58400
7007 | 10 | 292 | 22 | 0 | 0 | 0.45286 | 58400
7008 | 10 | 292 | 23 | 0 | 0 | 0.54565 | 58400
7009 | 10 | 293 | 0 | 0 | 0 | 0.65436 | 58400
7010 | 10 | 293 | 1 | 0 | 0 | 0.58683 | 58400
7011 | 10 | 293 | 2 | 0 | 0 | 0.55996 | 58400
7012 | 10 | 293 | 3 | 0 | 0 | 0.67138 | 58400
7013 | 10 | 293 | 4 | 0 | 0 | 0.50263 | 58400
7014 | 10 | 293 | 5 | 0 | 0 | 0.64412 | 58400
7015 | 10 | 293 | 6 | 0 | 0 | 0.79706 | 58400
7016 | 10 | 293 | 7 | 1 | 0.143 | 0.80628 | 58200
7017 | 10 | 293 | 8 | 1 | 0.43024 | 0.96787 | 58000
7018 | 10 | 293 | 9 | 0 | 0.73281 | 0.97191 | 58000
7019 | 10 | 293 | 10 | 0 | 0.99235 | 1 | 58000
7020 | 10 | 293 | 11 | 0 | 1 | 0.93263 | 58000
7021 | 10 | 293 | 12 | 0 | 1 | 0.79249 | 58000
7022 | 10 | 293 | 13 | 0 | 1 | 0.66946 | 58000
7023 | 10 | 293 | 14 | 0 | 0.99235 | 0.99027 | 58000
7024 | 10 | 293 | 15 | 0 | 0.73281 | 0.61174 | 58000
7025 | 10 | 293 | 16 | 0 | 0.43024 | 0.63792 | 58000
7026 | 10 | 293 | 17 | 0 | 0.143 | 0.69873 | 58000
7027 | 10 | 293 | 18 | 0 | 0 | 0.83265 | 58000
7028 | 10 | 293 | 19 | 1 | 0 | 0.6738 | 57800
7029 | 10 | 293 | 20 | 1 | 0 | 0.80556 | 57600
7030 | 10 | 293 | 21 | 0 | 0 | 0.70854 | 57600
7031 | 10 | 293 | 22 | 0 | 0 | 0.65255 | 57600
7032 | 10 | 293 | 23 | 0 | 0 | 0.63465 | 57600
7033 | 10 | 294 | 0 | 0 | 0 | 0.5479 | 57600
7034 | 10 | 294 | 1 | 0 | 0 | 0.39595 | 57600
7035 | 10 | 294 | 2 | 0 | 0 | 0.31121 | 57600
7036 | 10 | 294 | 3 | 0 | 0 | 0.23343 | 57600
7037 | 10 | 294 | 4 | 0 | 0 | 0.2294 | 57600
7038 | 10 | 294 | 5 | 0 | 0 | 0.21028 | 57600
7039 | 10 | 294 | 6 | 0 | 0 | 0.27791 | 57600
7040 | 10 | 294 | 7 | 1 | 0.15086 | 0.29089 | 57400
7041 | 10 | 294 | 8 | 1 | 0.4539 | 0.18924 | 57200
7042 | 10 | 294 | 9 | 0 | 0.7731 | 0.19056 | 57200
7043 | 10 | 294 | 10 | 0 | 1 | 0.21872 | 57200
7044 | 10 | 294 | 11 | 0 | 1 | 0.21938 | 57200
7045 | 10 | 294 | 12 | 0 | 1 | 0.25549 | 57200
7046 | 10 | 294 | 13 | 0 | 1 | 0.20844 | 57200
7047 | 10 | 294 | 14 | 0 | 1 | 0.31993 | 57200
7048 | 10 | 294 | 15 | 0 | 0.7731 | 0.38819 | 57200
7049 | 10 | 294 | 16 | 0 | 0.4539 | 0.37448 | 57200
7050 | 10 | 294 | 17 | 0 | 0.15086 | 0.30124 | 57200
7051 | 10 | 294 | 18 | 0 | 0 | 0.44899 | 57200
7052 | 10 | 294 | 19 | 1 | 0 | 0.61484 | 57000
7053 | 10 | 294 | 20 | 1 | 0 | 0.39106 | 56800
7054 | 10 | 294 | 21 | 0 | 0 | 0.41043 | 56800
7055 | 10 | 294 | 22 | 0 | 0 | 0.30531 | 56800
7056 | 10 | 294 | 23 | 0 | 0 | 0.31105 | 56800
7057 | 10 | 295 | 0 | 0 | 0 | 0.41184 | 56800
7058 | 10 | 295 | 1 | 0 | 0 | 0.40466 | 56800
7059 | 10 | 295 | 2 | 0 | 0 | 0.34471 | 56800
7060 | 10 | 295 | 3 | 0 | 0 | 0.36528 | 56800
7061 | 10 | 295 | 4 | 0 | 0 | 0.31623 | 56800
7062 | 10 | 295 | 5 | 0 | 0 | 0.43475 | 56800
7063 | 10 | 295 | 6 | 0 | 0 | 0.43856 | 56800
7064 | 10 | 295 | 7 | 1 | 0.15887 | 0.43105 | 56600
7065 | 10 | 295 | 8 | 1 | 0.47798 | 0.50433 | 56400
7066 | 10 | 295 | 9 | 0 | 0.81413 | 0.36915 | 56400
7067 | 10 | 295 | 10 | 0 | 1 | 0.23557 | 56400
7068 | 10 | 295 | 11 | 0 | 1 | 0.19623 | 56400
7069 | 10 | 295 | 12 | 0 | 1 | 0.12234 | 56400
7070 | 10 | 295 | 13 | 0 | 1 | 0.09307 | 56400
7071 | 10 | 295 | 14 | 0 | 1 | 0.071654 | 56400
7072 | 10 | 295 | 15 | 0 | 0.81413 | 0.10477 | 56400
7073 | 10 | 295 | 16 | 0 | 0.47798 | 0.16277 | 56400
7074 | 10 | 295 | 17 | 0 | 0.15887 | 0.17317 | 56400
7075 | 10 | 295 | 18 | 0 | 0 | 0.15342 | 56400
7076 | 10 | 295 | 19 | 1 | 0 | 0.13579 | 56200
7077 | 10 | 295 | 20 | 1 | 0 | 0.1319 | 56000
7078 | 10 | 295 | 21 | 0 | 0 | 0.10783 | 56000
7079 | 10 | 295 | 22 | 0 | 0 | 0.10287 | 56000
7080 | 10 | 295 | 23 | 0 | 0 | 0.088498 | 56000
7081 | 10 | 296 | 0 | 0 | 0 | 0.066135 | 56000
7082 | 10 | 296 | 1 | 0 | 0 | 0.048421 | 56000
7083 | 10 | 296 | 2 | 0 | 0 | 0.033215 | 56000
7084 | 10 | 296 | 3 | 0 | 0 | 0.045268 | 56000
7085 | 10 | 296 | 4 | 0 | 0 | 0.049623 | 56000
7086 | 10 | 296 | 5 | 0 | 0 | 0.049204 | 56000
7087 | 10 | 296 | 6 | 0 | 0 | 0.074546 | 56000
7088 | 10 | 296 | 7 | 1 | 0.15469 | 0.06174 | 55800
7089 | 10 | 296 | 8 | 1 | 0.4654 | 0.067824 | 55600
7090 | 10 | 296 | 9 | 0 | 0.79269 | 0.097882 | 55600
7091 | 10 | 296 | 10 | 0 | 1 | 0.11302 | 55600
7092 | 10 | 296 | 11 | 0 | 1 | 0.19804 | 55600
7093 | 10 | 296 | 12 | 0 | 1 | 0.32738 | 55600
7094 | 10 | 296 | 13 | 0 | 1 | 0.41343 | 55600
7095 | 10 | 296 | 14 | 0 | 1 | 0.5094 | 55600
7096 | 10 | 296 | 15 | 0 | 0.79269 | 0.52138 | 55600
7097 | 10 | 296 | 16 | 0 | 0.4654 | 0.36745 | 55600
7098 | 10 | 296 | 17 | 0 | 0.15469 | 0.38476 | 55600
7099 | 10 | 296 | 18 | 0 | 0 | 0.53335 | 55600
7100 | 10 | 296 | 19 | 1 | 0 | 0.32806 | 55400
7101 | 10 | 296 | 20 | 1 | 0 | 0.35039 | 55200
7102 | 10 | 296 | 21 | 0 | 0 | 0.48522 | 55200
7103 | 10 | 296 | 22 | 0 | 0 | 0.47965 | 55200
7104 | 10 | 296 | 23 | 0 | 0 | 0.4591 | 55200
7105 | 10 | 297 | 0 | 0 | 0 | 0.32584 | 55200
7106 | 10 | 297 | 1 | 0 | 0 | 0.29667 | 55200
7107 | 10 | 297 | 2 | 0 | 0 | 0.2098 | 55200
7108 | 10 | 297 | 3 | 0 | 0 | 0.31825 | 55200
7109 | 10 | 297 | 4 | 0 | 0 | 0.38499 | 55200
7110 | 10 | 297 | 5 | 0 | 0 | 0.56364 | 55200
7111 | 10 | 297 | 6 | 0 | 0 | 0.4492 | 55200
7112 | 10 | 297 | 7 | 1 | 0.18438 | 0.42066 | 55000
7113 | 10 | 297 | 8 | 1 | 0.55474 | 0.58196 | 54800
7114 | 10 | 297 | 9 | 0 | 0.94486 | 0.66512 | 54800
7115 | 10 | 297 | 10 | 0 | 1 | 0.84926 | 54800
7116 | 10 | 297 | 11 | 0 | 1 | 0.69115 | 54800
7117 | 10 | 297 | 12 | 0 | 1 | 0.91154 | 54800
7118 | 10 | 297 | 13 | 0 | 1 | 0.81814 | 54800
7119 | 10 | 297 | 14 | 0 | 1 | 0.84478 | 54800
7120 | 10 | 297 | 15 | 0 | 0.94486 | 0.84258 | 54800
7121 | 10 | 297 | 16 | 0 | 0.55474 | 0.68306 | 54800
7122 | 10 | 297 | 17 | 0 | 0.18438 | 0.61482 | 54800
7123 | 10 | 297 | 18 | 0 | 0 | 0.78995 | 54800
7124 | 10 | 297 | 19 | 1 | 0 | 0.98515 | 54600
7125 | 10 | 297 | 20 | 1 | 0 | 0.83874 | 54400
7126 | 10 | 297 | 21 | 0 | 0 | 1 | 54400
7127 | 10 | 297 | 22 | 0 | 0 | 0.7139 | 54400
7128 | 10 | 297 | 23 | 0 | 0 | 0.44722 | 54400
7129 | 10 | 298 | 0 | 0 | 0 | 0.51746 | 54400
7130 | 10 | 298 | 1 | 0 | 0 | 0.40556 | 54400
7131 | 10 | 298 | 2 | 0 | 0 | 0.38782 | 54400
7132 | 10 | 298 | 3 | 0 | 0 | 0.48871 | 54400
7133 | 10 | 298 | 4 | 0 | 0 | 0.44738 | 54400
7134 | 10 | 298 | 5 | 0 | 0 | 0.36433 | 54400
7135 | 10 | 298 | 6 | 0 | 0 | 0.40529 | 54400
7136 | 10 | 298 | 7 | 1 | 0.16081 | 0.40143 | 54200
7137 | 10 | 298 | 8 | 1 | 0.48383 | 0.30289 | 54000
7138 | 10 | 298 | 9 | 0 | 0.82408 | 0.4375 | 54000
7139 | 10 | 298 | 10 | 0 | 1 | 0.36237 | 54000
7140 | 10 | 298 | 11 | 0 | 1 | 0.34722 | 54000
7141 | 10 | 298 | 12 | 0 | 1 | 0.3808 | 54000
7142 | 10 | 298 | 13 | 0 | 1 | 0.38576 | 54000
7143 | 10 | 298 | 14 | 0 | 1 | 0.37499 | 54000
7144 | 10 | 298 | 15 | 0 | 0.82408 | 0.31443 | 54000
7145 | 10 | 298 | 16 | 0 | 0.48383 | 0.33649 | 54000
7146 | 10 | 298 | 17 | 0 | 0.16081 | 0.23234 | 54000
7147 | 10 | 298 | 18 | 0 | 0 | 0.21079 | 54000
7148 | 10 | 298 | 19 | 1 | 0 | 0.19265 | 53800
7149 | 10 | 298 | 20 | 1 | 0 | 0.2545 | 53600
7150 | 10 | 298 | 21 | 0 | 0 | 0.17232 | 53600
7151 | 10 | 298 | 22 | 0 | 0 | 0.12969 | 53600
7152 | 10 | 298 | 23 | 0 | 0 | 0.14825 | 53600
7153 | 10 | 299 | 0 | 0 | 0 | 0.21269 | 53600
7154 | 10 | 299 | 1 | 0 | 0 | 0.30976 | 53600
7155 | 10 | 299 | 2 | 0 | 0 | 0.32623 | 53600
7156 | 10 | 299 | 3 | 0 | 0 | 0.27963 | 53600
7157 | 10 | 299 | 4 | 0 | 0 | 0.3053 | 53600
7158 | 10 | 299 | 5 | 0 | 0 | 0.30652 | 53600
7159 | 10 | 299 | 6 | 0 | 0 | 0.45189 | 53600
7160 | 10 | 299 | 7 | 1 | 0.15678 | 0.44853 | 53400
7161 | 10 | 299 | 8 | 1 | 0.4717 | 0.60816 | 53200
7162 | 10 | 299 | 9 | 0 | 0.80342 | 0.58322 | 53200
7163 | 10 | 299 | 10 | 0 | 1 | 0.52539 | 53200
7164 | 10 | 299 | 11 | 0 | 1 | 0.5417 | 53200
7165 | 10 | 299 | 12 | 0 | 1 | 0.76116 | 53200
7166 | 10 | 299 | 13 | 0 | 1 | 0.51883 | 53200
7167 | 10 | 299 | 14 | 0 | 1 | 0.65573 | 53200
7168 | 10 | 299 | 15 | 0 | 0.80342 | 0.43368 | 53200
7169 | 10 | 299 | 16 | 0 | 0.4717 | 0.46027 | 53200
7170 | 10 | 299 | 17 | 0 | 0.15678 | 0.37426 | 53200
7171 | 10 | 299 | 18 | 0 | 0 | 0.30348 | 53200
7172 | 10 | 299 | 19 | 1 | 0 | 0.33316 | 53000
7173 | 10 | 299 | 20 | 1 | 0 | 0.35028 | 52800
7174 | 10 | 299 | 21 | 0 | 0 | 0.33463 | 52800
7175 | 10 | 299 | 22 | 0 | 0 | 0.23319 | 52800
7176 | 10 | 299 | 23 | 0 | 0 | 0.27677 | 52800
7177 | 10 | 300 | 0 | 0 | 0 | 0.26927 | 52800
7178 | 10 | 300 | 1 | 0 | 0 | 0.31335 | 52800
7179 | 10 | 300 | 2 | 0 | 0 | 0.22539 | 52800
7180 | 10 | 300 | 3 | 0 | 0 | 0.19768 | 52800
7181 | 10 | 300 | 4 | 0 | 0 | 0.28071 | 52800
7182 | 10 | 300 | 5 | 0 | 0 | 0.25052 | 52800
7183 | 10 | 300 | 6 | 0 | 0 | 0.39787 | 52800
7184 | 10 | 300 | 7 | 1 | 0.16259 | 0.49865 | 52600
7185 | 10 | 300 | 8 | 1 | 0.48918 | 0.51735 | 52400
7186 | 10 | 300 | 9 | 0 | 0.8332 | 0.61612 | 52400
7187 | 10 | 300 | 10 | 0 | 1 | 0.46812 | 52400
7188 | 10 | 300 | 11 | 0 | 1 | 0.48487 | 52400
7189 | 10 | 300 | 12 | 0 | 1 | 0.55007 | 52400
7190 | 10 | 300 | 13 | 0 | 1 | 0.59791 | 52400
7191 | 10 | 300 | 14 | 0 | 1 | 0.50229 | 52400
7192 | 10 | 300 | 15 | 0 | 0.8332 | 0.6199 | 52400
7193 | 10 | 300 | 16 | 0 | 0.48918 | 0.77196 | 52400
7194 | 10 | 300 | 17 | 0 | 0.16259 | 0.69125 | 52400
7195 | 10 | 300 | 18 | 0 | 0 | 0.84548 | 52400
7196 | 10 | 300 | 19 | 1 | 0 | 1 | 52200
7197 | 10 | 300 | 20 | 1 | 0 | 0.7099 | 52000
7198 | 10 | 300 | 21 | 0 | 0 | 0.57206 | 52000
7199 | 10 | 300 | 22 | 0 | 0 | 0.58907 | 52000
7200 | 10 | 300 | 23 | 0 | 0 | 0.65106 | 52000
7201 | 10 | 301 | 0 | 0 | 0 | 0.54964 | 52000
7202 | 10 | 301 | 1 | 0 | 0 | 0.57277 | 52000
7203 | 10 | 301 | 2 | 0 | 0 | 0.39937 | 52000
7204 | 10 | 301 | 3 | 0 | 0 | 0.58421 | 52000
7205 | 10 | 301 | 4 | 0 | 0 | 0.22006 | 52000
7206 | 10 | 301 | 5 | 0 | 0 | 0.21688 | 52000
7207 | 10 | 301 | 6 | 0 | 0 | 0.25655 | 52000
7208 | 10 | 301 | 7 | 1 | 0.16 | 0.23431 | 51800
7209 | 10 | 301 | 8 | 1 | 0.48139 | 0.15309 | 51600
7210 | 10 | 301 | 9 | 0 | 0.81993 | 0.12622 | 51600
7211 | 10 | 301 | 10 | 0 | 1 | 0.13268 | 51600
7212 | 10 | 301 | 11 | 0 | 1 | 0.15483 | 51600
7213 | 10 | 301 | 12 | 0 | 1 | 0.12732 | 51600
7214 | 10 | 301 | 13 | 0 | 1 | 0.11611 | 51600
7215 | 10 | 301 | 14 | 0 | 1 | 0.10798 | 51600
7216 | 10 | 301 | 15 | 0 | 0.81993 | 0.082451 | 51600
7217 | 10 | 301 | 16 | 0 | 0.48139 | 0.079246 | 51600
7218 | 10 | 301 | 17 | 0 | 0.16 | 0.088659 | 51600
7219 | 10 | 301 | 18 | 0 | 0 | 0.11063 | 51600
7220 | 10 | 301 | 19 | 1 | 0 | 0.114 | 51400
7221 | 10 | 301 | 20 | 1 | 0 | 0.091407 | 51200
7222 | 10 | 301 | 21 | 0 | 0 | 0.10392 | 51200
7223 | 10 | 301 | 22 | 0 | 0 | 0.13685 | 51200
7224 | 10 | 301 | 23 | 0 | 0 | 0.12927 | 51200
7225 | 10 | 302 | 0 | 0 | 0 | 0.14307 | 51200
7226 | 10 | 302 | 1 | 0 | 0 | 0.1567 | 51200
7227 | 10 | 302 | 2 | 0 | 0 | 0.21741 | 51200
7228 | 10 | 302 | 3 | 0 | 0 | 0.14981 | 51200
7229 | 10 | 302 | 4 | 0 | 0 | 0.12698 | 51200
7230 | 10 | 302 | 5 | 0 | 0 | 0.14349 | 51200
7231 | 10 | 302 | 6 | 0 | 0 | 0.13546 | 51200
7232 | 10 | 302 | 7 | 1 | 0.13726 | 0.1303 | 51000
7233 | 10 | 302 | 8 | 1 | 0.41298 | 0.2111 | 50800
7234 | 10 | 302 | 9 | 0 | 0.7034 | 0.25603 | 50800
7235 | 10 | 302 | 10 | 0 | 0.95252 | 0.22357 | 50800
7236 | 10 | 302 | 11 | 0 | 1 | 0.16186 | 50800
7237 | 10 | 302 | 12 | 0 | 1 | 0.22767 | 50800
7238 | 10 | 302 | 13 | 0 | 1 | 0.28135 | 50800
7239 | 10 | 302 | 14 | 0 | 0.95252 | 0.18743 | 50800
7240 | 10 | 302 | 15 | 0 | 0.7034 | 0.21121 | 50800
7241 | 10 | 302 | 16 | 0 | 0.41298 | 0.20005 | 50800
7242 | 10 | 302 | 17 | 0 | 0.13726 | 0.2943 | 50800
7243 | 10 | 302 | 18 | 0 | 0 | 0.33582 | 50800
7244 | 10 | 302 | 19 | 1 | 0 | 0.23238 | 50600
7245 | 10 | 302 | 20 | 1 | 0 | 0.10896 | 50400
7246 | 10 | 302 | 21 | 0 | 0 | 0.15471 | 50400
7247 | 10 | 302 | 22 | 0 | 0 | 0.20528 | 50400
7248 | 10 | 302 | 23 | 0 | 0 | 0.22386 | 50400
7249 | 10 | 303 | 0 | 0 | 0 | 0.18989 | 50400
7250 | 10 | 303 | 1 | 0 | 0 | 0.19704 | 50400
7251 | 10 | 303 | 2 | 0 | 0 | 0.14558 | 50400
7252 | 10 | 303 | 3 | 0 | 0 | 0.169 | 50400
7253 | 10 | 303 | 4 | 0 | 0 | 0.21639 | 50400
7254 | 10 | 303 | 5 | 0 | 0 | 0.2926 | 50400
7255 | 10 | 303 | 6 | 0 | 0 | 0.32058 | 50400
7256 | 10 | 303 | 7 | 1 | 0.13967 | 0.38706 | 50200
7257 | 10 | 303 | 8 | 1 | 0.42023 | 0.43851 | 50000
7258 | 10 | 303 | 9 | 0 | 0.71576 | 0.89125 | 50000
7259 | 10 | 303 | 10 | 0 | 0.96926 | 1 | 50000
7260 | 10 | 303 | 11 | 0 | 1 | 0.92318 | 50000
7261 | 10 | 303 | 12 | 0 | 1 | 0.67631 | 50000
7262 | 10 | 303 | 13 | 0 | 1 | 0.59508 | 50000
7263 | 10 | 303 | 14 | 0 | 0.96926 | 0.32876 | 50000
7264 | 10 | 303 | 15 | 0 | 0.71576 | 0.29589 | 50000
7265 | 10 | 303 | 16 | 0 | 0.42023 | 0.31562 | 50000
7266 | 10 | 303 | 17 | 0 | 0.13967 | 0.3821 | 50000
7267 | 10 | 303 | 18 | 0 | 0 | 0.40074 | 50000
7268 | 10 | 303 | 19 | 1 | 0 | 0.71236 | 49800
7269 | 10 | 303 | 20 | 1 | 0 | 0.64168 | 49600
7270 | 10 | 303 | 21 | 0 | 0 | 0.85665 | 49600
7271 | 10 | 303 | 22 | 0 | 0 | 0.83716 | 49600
7272 | 10 | 303 | 23 | 0 | 0 | 0.60718 | 49600
7273 | 10 | 304 | 0 | 0 | 0 | 0.35096 | 49600
7274 | 10 | 304 | 1 | 0 | 0 | 0.32076 | 49600
7275 | 10 | 304 | 2 | 0 | 0 | 0.24969 | 49600
7276 | 10 | 304 | 3 | 0 | 0 | 0.34693 | 49600
7277 | 10 | 304 | 4 | 0 | 0 | 0.34019 | 49600
7278 | 10 | 304 | 5 | 0 | 0 | 0.27398 | 49600
7279 | 10 | 304 | 6 | 0 | 0 | 0.30526 | 49600
7280 | 10 | 304 | 7 | 1 | 0.14995 | 0.32939 | 49400
7281 | 10 | 304 | 8 | 1 | 0.45114 | 0.29456 | 49200
7282 | 10 | 304 | 9 | 0 | 0.76841 | 0.3454 | 49200
7283 | 10 | 304 | 10 | 0 | 1 | 0.63579 | 49200
7284 | 10 | 304 | 11 | 0 | 1 | 0.87186 | 49200
7285 | 10 | 304 | 12 | 0 | 1 | 1 | 49200
7286 | 10 | 304 | 13 | 0 | 1 | 1 | 49200
7287 | 10 | 304 | 14 | 0 | 1 | 1 | 49200
7288 | 10 | 304 | 15 | 0 | 0.76841 | 0.94366 | 49200
7289 | 10 | 304 | 16 | 0 | 0.45114 | 0.67126 | 49200
7290 | 10 | 304 | 17 | 0 | 0.14995 | 0.79173 | 49200
7291 | 10 | 304 | 18 | 0 | 0 | 0.44784 | 49200
7292 | 10 | 304 | 19 | 1 | 0 | 0.40009 | 49000
7293 | 10 | 304 | 20 | 1 | 0 | 0.26239 | 48800
7294 | 10 | 304 | 21 | 0 | 0 | 0.1392 | 48800
7295 | 10 | 304 | 22 | 0 | 0 | 0.16406 | 48800
7296 | 10 | 304 | 23 | 0 | 0 | 0.15284 | 48800
7297 | 11 | 305 | 0 | 0 | 0 | 0.10271 | 48800
7298 | 11 | 305 | 1 | 0 | 0 | 0.077925 | 48800
7299 | 11 | 305 | 2 | 0 | 0 | 0.092586 | 48800
7300 | 11 | 305 | 3 | 0 | 0 | 0.16167 | 48800
7301 | 11 | 305 | 4 | 0 | 0 | 0.1559 | 48800
7302 | 11 | 305 | 5 | 0 | 0 | 0.17 | 48800
7303 | 11 | 305 | 6 | 0 | 0 | 0.2222 | 48800
7304 | 11 | 305 | 7 | 1 | 0.08065 | 0.31136 | 48600
7305 | 11 | 305 | 8 | 1 | 0.37765 | 0.40415 | 48400
7306 | 11 | 305 | 9 | 0 | 0.71158 | 0.53425 | 48400
7307 | 11 | 305 | 10 | 0 | 1 | 0.31146 | 48400
7308 | 11 | 305 | 11 | 0 | 1 | 0.27857 | 48400
7309 | 11 | 305 | 12 | 0 | 1 | 0.23728 | 48400
7310 | 11 | 305 | 13 | 0 | 1 | 0.25531 | 48400
7311 | 11 | 305 | 14 | 0 | 1 | 0.2247 | 48400
7312 | 11 | 305 | 15 | 0 | 0.71158 | 0.19383 | 48400
7313 | 11 | 305 | 16 | 0 | 0.37765 | 0.21586 | 48400
7314 | 11 | 305 | 17 | 0 | 0.08065 | 0.22891 | 48400
7315 | 11 | 305 | 18 | 0 | 0 | 0.1422 | 48400
7316 | 11 | 305 | 19 | 1 | 0 | 0.18464 | 48200
7317 | 11 | 305 | 20 | 1 | 0 | 0.1961 | 48000
7318 | 11 | 305 | 21 | 0 | 0 | 0.4184 | 48000
7319 | 11 | 305 | 22 | 0 | 0 | 0.34965 | 48000
7320 | 11 | 305 | 23 | 0 | 0 | 0.31477 | 48000
7321 | 11 | 306 | 0 | 0 | 0 | 0.35386 | 48000
7322 | 11 | 306 | 1 | 0 | 0 | 0.40408 | 48000
7323 | 11 | 306 | 2 | 0 | 0 | 0.42492 | 48000
7324 | 11 | 306 | 3 | 0 | 0 | 0.41684 | 48000
7325 | 11 | 306 | 4 | 0 | 0 | 0.40816 | 48000
7326 | 11 | 306 | 5 | 0 | 0 | 0.61333 | 48000
7327 | 11 | 306 | 6 | 0 | 0 | 0.76582 | 48000
7328 | 11 | 306 | 7 | 1 | 0.086069 | 0.83062 | 47800
7329 | 11 | 306 | 8 | 1 | 0.40303 | 0.77449 | 47600
7330 | 11 | 306 | 9 | 0 | 0.7594 | 0.66693 | 47600
7331 | 11 | 306 | 10 | 0 | 1 | 0.67361 | 47600
7332 | 11 | 306 | 11 | 0 | 1 | 0.94303 | 47600
7333 | 11 | 306 | 12 | 0 | 1 | 0.99023 | 47600
7334 | 11 | 306 | 13 | 0 | 1 | 0.80941 | 47600
7335 | 11 | 306 | 14 | 0 | 1 | 0.65598 | 47600
7336 | 11 | 306 | 15 | 0 | 0.7594 | 0.37668 | 47600
7337 | 11 | 306 | 16 | 0 | 0.40303 | 0.35833 | 47600
7338 | 11 | 306 | 17 | 0 | 0.086069 | 0.3634 | 47600
7339 | 11 | 306 | 18 | 0 | 0 | 0.41322 | 47600
7340 | 11 | 306 | 19 | 1 | 0 | 0.2949 | 47400
7341 | 11 | 306 | 20 | 1 | 0 | 0.2378 | 47200
7342 | 11 | 306 | 21 | 0 | 0 | 0.19446 | 47200
7343 | 11 | 306 | 22 | 0 | 0 | 0.19121 | 47200
7344 | 11 | 306 | 23 | 0 | 0 | 0.23937 | 47200
7345 | 11 | 307 | 0 | 0 | 0 | 0.14305 | 47200
7346 | 11 | 307 | 1 | 0 | 0 | 0.15129 | 47200
7347 | 11 | 307 | 2 | 0 | 0 | 0.14252 | 47200
7348 | 11 | 307 | 3 | 0 | 0 | 0.13267 | 47200
7349 | 11 | 307 | 4 | 0 | 0 | 0.14257 | 47200
7350 | 11 | 307 | 5 | 0 | 0 | 0.15336 | 47200
7351 | 11 | 307 | 6 | 0 | 0 | 0.14891 | 47200
7352 | 11 | 307 | 7 | 1 | 0.090522 | 0.20204 | 47000
7353 | 11 | 307 | 8 | 1 | 0.42388 | 0.18657 | 46800
7354 | 11 | 307 | 9 | 0 | 0.79868 | 0.1839 | 46800
7355 | 11 | 307 | 10 | 0 | 1 | 0.23747 | 46800
7356 | 11 | 307 | 11 | 0 | 1 | 0.287 | 46800
7357 | 11 | 307 | 12 | 0 | 1 | 0.28528 | 46800
7358 | 11 | 307 | 13 | 0 | 1 | 0.24739 | 46800
7359 | 11 | 307 | 14 | 0 | 1 | 0.27206 | 46800
7360 | 11 | 307 | 15 | 0 | 0.79868 | 0.25302 | 46800
7361 | 11 | 307 | 16 | 0 | 0.42388 | 0.3418 | 46800
7362 | 11 | 307 | 17 | 0 | 0.090522 | 0.40622 | 46800
7363 | 11 | 307 | 18 | 0 | 0 | 0.38615 | 46800
7364 | 11 | 307 | 19 | 1 | 0 | 0.25683 | 46600
7365 | 11 | 307 | 20 | 1 | 0 | 0.18723 | 46400
7366 | 11 | 307 | 21 | 0 | 0 | 0.24577 | 46400
7367 | 11 | 307 | 22 | 0 | 0 | 0.23679 | 46400
7368 | 11 | 307 | 23 | 0 | 0 | 0.26778 | 46400
7369 | 11 | 308 | 0 | 0 | 0 | 0.20499 | 46400
7370 | 11 | 308 | 1 | 0 | 0 | 0.11432 | 46400
7371 | 11 | 308 | 2 | 0 | 0 | 0.12406 | 46400
7372 | 11 | 308 | 3 | 0 | 0 | 0.13437 | 46400
7373 | 11 | 308 | 4 | 0 | 0 | 0.13577 | 46400
7374 | 11 | 308 | 5 | 0 | 0 | 0.13496 | 46400
7375 | 11 | 308 | 6 | 0 | 0 | 0.14954 | 46400
7376 | 11 | 308 | 7 | 1 | 0.086486 | 0.13334 | 46200
7377 | 11 | 308 | 8 | 1 | 0.40498 | 0.23322 | 46000
7378 | 11 | 308 | 9 | 0 | 0.76307 | 0.25994 | 46000
7379 | 11 | 308 | 10 | 0 | 1 | 0.28507 | 46000
7380 | 11 | 308 | 11 | 0 | 1 | 0.31682 | 46000
7381 | 11 | 308 | 12 | 0 | 1 | 0.27486 | 46000
7382 | 11 | 308 | 13 | 0 | 1 | 0.38484 | 46000
7383 | 11 | 308 | 14 | 0 | 1 | 0.33118 | 46000
7384 | 11 | 308 | 15 | 0 | 0.76307 | 0.2694 | 46000
7385 | 11 | 308 | 16 | 0 | 0.40498 | 0.20004 | 46000
7386 | 11 | 308 | 17 | 0 | 0.086486 | 0.18527 | 46000
7387 | 11 | 308 | 18 | 0 | 0 | 0.20082 | 46000
7388 | 11 | 308 | 19 | 1 | 0 | 0.17391 | 45800
7389 | 11 | 308 | 20 | 1 | 0 | 0.14403 | 45600
7390 | 11 | 308 | 21 | 0 | 0 | 0.16043 | 45600
7391 | 11 | 308 | 22 | 0 | 0 | 0.20161 | 45600
7392 | 11 | 308 | 23 | 0 | 0 | 0.24427 | 45600
7393 | 11 | 309 | 0 | 0 | 0 | 0.22901 | 45600
7394 | 11 | 309 | 1 | 0 | 0 | 0.1769 | 45600
7395 | 11 | 309 | 2 | 0 | 0 | 0.12275 | 45600
7396 | 11 | 309 | 3 | 0 | 0 | 0.1733 | 45600
7397 | 11 | 309 | 4 | 0 | 0 | 0.34438 | 45600
7398 | 11 | 309 | 5 | 0 | 0 | 0.34795 | 45600
7399 | 11 | 309 | 6 | 0 | 0 | 0.31103 | 45600
7400 | 11 | 309 | 7 | 1 | 0.091204 | 0.33351 | 45400
7401 | 11 | 309 | 8 | 1 | 0.42707 | 0.32925 | 45200
7402 | 11 | 309 | 9 | 0 | 0.8047 | 0.24001 | 45200
7403 | 11 | 309 | 10 | 0 | 1 | 0.20183 | 45200
7404 | 11 | 309 | 11 | 0 | 1 | 0.12689 | 45200
7405 | 11 | 309 | 12 | 0 | 1 | 0.19315 | 45200
7406 | 11 | 309 | 13 | 0 | 1 | 0.15494 | 45200
7407 | 11 | 309 | 14 | 0 | 1 | 0.23876 | 45200
7408 | 11 | 309 | 15 | 0 | 0.8047 | 0.1932 | 45200
7409 | 11 | 309 | 16 | 0 | 0.42707 | 0.12442 | 45200
7410 | 11 | 309 | 17 | 0 | 0.091204 | 0.15466 | 45200
7411 | 11 | 309 | 18 | 0 | 0 | 0.1486 | 45200
7412 | 11 | 309 | 19 | 1 | 0 | 0.25928 | 45000
7413 | 11 | 309 | 20 | 1 | 0 | 0.30991 | 44800
7414 | 11 | 309 | 21 | 0 | 0 | 0.19611 | 44800
7415 | 11 | 309 | 22 | 0 | 0 | 0.19579 | 44800
7416 | 11 | 309 | 23 | 0 | 0 | 0.15141 | 44800
7417 | 11 | 310 | 0 | 0 | 0 | 0.18669 | 44800
7418 | 11 | 310 | 1 | 0 | 0 | 0.35472 | 44800
7419 | 11 | 310 | 2 | 0 | 0 | 0.27402 | 44800
7420 | 11 | 310 | 3 | 0 | 0 | 0.37989 | 44800
7421 | 11 | 310 | 4 | 0 | 0 | 0.22795 | 44800
7422 | 11 | 310 | 5 | 0 | 0 | 0.23089 | 44800
7423 | 11 | 310 | 6 | 0 | 0 | 0.22217 | 44800
7424 | 11 | 310 | 7 | 1 | 0.097551 | 0.40572 | 44600
7425 | 11 | 310 | 8 | 1 | 0.45679 | 0.31732 | 44400
7426 | 11 | 310 | 9 | 0 | 0.8607 | 0.40528 | 44400
7427 | 11 | 310 | 10 | 0 | 1 | 0.39168 | 44400
7428 | 11 | 310 | 11 | 0 | 1 | 0.83145 | 44400
7429 | 11 | 310 | 12 | 0 | 1 | 1 | 44400
7430 | 11 | 310 | 13 | 0 | 1 | 1 | 44400
7431 | 11 | 310 | 14 | 0 | 1 | 1 | 44400
7432 | 11 | 310 | 15 | 0 | 0.8607 | 1 | 44400
7433 | 11 | 310 | 16 | 0 | 0.45679 | 0.76083 | 44400
7434 | 11 | 310 | 17 | 0 | 0.097551 | 0.60042 | 44400
7435 | 11 | 310 | 18 | 0 | 0 | 0.37316 | 44400
7436 | 11 | 310 | 19 | 1 | 0 | 0.30798 | 44200
7437 | 11 | 310 | 20 | 1 | 0 | 0.2617 | 44000
7438 | 11 | 310 | 21 | 0 | 0 | 0.27603 | 44000
7439 | 11 | 310 | 22 | 0 | 0 | 0.28035 | 44000
7440 | 11 | 310 | 23 | 0 | 0 | 0.24487 | 44000
7441 | 11 | 311 | 0 | 0 | 0 | 0.24115 | 44000
7442 | 11 | 311 | 1 | 0 | 0 | 0.28694 | 44000
7443 | 11 | 311 | 2 | 0 | 0 | 0.24407 | 44000
7444 | 11 | 311 | 3 | 0 | 0 | 0.1857 | 44000
7445 | 11 | 311 | 4 | 0 | 0 | 0.11667 | 44000
7446 | 11 | 311 | 5 | 0 | 0 | 0.11185 | 44000
7447 | 11 | 311 | 6 | 0 | 0 | 0.12294 | 44000
7448 | 11 | 311 | 7 | 1 | 0.084335 | 0.12299 | 43800
7449 | 11 | 311 | 8 | 1 | 0.39491 | 0.20375 | 43600
7450 | 11 | 311 | 9 | 0 | 0.7441 | 0.23775 | 43600
7451 | 11 | 311 | 10 | 0 | 1 | 0.20274 | 43600
7452 | 11 | 311 | 11 | 0 | 1 | 0.23973 | 43600
7453 | 11 | 311 | 12 | 0 | 1 | 0.2687 | 43600
7454 | 11 | 311 | 13 | 0 | 1 | 0.18684 | 43600
7455 | 11 | 311 | 14 | 0 | 1 | 0.14184 | 43600
7456 | 11 | 311 | 15 | 0 | 0.7441 | 0.17802 | 43600
7457 | 11 | 311 | 16 | 0 | 0.39491 | 0.15877 | 43600
7458 | 11 | 311 | 17 | 0 | 0.084335 | 0.16704 | 43600
7459 | 11 | 311 | 18 | 0 | 0 | 0.1806 | 43600
7460 | 11 | 311 | 19 | 1 | 0 | 0.20576 | 43400
7461 | 11 | 311 | 20 | 1 | 0 | 0.17699 | 43200
7462 | 11 | 311 | 21 | 0 | 0 | 0.13867 | 43200
7463 | 11 | 311 | 22 | 0 | 0 | 0.17508 | 43200
7464 | 11 | 311 | 23 | 0 | 0 | 0.13173 | 43200
7465 | 11 | 312 | 0 | 0 | 0 | 0.14952 | 43200
7466 | 11 | 312 | 1 | 0 | 0 | 0.10299 | 43200
7467 | 11 | 312 | 2 | 0 | 0 | 0.08999 | 43200
7468 | 11 | 312 | 3 | 0 | 0 | 0.084451 | 43200
7469 | 11 | 312 | 4 | 0 | 0 | 0.10298 | 43200
7470 | 11 | 312 | 5 | 0 | 0 | 0.092605 | 43200
7471 | 11 | 312 | 6 | 0 | 0 | 0.12535 | 43200
7472 | 11 | 312 | 7 | 1 | 0.078207 | 0.20012 | 43000
7473 | 11 | 312 | 8 | 1 | 0.36621 | 0.32817 | 42800
7474 | 11 | 312 | 9 | 0 | 0.69003 | 0.47991 | 42800
7475 | 11 | 312 | 10 | 0 | 0.9752 | 0.70387 | 42800
7476 | 11 | 312 | 11 | 0 | 1 | 0.64725 | 42800
7477 | 11 | 312 | 12 | 0 | 1 | 0.44655 | 42800
7478 | 11 | 312 | 13 | 0 | 1 | 0.27746 | 42800
7479 | 11 | 312 | 14 | 0 | 0.9752 | 0.29007 | 42800
7480 | 11 | 312 | 15 | 0 | 0.69003 | 0.32722 | 42800
7481 | 11 | 312 | 16 | 0 | 0.36621 | 0.33688 | 42800
7482 | 11 | 312 | 17 | 0 | 0.078207 | 0.31635 | 42800
7483 | 11 | 312 | 18 | 0 | 0 | 0.41127 | 42800
7484 | 11 | 312 | 19 | 1 | 0 | 0.29377 | 42600
7485 | 11 | 312 | 20 | 1 | 0 | 0.42207 | 42400
7486 | 11 | 312 | 21 | 0 | 0 | 0.42149 | 42400
7487 | 11 | 312 | 22 | 0 | 0 | 0.50798 | 42400
7488 | 11 | 312 | 23 | 0 | 0 | 0.26583 | 42400
7489 | 11 | 313 | 0 | 0 | 0 | 0.23298 | 42400
7490 | 11 | 313 | 1 | 0 | 0 | 0.25598 | 42400
7491 | 11 | 313 | 2 | 0 | 0 | 0.37926 | 42400
7492 | 11 | 313 | 3 | 0 | 0 | 0.28603 | 42400
7493 | 11 | 313 | 4 | 0 | 0 | 0.42519 | 42400
7494 | 11 | 313 | 5 | 0 | 0 | 0.31459 | 42400
7495 | 11 | 313 | 6 | 0 | 0 | 0.3114 | 42400
7496 | 11 | 313 | 7 | 1 | 0.09592 | 0.31488 | 42200
7497 | 11 | 313 | 8 | 1 | 0.44916 | 0.45448 | 42000
7498 | 11 | 313 | 9 | 0 | 0.84631 | 0.34644 | 42000
7499 | 11 | 313 | 10 | 0 | 1 | 0.3855 | 42000
7500 | 11 | 313 | 11 | 0 | 1 | 0.39279 | 42000
7501 | 11 | 313 | 12 | 0 | 1 | 0.3086 | 42000
7502 | 11 | 313 | 13 | 0 | 1 | 0.25353 | 42000
7503 | 11 | 313 | 14 | 0 | 1 | 0.34691 | 42000
7504 | 11 | 313 | 15 | 0 | 0.84631 | 0.41016 | 42000
7505 | 11 | 313 | 16 | 0 | 0.44916 | 0.53106 | 42000
7506 | 11 | 313 | 17 | 0 | 0.09592 | 0.50351 | 42000
7507 | 11 | 313 | 18 | 0 | 0 | 0.54297 | 42000
7508 | 11 | 313 | 19 | 1 | 0 | 0.82931 | 41800
7509 | 11 | 313 | 20 | 1 | 0 | 0.74594 | 41600
7510 | 11 | 313 | 21 | 0 | 0 | 0.67132 | 41600
7511 | 11 | 313 | 22 | 0 | 0 | 0.69603 | 41600
7512 | 11 | 313 | 23 | 0 | 0 | 0.6013 | 41600
7513 | 11 | 314 | 0 | 0 | 0 | 0.45699 | 41600
7514 | 11 | 314 | 1 | 0 | 0 | 0.4558 | 41600
7515 | 11 | 314 | 2 | 0 | 0 | 0.35654 | 41600
7516 | 11 | 314 | 3 | 0 | 0 | 0.39195 | 41600
7517 | 11 | 314 | 4 | 0 | 0 | 0.46372 | 41600
7518 | 11 | 314 | 5 | 0 | 0 | 0.37616 | 41600
7519 | 11 | 314 | 6 | 0 | 0 | 0.44784 | 41600
7520 | 11 | 314 | 7 | 1 | 0.083715 | 0.54132 | 41400
7521 | 11 | 314 | 8 | 1 | 0.39201 | 0.40768 | 41200
7522 | 11 | 314 | 9 | 0 | 0.73863 | 0.60788 | 41200
7523 | 11 | 314 | 10 | 0 | 1 | 0.45358 | 41200
7524 | 11 | 314 | 11 | 0 | 1 | 0.42944 | 41200
7525 | 11 | 314 | 12 | 0 | 1 | 0.48417 | 41200
7526 | 11 | 314 | 13 | 0 | 1 | 0.62993 | 41200
7527 | 11 | 314 | 14 | 0 | 1 | 0.69641 | 41200
7528 | 11 | 314 | 15 | 0 | 0.73863 | 0.67133 | 41200
7529 | 11 | 314 | 16 | 0 | 0.39201 | 0.43235 | 41200
7530 | 11 | 314 | 17 | 0 | 0.083715 | 0.47071 | 41200
7531 | 11 | 314 | 18 | 0 | 0 | 0.51265 | 41200
7532 | 11 | 314 | 19 | 1 | 0 | 0.61684 | 41000
7533 | 11 | 314 | 20 | 1 | 0 | 0.32206 | 40800
7534 | 11 | 314 | 21 | 0 | 0 | 0.37361 | 40800
7535 | 11 | 314 | 22 | 0 | 0 | 0.31555 | 40800
7536 | 11 | 314 | 23 | 0 | 0 | 0.36884 | 40800
7537 | 11 | 315 | 0 | 0 | 0 | 0.42192 | 40800
7538 | 11 | 315 | 1 | 0 | 0 | 0.45334 | 40800
7539 | 11 | 315 | 2 | 0 | 0 | 0.51871 | 40800
7540 | 11 | 315 | 3 | 0 | 0 | 0.32029 | 40800
7541 | 11 | 315 | 4 | 0 | 0 | 0.39026 | 40800
7542 | 11 | 315 | 5 | 0 | 0 | 0.28204 | 40800
7543 | 11 | 315 | 6 | 0 | 0 | 0.16582 | 40800
7544 | 11 | 315 | 7 | 1 | 0.08601 | 0.10098 | 40600
7545 | 11 | 315 | 8 | 1 | 0.40275 | 0.093772 | 40400
7546 | 11 | 315 | 9 | 0 | 0.75887 | 0.10966 | 40400
7547 | 11 | 315 | 10 | 0 | 1 | 0.19464 | 40400
7548 | 11 | 315 | 11 | 0 | 1 | 0.20077 | 40400
7549 | 11 | 315 | 12 | 0 | 1 | 0.26673 | 40400
7550 | 11 | 315 | 13 | 0 | 1 | 0.23053 | 40400
7551 | 11 | 315 | 14 | 0 | 1 | 0.27365 | 40400
7552 | 11 | 315 | 15 | 0 | 0.75887 | 0.28276 | 40400
7553 | 11 | 315 | 16 | 0 | 0.40275 | 0.38857 | 40400
7554 | 11 | 315 | 17 | 0 | 0.08601 | 0.35016 | 40400
7555 | 11 | 315 | 18 | 0 | 0 | 0.37383 | 40400
7556 | 11 | 315 | 19 | 1 | 0 | 0.46712 | 40200
7557 | 11 | 315 | 20 | 1 | 0 | 0.38643 | 40000
7558 | 11 | 315 | 21 | 0 | 0 | 0.41495 | 40000
7559 | 11 | 315 | 22 | 0 | 0 | 0.35981 | 40000
7560 | 11 | 315 | 23 | 0 | 0 | 0.23381 | 40000
7561 | 11 | 316 | 0 | 0 | 0 | 0.21614 | 40000
7562 | 11 | 316 | 1 | 0 | 0 | 0.26414 | 40000
7563 | 11 | 316 | 2 | 0 | 0 | 0.28324 | 40000
7564 | 11 | 316 | 3 | 0 | 0 | 0.36717 | 40000
7565 | 11 | 316 | 4 | 0 | 0 | 0.46831 | 40000
7566 | 11 | 316 | 5 | 0 | 0 | 0.66352 | 40000
7567 | 11 | 316 | 6 | 0 | 0 | 0.65103 | 40000
7568 | 11 | 316 | 7 | 1 | 0.094716 | 0.59644 | 39800
7569 | 11 | 316 | 8 | 1 | 0.44352 | 0.66521 | 39600
7570 | 11 | 316 | 9 | 0 | 0.83569 | 0.77214 | 39600
7571 | 11 | 316 | 10 | 0 | 1 | 0.37568 | 39600
7572 | 11 | 316 | 11 | 0 | 1 | 0.38509 | 39600
7573 | 11 | 316 | 12 | 0 | 1 | 0.42097 | 39600
7574 | 11 | 316 | 13 | 0 | 1 | 0.33034 | 39600
7575 | 11 | 316 | 14 | 0 | 1 | 0.28298 | 39600
7576 | 11 | 316 | 15 | 0 | 0.83569 | 0.37399 | 39600
7577 | 11 | 316 | 16 | 0 | 0.44352 | 0.38583 | 39600
7578 | 11 | 316 | 17 | 0 | 0.094716 | 0.35481 | 39600
7579 | 11 | 316 | 18 | 0 | 0 | 0.532 | 39600
7580 | 11 | 316 | 19 | 1 | 0 | 0.40234 | 39400
7581 | 11 | 316 | 20 | 1 | 0 | 0.39632 | 39200
7582 | 11 | 316 | 21 | 0 | 0 | 0.50999 | 39200
7583 | 11 | 316 | 22 | 0 | 0 | 0.30739 | 39200
7584 | 11 | 316 | 23 | 0 | 0 | 0.22343 | 39200
7585 | 11 | 317 | 0 | 0 | 0 | 0.17802 | 39200
7586 | 11 | 317 | 1 | 0 | 0 | 0.20101 | 39200
7587 | 11 | 317 | 2 | 0 | 0 | 0.20887 | 39200
7588 | 11 | 317 | 3 | 0 | 0 | 0.23043 | 39200
7589 | 11 | 317 | 4 | 0 | 0 | 0.2158 | 39200
7590 | 11 | 317 | 5 | 0 | 0 | 0.11714 | 39200
7591 | 11 | 317 | 6 | 0 | 0 | 0.10197 | 39200
7592 | 11 | 317 | 7 | 1 | 0.092844 | 0.070088 | 39000
7593 | 11 | 317 | 8 | 1 | 0.43475 | 0.086937 | 38800
7594 | 11 | 317 | 9 | 0 | 0.81917 | 0.068761 | 38800
7595 | 11 | 317 | 10 | 0 | 1 | 0.07291 | 38800
7596 | 11 | 317 | 11 | 0 | 1 | 0.098542 | 38800
7597 | 11 | 317 | 12 | 0 | 1 | 0.13446 | 38800
7598 | 11 | 317 | 13 | 0 | 1 | 0.14147 | 38800
7599 | 11 | 317 | 14 | 0 | 1 | 0.2133 | 38800
7600 | 11 | 317 | 15 | 0 | 0.81917 | 0.27987 | 38800
7601 | 11 | 317 | 16 | 0 | 0.43475 | 0.28666 | 38800
7602 | 11 | 317 | 17 | 0 | 0.092844 | 0.46526 | 38800
7603 | 11 | 317 | 18 | 0 | 0 | 0.50128 | 38800
7604 | 11 | 317 | 19 | 1 | 0 | 0.30655 | 38600
7605 | 11 | 317 | 20 | 1 | 0 | 0.40289 | 38400
7606 | 11 | 317 | 21 | 0 | 0 | 0.42079 | 38400
7607 | 11 | 317 | 22 | 0 | 0 | 0.35013 | 38400
7608 | 11 | 317 | 23 | 0 | 0 | 0.42806 | 38400
7609 | 11 | 318 | 0 | 0 | 0 | 0.58714 | 38400
7610 | 11 | 318 | 1 | 0 | 0 | 0.38359 | 38400
7611 | 11 | 318 | 2 | 0 | 0 | 0.32571 | 38400
7612 | 11 | 318 | 3 | 0 | 0 | 0.22956 | 38400
7613 | 11 | 318 | 4 | 0 | 0 | 0.18357 | 38400
7614 | 11 | 318 | 5 | 0 | 0 | 0.24302 | 38400
7615 | 11 | 318 | 6 | 0 | 0 | 0.21038 | 38400
7616 | 11 | 318 | 7 | 1 | 0.082503 | 0.14454 | 38200
7617 | 11 | 318 | 8 | 1 | 0.38633 | 0.14624 | 38000
7618 | 11 | 318 | 9 | 0 | 0.72793 | 0.15446 | 38000
7619 | 11 | 318 | 10 | 0 | 1 | 0.14771 | 38000
7620 | 11 | 318 | 11 | 0 | 1 | 0.15203 | 38000
7621 | 11 | 318 | 12 | 0 | 1 | 0.0946 | 38000
7622 | 11 | 318 | 13 | 0 | 1 | 0.162 | 38000
7623 | 11 | 318 | 14 | 0 | 1 | 0.19239 | 38000
7624 | 11 | 318 | 15 | 0 | 0.72793 | 0.22473 | 38000
7625 | 11 | 318 | 16 | 0 | 0.38633 | 0.1866 | 38000
7626 | 11 | 318 | 17 | 0 | 0.082503 | 0.2327 | 38000
7627 | 11 | 318 | 18 | 0 | 0 | 0.31614 | 38000
7628 | 11 | 318 | 19 | 1 | 0 | 0.24979 | 37800
7629 | 11 | 318 | 20 | 1 | 0 | 0.21594 | 37600
7630 | 11 | 318 | 21 | 0 | 0 | 0.20945 | 37600
7631 | 11 | 318 | 22 | 0 | 0 | 0.25015 | 37600
7632 | 11 | 318 | 23 | 0 | 0 | 0.17986 | 37600
7633 | 11 | 319 | 0 | 0 | 0 | 0.22536 | 37600
7634 | 11 | 319 | 1 | 0 | 0 | 0.14367 | 37600
7635 | 11 | 319 | 2 | 0 | 0 | 0.19039 | 37600
7636 | 11 | 319 | 3 | 0 | 0 | 0.20546 | 37600
7637 | 11 | 319 | 4 | 0 | 0 | 0.17702 | 37600
7638 | 11 | 319 | 5 | 0 | 0 | 0.24929 | 37600
7639 | 11 | 319 | 6 | 0 | 0 | 0.19501 | 37600
7640 | 11 | 319 | 7 | 1 | 0.079686 | 0.21883 | 37400
7641 | 11 | 319 | 8 | 1 | 0.37314 | 0.21803 | 37200
7642 | 11 | 319 | 9 | 0 | 0.70307 | 0.3226 | 37200
7643 | 11 | 319 | 10 | 0 | 0.99363 | 0.28679 | 37200
7644 | 11 | 319 | 11 | 0 | 1 | 0.30169 | 37200
7645 | 11 | 319 | 12 | 0 | 1 | 0.30359 | 37200
7646 | 11 | 319 | 13 | 0 | 1 | 0.30373 | 37200
7647 | 11 | 319 | 14 | 0 | 0.99363 | 0.27879 | 37200
7648 | 11 | 319 | 15 | 0 | 0.70307 | 0.31552 | 37200
7649 | 11 | 319 | 16 | 0 | 0.37314 | 0.26886 | 37200
7650 | 11 | 319 | 17 | 0 | 0.079686 | 0.17811 | 37200
7651 | 11 | 319 | 18 | 0 | 0 | 0.18873 | 37200
7652 | 11 | 319 | 19 | 1 | 0 | 0.27552 | 37000
7653 | 11 | 319 | 20 | 1 | 0 | 0.2678 | 36800
7654 | 11 | 319 | 21 | 0 | 0 | 0.22008 | 36800
7655 | 11 | 319 | 22 | 0 | 0 | 0.1183 | 36800
7656 | 11 | 319 | 23 | 0 | 0 | 0.12462 | 36800
7657 | 11 | 320 | 0 | 0 | 0 | 0.11572 | 36800
7658 | 11 | 320 | 1 | 0 | 0 | 0.116 | 36800
7659 | 11 | 320 | 2 | 0 | 0 | 0.10374 | 36800
7660 | 11 | 320 | 3 | 0 | 0 | 0.11845 | 36800
7661 | 11 | 320 | 4 | 0 | 0 | 0.11018 | 36800
7662 | 11 | 320 | 5 | 0 | 0 | 0.15538 | 36800
7663 | 11 | 320 | 6 | 0 | 0 | 0.11394 | 36800
7664 | 11 | 320 | 7 | 1 | 0.07692 | 0.11462 | 36600
7665 | 11 | 320 | 8 | 1 | 0.36019 | 0.081798 | 36400
7666 | 11 | 320 | 9 | 0 | 0.67867 | 0.09338 | 36400
7667 | 11 | 320 | 10 | 0 | 0.95915 | 0.055987 | 36400
7668 | 11 | 320 | 11 | 0 | 1 | 0.071744 | 36400
7669 | 11 | 320 | 12 | 0 | 1 | 0.082538 | 36400
7670 | 11 | 320 | 13 | 0 | 1 | 0.11026 | 36400
7671 | 11 | 320 | 14 | 0 | 0.95915 | 0.11971 | 36400
7672 | 11 | 320 | 15 | 0 | 0.67867 | 0.11259 | 36400
7673 | 11 | 320 | 16 | 0 | 0.36019 | 0.10533 | 36400
7674 | 11 | 320 | 17 | 0 | 0.07692 | 0.078135 | 36400
7675 | 11 | 320 | 18 | 0 | 0 | 0.070785 | 36400
7676 | 11 | 320 | 19 | 1 | 0 | 0.084012 | 36200
7677 | 11 | 320 | 20 | 1 | 0 | 0.10388 | 36000
7678 | 11 | 320 | 21 | 0 | 0 | 0.12608 | 36000
7679 | 11 | 320 | 22 | 0 | 0 | 0.12846 | 36000
7680 | 11 | 320 | 23 | 0 | 0 | 0.14583 | 36000
7681 | 11 | 321 | 0 | 0 | 0 | 0.16123 | 36000
7682 | 11 | 321 | 1 | 0 | 0 | 0.22917 | 36000
7683 | 11 | 321 | 2 | 0 | 0 | 0.13899 | 36000
7684 | 11 | 321 | 3 | 0 | 0 | 0.15146 | 36000
7685 | 11 | 321 | 4 | 0 | 0 | 0.12377 | 36000
7686 | 11 | 321 | 5 | 0 | 0 | 0.108 | 36000
7687 | 11 | 321 | 6 | 0 | 0 | 0.081818 | 36000
7688 | 11 | 321 | 7 | 1 | 0.079729 | 0.065359 | 35800
7689 | 11 | 321 | 8 | 1 | 0.37334 | 0.057156 | 35600
7690 | 11 | 321 | 9 | 0 | 0.70346 | 0.07158 | 35600
7691 | 11 | 321 | 10 | 0 | 0.99418 | 0.11869 | 35600
7692 | 11 | 321 | 11 | 0 | 1 | 0.094961 | 35600
7693 | 11 | 321 | 12 | 0 | 1 | 0.11217 | 35600
7694 | 11 | 321 | 13 | 0 | 1 | 0.12974 | 35600
7695 | 11 | 321 | 14 | 0 | 0.99418 | 0.14223 | 35600
7696 | 11 | 321 | 15 | 0 | 0.70346 | 0.13659 | 35600
7697 | 11 | 321 | 16 | 0 | 0.37334 | 0.1123 | 35600
7698 | 11 | 321 | 17 | 0 | 0.079729 | 0.16536 | 35600
7699 | 11 | 321 | 18 | 0 | 0 | 0.14965 | 35600
7700 | 11 | 321 | 19 | 1 | 0 | 0.15629 | 35400
7701 | 11 | 321 | 20 | 1 | 0 | 0.11371 | 35200
7702 | 11 | 321 | 21 | 0 | 0 | 0.1106 | 35200
7703 | 11 | 321 | 22 | 0 | 0 | 0.068325 | 35200
7704 | 11 | 321 | 23 | 0 | 0 | 0.07811 | 35200
7705 | 11 | 322 | 0 | 0 | 0 | 0.060519 | 35200
7706 | 11 | 322 | 1 | 0 | 0 | 0.064877 | 35200
7707 | 11 | 322 | 2 | 0 | 0 | 0.052849 | 35200
7708 | 11 | 322 | 3 | 0 | 0 | 0.081366 | 35200
7709 | 11 | 322 | 4 | 0 | 0 | 0.119 | 35200
7710 | 11 | 322 | 5 | 0 | 0 | 0.11221 | 35200
7711 | 11 | 322 | 6 | 0 | 0 | 0.11906 | 35200
7712 | 11 | 322 | 7 | 1 | 0.084538 | 0.12765 | 35000
7713 | 11 | 322 | 8 | 1 | 0.39586 | 0.15882 | 34800
7714 | 11 | 322 | 9 | 0 | 0.74589 | 0.15588 | 34800
7715 | 11 | 322 | 10 | 0 | 1 | 0.12659 | 34800
7716 | 11 | 322 | 11 | 0 | 1 | 0.10096 | 34800
7717 | 11 | 322 | 12 | 0 | 1 | 0.051866 | 34800
7718 | 11 | 322 | 13 | 0 | 1 | 0.059767 | 34800
7719 | 11 | 322 | 14 | 0 | 1 | 0.057217 | 34800
7720 | 11 | 322 | 15 | 0 | 0.74589 | 0.045423 | 34800
7721 | 11 | 322 | 16 | 0 | 0.39586 | 0.03764 | 34800
7722 | 11 | 322 | 17 | 0 | 0.084538 | 0.063351 | 34800
7723 | 11 | 322 | 18 | 0 | 0 | 0.081004 | 34800
7724 | 11 | 322 | 19 | 1 | 0 | 0.078749 | 34600
7725 | 11 | 322 | 20 | 1 | 0 | 0.073647 | 34400
7726 | 11 | 322 | 21 | 0 | 0 | 0.076106 | 34400
7727 | 11 | 322 | 22 | 0 | 0 | 0.1188 | 34400
7728 | 11 | 322 | 23 | 0 | 0 | 0.11701 | 34400
7729 | 11 | 323 | 0 | 0 | 0 | 0.12167 | 34400
7730 | 11 | 323 | 1 | 0 | 0 | 0.16322 | 34400
7731 | 11 | 323 | 2 | 0 | 0 | 0.1777 | 34400
7732 | 11 | 323 | 3 | 0 | 0 | 0.23484 | 34400
7733 | 11 | 323 | 4 | 0 | 0 | 0.20287 | 34400
7734 | 11 | 323 | 5 | 0 | 0 | 0.1748 | 34400
7735 | 11 | 323 | 6 | 0 | 0 | 0.14096 | 34400
7736 | 11 | 323 | 7 | 1 | 0.074626 | 0.14987 | 34200
7737 | 11 | 323 | 8 | 1 | 0.34944 | 0.18359 | 34000
7738 | 11 | 323 | 9 | 0 | 0.65843 | 0.15026 | 34000
7739 | 11 | 323 | 10 | 0 | 0.93054 | 0.18676 | 34000
7740 | 11 | 323 | 11 | 0 | 1 | 0.22932 | 34000
7741 | 11 | 323 | 12 | 0 | 1 | 0.14452 | 34000
7742 | 11 | 323 | 13 | 0 | 1 | 0.14377 | 34000
7743 | 11 | 323 | 14 | 0 | 0.93054 | 0.10797 | 34000
7744 | 11 | 323 | 15 | 0 | 0.65843 | 0.078839 | 34000
7745 | 11 | 323 | 16 | 0 | 0.34944 | 0.083676 | 34000
7746 | 11 | 323 | 17 | 0 | 0.074626 | 0.077916 | 34000
7747 | 11 | 323 | 18 | 0 | 0 | 0.06936 | 34000
7748 | 11 | 323 | 19 | 1 | 0 | 0.084293 | 33800
7749 | 11 | 323 | 20 | 1 | 0 | 0.10152 | 33600
7750 | 11 | 323 | 21 | 0 | 0 | 0.10973 | 33600
7751 | 11 | 323 | 22 | 0 | 0 | 0.12587 | 33600
7752 | 11 | 323 | 23 | 0 | 0 | 0.21626 | 33600
7753 | 11 | 324 | 0 | 0 | 0 | 0.27181 | 33600
7754 | 11 | 324 | 1 | 0 | 0 | 0.29927 | 33600
7755 | 11 | 324 | 2 | 0 | 0 | 0.25682 | 33600
7756 | 11 | 324 | 3 | 0 | 0 | 0.22804 | 33600
7757 | 11 | 324 | 4 | 0 | 0 | 0.28909 | 33600
7758 | 11 | 324 | 5 | 0 | 0 | 0.2758 | 33600
7759 | 11 | 324 | 6 | 0 | 0 | 0.39446 | 33600
7760 | 11 | 324 | 7 | 1 | 0.088967 | 0.37222 | 33400
7761 | 11 | 324 | 8 | 1 | 0.4166 | 0.36249 | 33200
7762 | 11 | 324 | 9 | 0 | 0.78497 | 0.31209 | 33200
7763 | 11 | 324 | 10 | 0 | 1 | 0.25101 | 33200
7764 | 11 | 324 | 11 | 0 | 1 | 0.28213 | 33200
7765 | 11 | 324 | 12 | 0 | 1 | 0.22699 | 33200
7766 | 11 | 324 | 13 | 0 | 1 | 0.20599 | 33200
7767 | 11 | 324 | 14 | 0 | 1 | 0.19542 | 33200
7768 | 11 | 324 | 15 | 0 | 0.78497 | 0.15083 | 33200
7769 | 11 | 324 | 16 | 0 | 0.4166 | 0.15337 | 33200
7770 | 11 | 324 | 17 | 0 | 0.088967 | 0.15311 | 33200
7771 | 11 | 324 | 18 | 0 | 0 | 0.18105 | 33200
7772 | 11 | 324 | 19 | 1 | 0 | 0.13675 | 33000
7773 | 11 | 324 | 20 | 1 | 0 | 0.23513 | 32800
7774 | 11 | 324 | 21 | 0 | 0 | 0.3037 | 32800
7775 | 11 | 324 | 22 | 0 | 0 | 0.36123 | 32800
7776 | 11 | 324 | 23 | 0 | 0 | 0.36354 | 32800
7777 | 11 | 325 | 0 | 0 | 0 | 0.44316 | 32800
7778 | 11 | 325 | 1 | 0 | 0 | 0.32803 | 32800
7779 | 11 | 325 | 2 | 0 | 0 | 0.3219 | 32800
7780 | 11 | 325 | 3 | 0 | 0 | 0.38079 | 32800
7781 | 11 | 325 | 4 | 0 | 0 | 0.56699 | 32800
7782 | 11 | 325 | 5 | 0 | 0 | 0.51404 | 32800
7783 | 11 | 325 | 6 | 0 | 0 | 0.59437 | 32800
7784 | 11 | 325 | 7 | 1 | 0.09047 | 0.39636 | 32600
7785 | 11 | 325 | 8 | 1 | 0.42363 | 0.40714 | 32400
7786 | 11 | 325 | 9 | 0 | 0.79823 | 0.39794 | 32400
7787 | 11 | 325 | 10 | 0 | 1 | 0.30191 | 32400
7788 | 11 | 325 | 11 | 0 | 1 | 0.30238 | 32400
7789 | 11 | 325 | 12 | 0 | 1 | 0.35509 | 32400
7790 | 11 | 325 | 13 | 0 | 1 | 0.25771 | 32400
7791 | 11 | 325 | 14 | 0 | 1 | 0.2604 | 32400
7792 | 11 | 325 | 15 | 0 | 0.79823 | 0.379 | 32400
7793 | 11 | 325 | 16 | 0 | 0.42363 | 0.44437 | 32400
7794 | 11 | 325 | 17 | 0 | 0.09047 | 0.34953 | 32400
7795 | 11 | 325 | 18 | 0 | 0 | 0.37745 | 32400
7796 | 11 | 325 | 19 | 1 | 0 | 0.35125 | 32200
7797 | 11 | 325 | 20 | 1 | 0 | 0.30595 | 32000
7798 | 11 | 325 | 21 | 0 | 0 | 0.20952 | 32000
7799 | 11 | 325 | 22 | 0 | 0 | 0.24905 | 32000
7800 | 11 | 325 | 23 | 0 | 0 | 0.22883 | 32000
7801 | 11 | 326 | 0 | 0 | 0 | 0.18418 | 32000
7802 | 11 | 326 | 1 | 0 | 0 | 0.14905 | 32000
7803 | 11 | 326 | 2 | 0 | 0 | 0.11094 | 32000
7804 | 11 | 326 | 3 | 0 | 0 | 0.11535 | 32000
7805 | 11 | 326 | 4 | 0 | 0 | 0.13503 | 32000
7806 | 11 | 326 | 5 | 0 | 0 | 0.13139 | 32000
7807 | 11 | 326 | 6 | 0 | 0 | 0.13291 | 32000
7808 | 11 | 326 | 7 | 1 | 0.078023 | 0.098993 | 31800
7809 | 11 | 326 | 8 | 1 | 0.36535 | 0.074882 | 31600
7810 | 11 | 326 | 9 | 0 | 0.6884 | 0.10224 | 31600
7811 | 11 | 326 | 10 | 0 | 0.9729 | 0.10227 | 31600
7812 | 11 | 326 | 11 | 0 | 1 | 0.12008 | 31600
7813 | 11 | 326 | 12 | 0 | 1 | 0.13173 | 31600
7814 | 11 | 326 | 13 | 0 | 1 | 0.12467 | 31600
7815 | 11 | 326 | 14 | 0 | 0.9729 | 0.11212 | 31600
7816 | 11 | 326 | 15 | 0 | 0.6884 | 0.14009 | 31600
7817 | 11 | 326 | 16 | 0 | 0.36535 | 0.18175 | 31600
7818 | 11 | 326 | 17 | 0 | 0.078023 | 0.17366 | 31600
7819 | 11 | 326 | 18 | 0 | 0 | 0.1615 | 31600
7820 | 11 | 326 | 19 | 1 | 0 | 0.14739 | 31400
7821 | 11 | 326 | 20 | 1 | 0 | 0.13168 | 31200
7822 | 11 | 326 | 21 | 0 | 0 | 0.17505 | 31200
7823 | 11 | 326 | 22 | 0 | 0 | 0.16454 | 31200
7824 | 11 | 326 | 23 | 0 | 0 | 0.17742 | 31200
7825 | 11 | 327 | 0 | 0 | 0 | 0.15149 | 31200
7826 | 11 | 327 | 1 | 0 | 0 | 0.25133 | 31200
7827 | 11 | 327 | 2 | 0 | 0 | 0.23845 | 31200
7828 | 11 | 327 | 3 | 0 | 0 | 0.19284 | 31200
7829 | 11 | 327 | 4 | 0 | 0 | 0.1785 | 31200
7830 | 11 | 327 | 5 | 0 | 0 | 0.18835 | 31200
7831 | 11 | 327 | 6 | 0 | 0 | 0.14006 | 31200
7832 | 11 | 327 | 7 | 1 | 0.08939 | 0.11192 | 31000
7833 | 11 | 327 | 8 | 1 | 0.41858 | 0.16655 | 30800
7834 | 11 | 327 | 9 | 0 | 0.7887 | 0.17493 | 30800
7835 | 11 | 327 | 10 | 0 | 1 | 0.31505 | 30800
7836 | 11 | 327 | 11 | 0 | 1 | 0.29203 | 30800
7837 | 11 | 327 | 12 | 0 | 1 | 0.23746 | 30800
7838 | 11 | 327 | 13 | 0 | 1 | 0.39697 | 30800
7839 | 11 | 327 | 14 | 0 | 1 | 0.19219 | 30800
7840 | 11 | 327 | 15 | 0 | 0.7887 | 0.1895 | 30800
7841 | 11 | 327 | 16 | 0 | 0.41858 | 0.12737 | 30800
7842 | 11 | 327 | 17 | 0 | 0.08939 | 0.083235 | 30800
7843 | 11 | 327 | 18 | 0 | 0 | 0.14922 | 30800
7844 | 11 | 327 | 19 | 1 | 0 | 0.16301 | 30600
7845 | 11 | 327 | 20 | 1 | 0 | 0.21517 | 30400
7846 | 11 | 327 | 21 | 0 | 0 | 0.29576 | 30400
7847 | 11 | 327 | 22 | 0 | 0 | 0.25492 | 30400
7848 | 11 | 327 | 23 | 0 | 0 | 0.28724 | 30400
7849 | 11 | 328 | 0 | 0 | 0 | 0.21699 | 30400
7850 | 11 | 328 | 1 | 0 | 0 | 0.17023 | 30400
7851 | 11 | 328 | 2 | 0 | 0 | 0.20445 | 30400
7852 | 11 | 328 | 3 | 0 | 0 | 0.21505 | 30400
7853 | 11 | 328 | 4 | 0 | 0 | 0.20909 | 30400
7854 | 11 | 328 | 5 | 0 | 0 | 0.22364 | 30400
7855 | 11 | 328 | 6 | 0 | 0 | 0.25392 | 30400
7856 | 11 | 328 | 7 | 1 | 0.080669 | 0.2226 | 30200
7857 | 11 | 328 | 8 | 1 | 0.37774 | 0.22589 | 30000
7858 | 11 | 328 | 9 | 0 | 0.71175 | 0.23365 | 30000
7859 | 11 | 328 | 10 | 0 | 1 | 0.19281 | 30000
7860 | 11 | 328 | 11 | 0 | 1 | 0.13826 | 30000
7861 | 11 | 328 | 12 | 0 | 1 | 0.11726 | 30000
7862 | 11 | 328 | 13 | 0 | 1 | 0.12686 | 30000
7863 | 11 | 328 | 14 | 0 | 1 | 0.11796 | 30000
7864 | 11 | 328 | 15 | 0 | 0.71175 | 0.1229 | 30000
7865 | 11 | 328 | 16 | 0 | 0.37774 | 0.086512 | 30000
7866 | 11 | 328 | 17 | 0 | 0.080669 | 0.081773 | 30000
7867 | 11 | 328 | 18 | 0 | 0 | 0.11924 | 30000
7868 | 11 | 328 | 19 | 1 | 0 | 0.11383 | 29800
7869 | 11 | 328 | 20 | 1 | 0 | 0.13834 | 29600
7870 | 11 | 328 | 21 | 0 | 0 | 0.17046 | 29600
7871 | 11 | 328 | 22 | 0 | 0 | 0.19869 | 29600
7872 | 11 | 328 | 23 | 0 | 0 | 0.13842 | 29600
7873 | 11 | 329 | 0 | 0 | 0 | 0.21205 | 29600
7874 | 11 | 329 | 1 | 0 | 0 | 0.25586 | 29600
7875 | 11 | 329 | 2 | 0 | 0 | 0.28112 | 29600
7876 | 11 | 329 | 3 | 0 | 0 | 0.3829 | 29600
7877 | 11 | 329 | 4 | 0 | 0 | 0.3296 | 29600
7878 | 11 | 329 | 5 | 0 | 0 | 0.27468 | 29600
7879 | 11 | 329 | 6 | 0 | 0 | 0.28227 | 29600
7880 | 11 | 329 | 7 | 1 | 0.084543 | 0.27848 | 29400
7881 | 11 | 329 | 8 | 1 | 0.39588 | 0.38659 | 29200
7882 | 11 | 329 | 9 | 0 | 0.74593 | 0.39913 | 29200
7883 | 11 | 329 | 10 | 0 | 1 | 0.51731 | 29200
7884 | 11 | 329 | 11 | 0 | 1 | 0.55711 | 29200
7885 | 11 | 329 | 12 | 0 | 1 | 0.4227 | 29200
7886 | 11 | 329 | 13 | 0 | 1 | 0.43794 | 29200
7887 | 11 | 329 | 14 | 0 | 1 | 0.49119 | 29200
7888 | 11 | 329 | 15 | 0 | 0.74593 | 0.83415 | 29200
7889 | 11 | 329 | 16 | 0 | 0.39588 | 0.73927 | 29200
7890 | 11 | 329 | 17 | 0 | 0.084543 | 0.57343 | 29200
7891 | 11 | 329 | 18 | 0 | 0 | 0.41433 | 29200
7892 | 11 | 329 | 19 | 1 | 0 | 0.61709 | 29000
7893 | 11 | 329 | 20 | 1 | 0 | 0.69836 | 28800
7894 | 11 | 329 | 21 | 0 | 0 | 0.81792 | 28800
7895 | 11 | 329 | 22 | 0 | 0 | 0.75282 | 28800
7896 | 11 | 329 | 23 | 0 | 0 | 0.57032 | 28800
7897 | 11 | 330 | 0 | 0 | 0 | 0.3921 | 28800
7898 | 11 | 330 | 1 | 0 | 0 | 0.33183 | 28800
7899 | 11 | 330 | 2 | 0 | 0 | 0.42467 | 28800
7900 | 11 | 330 | 3 | 0 | 0 | 0.40496 | 28800
7901 | 11 | 330 | 4 | 0 | 0 | 0.39743 | 28800
7902 | 11 | 330 | 5 | 0 | 0 | 0.60391 | 28800
7903 | 11 | 330 | 6 | 0 | 0 | 0.399 | 28800
7904 | 11 | 330 | 7 | 1 | 0.081403 | 0.39279 | 28600
7905 | 11 | 330 | 8 | 1 | 0.38118 | 0.72544 | 28400
7906 | 11 | 330 | 9 | 0 | 0.71822 | 0.89341 | 28400
7907 | 11 | 330 | 10 | 0 | 1 | 1 | 28400
7908 | 11 | 330 | 11 | 0 | 1 | 1 | 28400
7909 | 11 | 330 | 12 | 0 | 1 | 0.92481 | 28400
7910 | 11 | 330 | 13 | 0 | 1 | 1 | 28400
7911 | 11 | 330 | 14 | 0 | 1 | 0.92998 | 28400
7912 | 11 | 330 | 15 | 0 | 0.71822 | 0.75656 | 28400
7913 | 11 | 330 | 16 | 0 | 0.38118 | 0.95104 | 28400
7914 | 11 | 330 | 17 | 0 | 0.081403 | 0.8346 | 28400
7915 | 11 | 330 | 18 | 0 | 0 | 1 | 28400
7916 | 11 | 330 | 19 | 1 | 0 | 0.82764 | 28200
7917 | 11 | 330 | 20 | 1 | 0 | 0.71353 | 28000
7918 | 11 | 330 | 21 | 0 | 0 | 0.73903 | 28000
7919 | 11 | 330 | 22 | 0 | 0 | 0.88116 | 28000
7920 | 11 | 330 | 23 | 0 | 0 | 0.77252 | 28000
7921 | 11 | 331 | 0 | 0 | 0 | 0.6146 | 28000
7922 | 11 | 331 | 1 | 0 | 0 | 0.33731 | 28000
7923 | 11 | 331 | 2 | 0 | 0 | 0.34222 | 28000
7924 | 11 | 331 | 3 | 0 | 0 | 0.25976 | 28000
7925 | 11 | 331 | 4 | 0 | 0 | 0.21133 | 28000
7926 | 11 | 331 | 5 | 0 | 0 | 0.19658 | 28000
7927 | 11 | 331 | 6 | 0 | 0 | 0.17646 | 28000
7928 | 11 | 331 | 7 | 1 | 0.075315 | 0.22324 | 27800
7929 | 11 | 331 | 8 | 1 | 0.35267 | 0.30252 | 27600
7930 | 11 | 331 | 9 | 0 | 0.66451 | 0.27127 | 27600
7931 | 11 | 331 | 10 | 0 | 0.93914 | 0.3403 | 27600
7932 | 11 | 331 | 11 | 0 | 1 | 0.34029 | 27600
7933 | 11 | 331 | 12 | 0 | 1 | 0.38181 | 27600
7934 | 11 | 331 | 13 | 0 | 1 | 0.31687 | 27600
7935 | 11 | 331 | 14 | 0 | 0.93914 | 0.38035 | 27600
7936 | 11 | 331 | 15 | 0 | 0.66451 | 0.52644 | 27600
7937 | 11 | 331 | 16 | 0 | 0.35267 | 0.95042 | 27600
7938 | 11 | 331 | 17 | 0 | 0.075315 | 0.72228 | 27600
7939 | 11 | 331 | 18 | 0 | 0 | 0.68369 | 27600
7940 | 11 | 331 | 19 | 1 | 0 | 0.79851 | 27400
7941 | 11 | 331 | 20 | 1 | 0 | 1 | 27200
7942 | 11 | 331 | 21 | 0 | 0 | 0.93685 | 27200
7943 | 11 | 331 | 22 | 0 | 0 | 0.61064 | 27200
7944 | 11 | 331 | 23 | 0 | 0 | 0.53733 | 27200
7945 | 11 | 332 | 0 | 0 | 0 | 0.51417 | 27200
7946 | 11 | 332 | 1 | 0 | 0 | 0.44608 | 27200
7947 | 11 | 332 | 2 | 0 | 0 | 0.53127 | 27200
7948 | 11 | 332 | 3 | 0 | 0 | 0.47438 | 27200
7949 | 11 | 332 | 4 | 0 | 0 | 0.52803 | 27200
7950 | 11 | 332 | 5 | 0 | 0 | 0.31246 | 27200
7951 | 11 | 332 | 6 | 0 | 0 | 0.30428 | 27200
7952 | 11 | 332 | 7 | 1 | 0.085646 | 0.39074 | 27000
7953 | 11 | 332 | 8 | 1 | 0.40104 | 0.44018 | 26800
7954 | 11 | 332 | 9 | 0 | 0.75566 | 0.50714 | 26800
7955 | 11 | 332 | 10 | 0 | 1 | 0.42575 | 26800
7956 | 11 | 332 | 11 | 0 | 1 | 0.52484 | 26800
7957 | 11 | 332 | 12 | 0 | 1 | 0.62481 | 26800
7958 | 11 | 332 | 13 | 0 | 1 | 0.48191 | 26800
7959 | 11 | 332 | 14 | 0 | 1 | 0.44788 | 26800
7960 | 11 | 332 | 15 | 0 | 0.75566 | 0.45609 | 26800
7961 | 11 | 332 | 16 | 0 | 0.40104 | 0.60528 | 26800
7962 | 11 | 332 | 17 | 0 | 0.085646 | 0.58173 | 26800
7963 | 11 | 332 | 18 | 0 | 0 | 0.40565 | 26800
7964 | 11 | 332 | 19 | 1 | 0 | 0.36387 | 26600
7965 | 11 | 332 | 20 | 1 | 0 | 0.38257 | 26400
7966 | 11 | 332 | 21 | 0 | 0 | 0.38117 | 26400
7967 | 11 | 332 | 22 | 0 | 0 | 0.28838 | 26400
7968 | 11 | 332 | 23 | 0 | 0 | 0.29692 | 26400
7969 | 11 | 333 | 0 | 0 | 0 | 0.26038 | 26400
7970 | 11 | 333 | 1 | 0 | 0 | 0.29128 | 26400
7971 | 11 | 333 | 2 | 0 | 0 | 0.32849 | 26400
7972 | 11 | 333 | 3 | 0 | 0 | 0.3737 | 26400
7973 | 11 | 333 | 4 | 0 | 0 | 0.35872 | 26400
7974 | 11 | 333 | 5 | 0 | 0 | 0.38693 | 26400
7975 | 11 | 333 | 6 | 0 | 0 | 0.42045 | 26400
7976 | 11 | 333 | 7 | 1 | 0.079438 | 0.27552 | 26200
7977 | 11 | 333 | 8 | 1 | 0.37198 | 0.24418 | 26000
7978 | 11 | 333 | 9 | 0 | 0.70089 | 0.39796 | 26000
7979 | 11 | 333 | 10 | 0 | 0.99055 | 0.44786 | 26000
7980 | 11 | 333 | 11 | 0 | 1 | 0.34321 | 26000
7981 | 11 | 333 | 12 | 0 | 1 | 0.32747 | 26000
7982 | 11 | 333 | 13 | 0 | 1 | 0.40009 | 26000
7983 | 11 | 333 | 14 | 0 | 0.99055 | 0.43609 | 26000
7984 | 11 | 333 | 15 | 0 | 0.70089 | 0.52532 | 26000
7985 | 11 | 333 | 16 | 0 | 0.37198 | 0.64825 | 26000
7986 | 11 | 333 | 17 | 0 | 0.079438 | 0.69368 | 26000
7987 | 11 | 333 | 18 | 0 | 0 | 0.72346 | 26000
7988 | 11 | 333 | 19 | 1 | 0 | 0.94767 | 25800
7989 | 11 | 333 | 20 | 1 | 0 | 0.91091 | 25600
7990 | 11 | 333 | 21 | 0 | 0 | 0.71098 | 25600
7991 | 11 | 333 | 22 | 0 | 0 | 0.47498 | 25600
7992 | 11 | 333 | 23 | 0 | 0 | 0.41691 | 25600
7993 | 11 | 334 | 0 | 0 | 0 | 0.27419 | 25600
7994 | 11 | 334 | 1 | 0 | 0 | 0.24978 | 25600
7995 | 11 | 334 | 2 | 0 | 0 | 0.2071 | 25600
7996 | 11 | 334 | 3 | 0 | 0 | 0.17124 | 25600
7997 | 11 | 334 | 4 | 0 | 0 | 0.21799 | 25600
7998 | 11 | 334 | 5 | 0 | 0 | 0.19793 | 25600
7999 | 11 | 334 | 6 | 0 | 0 | 0.28499 | 25600
8000 | 11 | 334 | 7 | 1 | 0.080415 | 0.29842 | 25400
8001 | 11 | 334 | 8 | 1 | 0.37655 | 0.3781 | 25200
8002 | 11 | 334 | 9 | 0 | 0.70951 | 0.53673 | 25200
8003 | 11 | 334 | 10 | 0 | 1 | 0.40714 | 25200
8004 | 11 | 334 | 11 | 0 | 1 | 0.30179 | 25200
8005 | 11 | 334 | 12 | 0 | 1 | 0.26949 | 25200
8006 | 11 | 334 | 13 | 0 | 1 | 0.20914 | 25200
8007 | 11 | 334 | 14 | 0 | 1 | 0.17266 | 25200
8008 | 11 | 334 | 15 | 0 | 0.70951 | 0.17935 | 25200
8009 | 11 | 334 | 16 | 0 | 0.37655 | 0.093434 | 25200
8010 | 11 | 334 | 17 | 0 | 0.080415 | 0.12114 | 25200
8011 | 11 | 334 | 18 | 0 | 0 | 0.13118 | 25200
8012 | 11 | 334 | 19 | 1 | 0 | 0.10447 | 25000
8013 | 11 | 334 | 20 | 1 | 0 | 0.09855 | 24800
8014 | 11 | 334 | 21 | 0 | 0 | 0.092543 | 24800
8015 | 11 | 334 | 22 | 0 | 0 | 0.10212 | 24800
8016 | 11 | 334 | 23 | 0 | 0 | 0.10452 | 24800
8017 | 12 | 335 | 0 | 0 | 0 | 0.10812 | 24800
8018 | 12 | 335 | 1 | 0 | 0 | 0.17362 | 24800
8019 | 12 | 335 | 2 | 0 | 0 | 0.27554 | 24800
8020 | 12 | 335 | 3 | 0 | 0 | 0.36761 | 24800
8021 | 12 | 335 | 4 | 0 | 0 | 0.36156 | 24800
8022 | 12 | 335 | 5 | 0 | 0 | 0.27886 | 24800
8023 | 12 | 335 | 6 | 0 | 0 | 0.26223 | 24800
8024 | 12 | 335 | 7 | 1 | 0.046221 | 0.20281 | 24600
8025 | 12 | 335 | 8 | 1 | 0.32415 | 0.30634 | 24400
8026 | 12 | 335 | 9 | 0 | 0.65118 | 0.40914 | 24400
8027 | 12 | 335 | 10 | 0 | 0.94373 | 0.49508 | 24400
8028 | 12 | 335 | 11 | 0 | 1 | 0.42732 | 24400
8029 | 12 | 335 | 12 | 0 | 1 | 0.39658 | 24400
8030 | 12 | 335 | 13 | 0 | 1 | 0.80742 | 24400
8031 | 12 | 335 | 14 | 0 | 0.94373 | 0.66383 | 24400
8032 | 12 | 335 | 15 | 0 | 0.65118 | 0.55327 | 24400
8033 | 12 | 335 | 16 | 0 | 0.32415 | 0.36196 | 24400
8034 | 12 | 335 | 17 | 0 | 0.046221 | 0.53119 | 24400
8035 | 12 | 335 | 18 | 0 | 0 | 0.6255 | 24400
8036 | 12 | 335 | 19 | 1 | 0 | 0.47489 | 24200
8037 | 12 | 335 | 20 | 1 | 0 | 0.44359 | 24000
8038 | 12 | 335 | 21 | 0 | 0 | 0.3339 | 24000
8039 | 12 | 335 | 22 | 0 | 0 | 0.30335 | 24000
8040 | 12 | 335 | 23 | 0 | 0 | 0.36627 | 24000
8041 | 12 | 336 | 0 | 0 | 0 | 0.33234 | 24000
8042 | 12 | 336 | 1 | 0 | 0 | 0.35507 | 24000
8043 | 12 | 336 | 2 | 0 | 0 | 0.62008 | 24000
8044 | 12 | 336 | 3 | 0 | 0 | 0.55381 | 24000
8045 | 12 | 336 | 4 | 0 | 0 | 0.62796 | 24000
8046 | 12 | 336 | 5 | 0 | 0 | 0.55566 | 24000
8047 | 12 | 336 | 6 | 0 | 0 | 0.49215 | 24000
8048 | 12 | 336 | 7 | 1 | 0.04587 | 0.45681 | 23800
8049 | 12 | 336 | 8 | 1 | 0.32168 | 0.37415 | 23600
8050 | 12 | 336 | 9 | 0 | 0.64623 | 0.28614 | 23600
8051 | 12 | 336 | 10 | 0 | 0.93655 | 0.23887 | 23600
8052 | 12 | 336 | 11 | 0 | 1 | 0.17024 | 23600
8053 | 12 | 336 | 12 | 0 | 1 | 0.14102 | 23600
8054 | 12 | 336 | 13 | 0 | 1 | 0.20226 | 23600
8055 | 12 | 336 | 14 | 0 | 0.93655 | 0.24173 | 23600
8056 | 12 | 336 | 15 | 0 | 0.64623 | 0.26649 | 23600
8057 | 12 | 336 | 16 | 0 | 0.32168 | 0.20672 | 23600
8058 | 12 | 336 | 17 | 0 | 0.04587 | 0.23452 | 23600
8059 | 12 | 336 | 18 | 0 | 0 | 0.19852 | 23600
8060 | 12 | 336 | 19 | 1 | 0 | 0.17336 | 23400
8061 | 12 | 336 | 20 | 1 | 0 | 0.15531 | 23200
8062 | 12 | 336 | 21 | 0 | 0 | 0.19073 | 23200
8063 | 12 | 336 | 22 | 0 | 0 | 0.23094 | 23200
8064 | 12 | 336 | 23 | 0 | 0 | 0.24037 | 23200
8065 | 12 | 337 | 0 | 0 | 0 | 0.32022 | 23200
8066 | 12 | 337 | 1 | 0 | 0 | 0.25904 | 23200
8067 | 12 | 337 | 2 | 0 | 0 | 0.2197 | 23200
8068 | 12 | 337 | 3 | 0 | 0 | 0.21638 | 23200
8069 | 12 | 337 | 4 | 0 | 0 | 0.34862 | 23200
8070 | 12 | 337 | 5 | 0 | 0 | 0.26349 | 23200
8071 | 12 | 337 | 6 | 0 | 0 | 0.28576 | 23200
8072 | 12 | 337 | 7 | 1 | 0.052687 | 0.22095 | 23000
8073 | 12 | 337 | 8 | 1 | 0.3695 | 0.21518 | 22800
8074 | 12 | 337 | 9 | 0 | 0.74228 | 0.18388 | 22800
8075 | 12 | 337 | 10 | 0 | 1 | 0.12089 | 22800
8076 | 12 | 337 | 11 | 0 | 1 | 0.11865 | 22800
8077 | 12 | 337 | 12 | 0 | 1 | 0.088932 | 22800
8078 | 12 | 337 | 13 | 0 | 1 | 0.060189 | 22800
8079 | 12 | 337 | 14 | 0 | 1 | 0.037121 | 22800
8080 | 12 | 337 | 15 | 0 | 0.74228 | 0.051778 | 22800
8081 | 12 | 337 | 16 | 0 | 0.3695 | 0.058187 | 22800
8082 | 12 | 337 | 17 | 0 | 0.052687 | 0.042494 | 22800
8083 | 12 | 337 | 18 | 0 | 0 | 0.041382 | 22800
8084 | 12 | 337 | 19 | 1 | 0 | 0.039579 | 22600
8085 | 12 | 337 | 20 | 1 | 0 | 0.040427 | 22400
8086 | 12 | 337 | 21 | 0 | 0 | 0.077214 | 22400
8087 | 12 | 337 | 22 | 0 | 0 | 0.079211 | 22400
8088 | 12 | 337 | 23 | 0 | 0 | 0.079011 | 22400
8089 | 12 | 338 | 0 | 0 | 0 | 0.055462 | 22400
8090 | 12 | 338 | 1 | 0 | 0 | 0.056795 | 22400
8091 | 12 | 338 | 2 | 0 | 0 | 0.13936 | 22400
8092 | 12 | 338 | 3 | 0 | 0 | 0.17901 | 22400
8093 | 12 | 338 | 4 | 0 | 0 | 0.22101 | 22400
8094 | 12 | 338 | 5 | 0 | 0 | 0.19087 | 22400
8095 | 12 | 338 | 6 | 0 | 0 | 0.19895 | 22400
8096 | 12 | 338 | 7 | 1 | 0.043916 | 0.14721 | 22200
8097 | 12 | 338 | 8 | 1 | 0.30798 | 0.097999 | 22000
8098 | 12 | 338 | 9 | 0 | 0.6187 | 0.14236 | 22000
8099 | 12 | 338 | 10 | 0 | 0.89666 | 0.159 | 22000
8100 | 12 | 338 | 11 | 0 | 1 | 0.18891 | 22000
8101 | 12 | 338 | 12 | 0 | 1 | 0.40046 | 22000
8102 | 12 | 338 | 13 | 0 | 1 | 0.56664 | 22000
8103 | 12 | 338 | 14 | 0 | 0.89666 | 0.41453 | 22000
8104 | 12 | 338 | 15 | 0 | 0.6187 | 0.41156 | 22000
8105 | 12 | 338 | 16 | 0 | 0.30798 | 0.42929 | 22000
8106 | 12 | 338 | 17 | 0 | 0.043916 | 0.65011 | 22000
8107 | 12 | 338 | 18 | 0 | 0 | 0.71345 | 22000
8108 | 12 | 338 | 19 | 1 | 0 | 0.7097 | 21800
8109 | 12 | 338 | 20 | 1 | 0 | 0.47518 | 21600
8110 | 12 | 338 | 21 | 0 | 0 | 0.47969 | 21600
8111 | 12 | 338 | 22 | 0 | 0 | 0.72788 | 21600
8112 | 12 | 338 | 23 | 0 | 0 | 0.61298 | 21600
8113 | 12 | 339 | 0 | 0 | 0 | 0.60541 | 21600
8114 | 12 | 339 | 1 | 0 | 0 | 0.54761 | 21600
8115 | 12 | 339 | 2 | 0 | 0 | 0.42383 | 21600
8116 | 12 | 339 | 3 | 0 | 0 | 0.30275 | 21600
8117 | 12 | 339 | 4 | 0 | 0 | 0.22623 | 21600
8118 | 12 | 339 | 5 | 0 | 0 | 0.14078 | 21600
8119 | 12 | 339 | 6 | 0 | 0 | 0.18836 | 21600
8120 | 12 | 339 | 7 | 1 | 0.050166 | 0.15634 | 21400
8121 | 12 | 339 | 8 | 1 | 0.35182 | 0.19762 | 21200
8122 | 12 | 339 | 9 | 0 | 0.70676 | 0.27474 | 21200
8123 | 12 | 339 | 10 | 0 | 1 | 0.3864 | 21200
8124 | 12 | 339 | 11 | 0 | 1 | 0.28042 | 21200
8125 | 12 | 339 | 12 | 0 | 1 | 0.33379 | 21200
8126 | 12 | 339 | 13 | 0 | 1 | 0.33728 | 21200
8127 | 12 | 339 | 14 | 0 | 1 | 0.3456 | 21200
8128 | 12 | 339 | 15 | 0 | 0.70676 | 0.21587 | 21200
8129 | 12 | 339 | 16 | 0 | 0.35182 | 0.1349 | 21200
8130 | 12 | 339 | 17 | 0 | 0.050166 | 0.15705 | 21200
8131 | 12 | 339 | 18 | 0 | 0 | 0.10889 | 21200
8132 | 12 | 339 | 19 | 1 | 0 | 0.16374 | 21000
8133 | 12 | 339 | 20 | 1 | 0 | 0.17705 | 20800
8134 | 12 | 339 | 21 | 0 | 0 | 0.17177 | 20800
8135 | 12 | 339 | 22 | 0 | 0 | 0.13762 | 20800
8136 | 12 | 339 | 23 | 0 | 0 | 0.1215 | 20800
8137 | 12 | 340 | 0 | 0 | 0 | 0.1857 | 20800
8138 | 12 | 340 | 1 | 0 | 0 | 0.12948 | 20800
8139 | 12 | 340 | 2 | 0 | 0 | 0.097459 | 20800
8140 | 12 | 340 | 3 | 0 | 0 | 0.099931 | 20800
8141 | 12 | 340 | 4 | 0 | 0 | 0.10036 | 20800
8142 | 12 | 340 | 5 | 0 | 0 | 0.10454 | 20800
8143 | 12 | 340 | 6 | 0 | 0 | 0.14291 | 20800
8144 | 12 | 340 | 7 | 1 | 0.050731 | 0.13877 | 20600
8145 | 12 | 340 | 8 | 1 | 0.35578 | 0.21883 | 20400
8146 | 12 | 340 | 9 | 0 | 0.71472 | 0.27882 | 20400
8147 | 12 | 340 | 10 | 0 | 1 | 0.34178 | 20400
8148 | 12 | 340 | 11 | 0 | 1 | 0.34701 | 20400
8149 | 12 | 340 | 12 | 0 | 1 | 0.39833 | 20400
8150 | 12 | 340 | 13 | 0 | 1 | 0.33815 | 20400
8151 | 12 | 340 | 14 | 0 | 1 | 0.40749 | 20400
8152 | 12 | 340 | 15 | 0 | 0.71472 | 0.38166 | 20400
8153 | 12 | 340 | 16 | 0 | 0.35578 | 0.32369 | 20400
8154 | 12 | 340 | 17 | 0 | 0.050731 | 0.22217 | 20400
8155 | 12 | 340 | 18 | 0 | 0 | 0.18797 | 20400
8156 | 12 | 340 | 19 | 1 | 0 | 0.17095 | 20200
8157 | 12 | 340 | 20 | 1 | 0 | 0.15632 | 20000
8158 | 12 | 340 | 21 | 0 | 0 | 0.15253 | 20000
8159 | 12 | 340 | 22 | 0 | 0 | 0.12978 | 20000
8160 | 12 | 340 | 23 | 0 | 0 | 0.093842 | 20000
8161 | 12 | 341 | 0 | 0 | 0 | 0.15798 | 20000
8162 | 12 | 341 | 1 | 0 | 0 | 0.13533 | 20000
8163 | 12 | 341 | 2 | 0 | 0 | 0.18574 | 20000
8164 | 12 | 341 | 3 | 0 | 0 | 0.16685 | 20000
8165 | 12 | 341 | 4 | 0 | 0 | 0.16956 | 20000
8166 | 12 | 341 | 5 | 0 | 0 | 0.15238 | 20000
8167 | 12 | 341 | 6 | 0 | 0 | 0.16544 | 20000
8168 | 12 | 341 | 7 | 1 | 0.045907 | 0.19265 | 19800
8169 | 12 | 341 | 8 | 1 | 0.32194 | 0.25842 | 19600
8170 | 12 | 341 | 9 | 0 | 0.64675 | 0.26551 | 19600
8171 | 12 | 341 | 10 | 0 | 0.93731 | 0.24173 | 19600
8172 | 12 | 341 | 11 | 0 | 1 | 0.25988 | 19600
8173 | 12 | 341 | 12 | 0 | 1 | 0.4151 | 19600
8174 | 12 | 341 | 13 | 0 | 1 | 0.56711 | 19600
8175 | 12 | 341 | 14 | 0 | 0.93731 | 0.57573 | 19600
8176 | 12 | 341 | 15 | 0 | 0.64675 | 0.35113 | 19600
8177 | 12 | 341 | 16 | 0 | 0.32194 | 0.27735 | 19600
8178 | 12 | 341 | 17 | 0 | 0.045907 | 0.39444 | 19600
8179 | 12 | 341 | 18 | 0 | 0 | 0.33747 | 19600
8180 | 12 | 341 | 19 | 1 | 0 | 0.30957 | 19400
8181 | 12 | 341 | 20 | 1 | 0 | 0.33373 | 19200
8182 | 12 | 341 | 21 | 0 | 0 | 0.29387 | 19200
8183 | 12 | 341 | 22 | 0 | 0 | 0.33093 | 19200
8184 | 12 | 341 | 23 | 0 | 0 | 0.3257 | 19200
8185 | 12 | 342 | 0 | 0 | 0 | 0.2092 | 19200
8186 | 12 | 342 | 1 | 0 | 0 | 0.37895 | 19200
8187 | 12 | 342 | 2 | 0 | 0 | 0.32344 | 19200
8188 | 12 | 342 | 3 | 0 | 0 | 0.21498 | 19200
8189 | 12 | 342 | 4 | 0 | 0 | 0.18682 | 19200
8190 | 12 | 342 | 5 | 0 | 0 | 0.14442 | 19200
8191 | 12 | 342 | 6 | 0 | 0 | 0.1549 | 19200
8192 | 12 | 342 | 7 | 1 | 0.045825 | 0.10919 | 19000
8193 | 12 | 342 | 8 | 1 | 0.32137 | 0.087411 | 18800
8194 | 12 | 342 | 9 | 0 | 0.64561 | 0.17403 | 18800
8195 | 12 | 342 | 10 | 0 | 0.93565 | 0.18471 | 18800
8196 | 12 | 342 | 11 | 0 | 1 | 0.18592 | 18800
8197 | 12 | 342 | 12 | 0 | 1 | 0.29211 | 18800
8198 | 12 | 342 | 13 | 0 | 1 | 0.26746 | 18800
8199 | 12 | 342 | 14 | 0 | 0.93565 | 0.29531 | 18800
8200 | 12 | 342 | 15 | 0 | 0.64561 | 0.35502 | 18800
8201 | 12 | 342 | 16 | 0 | 0.32137 | 0.38793 | 18800
8202 | 12 | 342 | 17 | 0 | 0.045825 | 0.28545 | 18800
8203 | 12 | 342 | 18 | 0 | 0 | 0.32822 | 18800
8204 | 12 | 342 | 19 | 1 | 0 | 0.29451 | 18600
8205 | 12 | 342 | 20 | 1 | 0 | 0.27159 | 18400
8206 | 12 | 342 | 21 | 0 | 0 | 0.23897 | 18400
8207 | 12 | 342 | 22 | 0 | 0 | 0.25882 | 18400
8208 | 12 | 342 | 23 | 0 | 0 | 0.24757 | 18400
8209 | 12 | 343 | 0 | 0 | 0 | 0.3461 | 18400
8210 | 12 | 343 | 1 | 0 | 0 | 0.28683 | 18400
8211 | 12 | 343 | 2 | 0 | 0 | 0.30991 | 18400
8212 | 12 | 343 | 3 | 0 | 0 | 0.28942 | 18400
8213 | 12 | 343 | 4 | 0 | 0 | 0.2464 | 18400
8214 | 12 | 343 | 5 | 0 | 0 | 0.20887 | 18400
8215 | 12 | 343 | 6 | 0 | 0 | 0.29366 | 18400
8216 | 12 | 343 | 7 | 1 | 0.047731 | 0.30663 | 18200
8217 | 12 | 343 | 8 | 1 | 0.33474 | 0.3628 | 18000
8218 | 12 | 343 | 9 | 0 | 0.67245 | 0.34914 | 18000
8219 | 12 | 343 | 10 | 0 | 0.97455 | 0.43039 | 18000
8220 | 12 | 343 | 11 | 0 | 1 | 0.38648 | 18000
8221 | 12 | 343 | 12 | 0 | 1 | 0.33035 | 18000
8222 | 12 | 343 | 13 | 0 | 1 | 0.18403 | 18000
8223 | 12 | 343 | 14 | 0 | 0.97455 | 0.16395 | 18000
8224 | 12 | 343 | 15 | 0 | 0.67245 | 0.13363 | 18000
8225 | 12 | 343 | 16 | 0 | 0.33474 | 0.099322 | 18000
8226 | 12 | 343 | 17 | 0 | 0.047731 | 0.12485 | 18000
8227 | 12 | 343 | 18 | 0 | 0 | 0.23793 | 18000
8228 | 12 | 343 | 19 | 1 | 0 | 0.23583 | 17800
8229 | 12 | 343 | 20 | 1 | 0 | 0.15071 | 17600
8230 | 12 | 343 | 21 | 0 | 0 | 0.16502 | 17600
8231 | 12 | 343 | 22 | 0 | 0 | 0.14781 | 17600
8232 | 12 | 343 | 23 | 0 | 0 | 0.17539 | 17600
8233 | 12 | 344 | 0 | 0 | 0 | 0.18799 | 17600
8234 | 12 | 344 | 1 | 0 | 0 | 0.21183 | 17600
8235 | 12 | 344 | 2 | 0 | 0 | 0.29506 | 17600
8236 | 12 | 344 | 3 | 0 | 0 | 0.39056 | 17600
8237 | 12 | 344 | 4 | 0 | 0 | 0.38299 | 17600
8238 | 12 | 344 | 5 | 0 | 0 | 0.39497 | 17600
8239 | 12 | 344 | 6 | 0 | 0 | 0.41457 | 17600
8240 | 12 | 344 | 7 | 1 | 0.048026 | 0.35256 | 17400
8241 | 12 | 344 | 8 | 1 | 0.33681 | 0.28347 | 17200
8242 | 12 | 344 | 9 | 0 | 0.67661 | 0.27444 | 17200
8243 | 12 | 344 | 10 | 0 | 0.98058 | 0.25878 | 17200
8244 | 12 | 344 | 11 | 0 | 1 | 0.27037 | 17200
8245 | 12 | 344 | 12 | 0 | 1 | 0.6327 | 17200
8246 | 12 | 344 | 13 | 0 | 1 | 0.60279 | 17200
8247 | 12 | 344 | 14 | 0 | 0.98058 | 0.66494 | 17200
8248 | 12 | 344 | 15 | 0 | 0.67661 | 0.6999 | 17200
8249 | 12 | 344 | 16 | 0 | 0.33681 | 0.8893 | 17200
8250 | 12 | 344 | 17 | 0 | 0.048026 | 1 | 17200
8251 | 12 | 344 | 18 | 0 | 0 | 0.72169 | 17200
8252 | 12 | 344 | 19 | 1 | 0 | 0.86507 | 17000
8253 | 12 | 344 | 20 | 1 | 0 | 0.79988 | 16800
8254 | 12 | 344 | 21 | 0 | 0 | 0.61372 | 16800
8255 | 12 | 344 | 22 | 0 | 0 | 0.52079 | 16800
8256 | 12 | 344 | 23 | 0 | 0 | 0.5239 | 16800
8257 | 12 | 345 | 0 | 0 | 0 | 0.45771 | 16800
8258 | 12 | 345 | 1 | 0 | 0 | 0.42064 | 16800
8259 | 12 | 345 | 2 | 0 | 0 | 0.35998 | 16800
8260 | 12 | 345 | 3 | 0 | 0 | 0.29099 | 16800
8261 | 12 | 345 | 4 | 0 | 0 | 0.38135 | 16800
8262 | 12 | 345 | 5 | 0 | 0 | 0.35632 | 16800
8263 | 12 | 345 | 6 | 0 | 0 | 0.27888 | 16800
8264 | 12 | 345 | 7 | 1 | 0.053323 | 0.34736 | 16600
8265 | 12 | 345 | 8 | 1 | 0.37395 | 0.39314 | 16400
8266 | 12 | 345 | 9 | 0 | 0.75123 | 0.2784 | 16400
8267 | 12 | 345 | 10 | 0 | 1 | 0.29637 | 16400
8268 | 12 | 345 | 11 | 0 | 1 | 0.24444 | 16400
8269 | 12 | 345 | 12 | 0 | 1 | 0.25873 | 16400
8270 | 12 | 345 | 13 | 0 | 1 | 0.17243 | 16400
8271 | 12 | 345 | 14 | 0 | 1 | 0.20614 | 16400
8272 | 12 | 345 | 15 | 0 | 0.75123 | 0.22225 | 16400
8273 | 12 | 345 | 16 | 0 | 0.37395 | 0.17847 | 16400
8274 | 12 | 345 | 17 | 0 | 0.053323 | 0.27866 | 16400
8275 | 12 | 345 | 18 | 0 | 0 | 0.19079 | 16400
8276 | 12 | 345 | 19 | 1 | 0 | 0.16546 | 16200
8277 | 12 | 345 | 20 | 1 | 0 | 0.16489 | 16000
8278 | 12 | 345 | 21 | 0 | 0 | 0.10684 | 16000
8279 | 12 | 345 | 22 | 0 | 0 | 0.13465 | 16000
8280 | 12 | 345 | 23 | 0 | 0 | 0.11676 | 16000
8281 | 12 | 346 | 0 | 0 | 0 | 0.11806 | 16000
8282 | 12 | 346 | 1 | 0 | 0 | 0.12648 | 16000
8283 | 12 | 346 | 2 | 0 | 0 | 0.085273 | 16000
8284 | 12 | 346 | 3 | 0 | 0 | 0.089636 | 16000
8285 | 12 | 346 | 4 | 0 | 0 | 0.060879 | 16000
8286 | 12 | 346 | 5 | 0 | 0 | 0.074928 | 16000
8287 | 12 | 346 | 6 | 0 | 0 | 0.07583 | 16000
8288 | 12 | 346 | 7 | 1 | 0.042696 | 0.084935 | 15800
8289 | 12 | 346 | 8 | 1 | 0.29942 | 0.1106 | 15600
8290 | 12 | 346 | 9 | 0 | 0.60151 | 0.10569 | 15600
8291 | 12 | 346 | 10 | 0 | 0.87174 | 0.11001 | 15600
8292 | 12 | 346 | 11 | 0 | 1 | 0.11573 | 15600
8293 | 12 | 346 | 12 | 0 | 1 | 0.10705 | 15600
8294 | 12 | 346 | 13 | 0 | 1 | 0.10255 | 15600
8295 | 12 | 346 | 14 | 0 | 0.87174 | 0.1132 | 15600
8296 | 12 | 346 | 15 | 0 | 0.60151 | 0.08147 | 15600
8297 | 12 | 346 | 16 | 0 | 0.29942 | 0.087855 | 15600
8298 | 12 | 346 | 17 | 0 | 0.042696 | 0.10719 | 15600
8299 | 12 | 346 | 18 | 0 | 0 | 0.089646 | 15600
8300 | 12 | 346 | 19 | 1 | 0 | 0.10116 | 15400
8301 | 12 | 346 | 20 | 1 | 0 | 0.1174 | 15200
8302 | 12 | 346 | 21 | 0 | 0 | 0.14753 | 15200
8303 | 12 | 346 | 22 | 0 | 0 | 0.17711 | 15200
8304 | 12 | 346 | 23 | 0 | 0 | 0.11488 | 15200
8305 | 12 | 347 | 0 | 0 | 0 | 0.14881 | 15200
8306 | 12 | 347 | 1 | 0 | 0 | 0.17406 | 15200
8307 | 12 | 347 | 2 | 0 | 0 | 0.14033 | 15200
8308 | 12 | 347 | 3 | 0 | 0 | 0.094103 | 15200
8309 | 12 | 347 | 4 | 0 | 0 | 0.15564 | 15200
8310 | 12 | 347 | 5 | 0 | 0 | 0.27099 | 15200
8311 | 12 | 347 | 6 | 0 | 0 | 0.24612 | 15200
8312 | 12 | 347 | 7 | 1 | 0.045857 | 0.25766 | 15000
8313 | 12 | 347 | 8 | 1 | 0.3216 | 0.21785 | 14800
8314 | 12 | 347 | 9 | 0 | 0.64606 | 0.17342 | 14800
8315 | 12 | 347 | 10 | 0 | 0.9363 | 0.2715 | 14800
8316 | 12 | 347 | 11 | 0 | 1 | 0.2417 | 14800
8317 | 12 | 347 | 12 | 0 | 1 | 0.33731 | 14800
8318 | 12 | 347 | 13 | 0 | 1 | 0.40331 | 14800
8319 | 12 | 347 | 14 | 0 | 0.9363 | 0.57709 | 14800
8320 | 12 | 347 | 15 | 0 | 0.64606 | 0.51981 | 14800
8321 | 12 | 347 | 16 | 0 | 0.3216 | 0.51119 | 14800
8322 | 12 | 347 | 17 | 0 | 0.045857 | 0.81613 | 14800
8323 | 12 | 347 | 18 | 0 | 0 | 0.76071 | 14800
8324 | 12 | 347 | 19 | 1 | 0 | 0.59941 | 14600
8325 | 12 | 347 | 20 | 1 | 0 | 0.68162 | 14400
8326 | 12 | 347 | 21 | 0 | 0 | 0.74984 | 14400
8327 | 12 | 347 | 22 | 0 | 0 | 0.77555 | 14400
8328 | 12 | 347 | 23 | 0 | 0 | 0.42604 | 14400
8329 | 12 | 348 | 0 | 0 | 0 | 0.42908 | 14400
8330 | 12 | 348 | 1 | 0 | 0 | 0.39483 | 14400
8331 | 12 | 348 | 2 | 0 | 0 | 0.34449 | 14400
8332 | 12 | 348 | 3 | 0 | 0 | 0.34937 | 14400
8333 | 12 | 348 | 4 | 0 | 0 | 0.27686 | 14400
8334 | 12 | 348 | 5 | 0 | 0 | 0.30465 | 14400
8335 | 12 | 348 | 6 | 0 | 0 | 0.41764 | 14400
8336 | 12 | 348 | 7 | 1 | 0.04871 | 0.27582 | 14200
8337 | 12 | 348 | 8 | 1 | 0.3416 | 0.30334 | 14000
8338 | 12 | 348 | 9 | 0 | 0.68624 | 0.31456 | 14000
8339 | 12 | 348 | 10 | 0 | 0.99454 | 0.26554 | 14000
8340 | 12 | 348 | 11 | 0 | 1 | 0.27645 | 14000
8341 | 12 | 348 | 12 | 0 | 1 | 0.17665 | 14000
8342 | 12 | 348 | 13 | 0 | 1 | 0.1508 | 14000
8343 | 12 | 348 | 14 | 0 | 0.99454 | 0.1506 | 14000
8344 | 12 | 348 | 15 | 0 | 0.68624 | 0.15271 | 14000
8345 | 12 | 348 | 16 | 0 | 0.3416 | 0.22017 | 14000
8346 | 12 | 348 | 17 | 0 | 0.04871 | 0.30385 | 14000
8347 | 12 | 348 | 18 | 0 | 0 | 0.38056 | 14000
8348 | 12 | 348 | 19 | 1 | 0 | 0.42245 | 13800
8349 | 12 | 348 | 20 | 1 | 0 | 0.47537 | 13600
8350 | 12 | 348 | 21 | 0 | 0 | 0.42181 | 13600
8351 | 12 | 348 | 22 | 0 | 0 | 0.43644 | 13600
8352 | 12 | 348 | 23 | 0 | 0 | 0.26958 | 13600
8353 | 12 | 349 | 0 | 0 | 0 | 0.4782 | 13600
8354 | 12 | 349 | 1 | 0 | 0 | 0.27291 | 13600
8355 | 12 | 349 | 2 | 0 | 0 | 0.34728 | 13600
8356 | 12 | 349 | 3 | 0 | 0 | 0.38258 | 13600
8357 | 12 | 349 | 4 | 0 | 0 | 0.29423 | 13600
8358 | 12 | 349 | 5 | 0 | 0 | 0.2766 | 13600
8359 | 12 | 349 | 6 | 0 | 0 | 0.34945 | 13600
8360 | 12 | 349 | 7 | 1 | 0.035954 | 0.33494 | 13400
8361 | 12 | 349 | 8 | 1 | 0.25215 | 0.3126 | 13200
8362 | 12 | 349 | 9 | 0 | 0.50654 | 0.28313 | 13200
8363 | 12 | 349 | 10 | 0 | 0.73411 | 0.2377 | 13200
8364 | 12 | 349 | 11 | 0 | 0.88979 | 0.2703 | 13200
8365 | 12 | 349 | 12 | 0 | 0.94498 | 0.17066 | 13200
8366 | 12 | 349 | 13 | 0 | 0.88979 | 0.12461 | 13200
8367 | 12 | 349 | 14 | 0 | 0.73411 | 0.13573 | 13200
8368 | 12 | 349 | 15 | 0 | 0.50654 | 0.1208 | 13200
8369 | 12 | 349 | 16 | 0 | 0.25215 | 0.13318 | 13200
8370 | 12 | 349 | 17 | 0 | 0.035954 | 0.12188 | 13200
8371 | 12 | 349 | 18 | 0 | 0 | 0.12355 | 13200
8372 | 12 | 349 | 19 | 1 | 0 | 0.17989 | 13000
8373 | 12 | 349 | 20 | 1 | 0 | 0.18206 | 12800
8374 | 12 | 349 | 21 | 0 | 0 | 0.16115 | 12800
8375 | 12 | 349 | 22 | 0 | 0 | 0.18587 | 12800
8376 | 12 | 349 | 23 | 0 | 0 | 0.35585 | 12800
8377 | 12 | 350 | 0 | 0 | 0 | 0.32906 | 12800
8378 | 12 | 350 | 1 | 0 | 0 | 0.44323 | 12800
8379 | 12 | 350 | 2 | 0 | 0 | 0.51898 | 12800
8380 | 12 | 350 | 3 | 0 | 0 | 0.32062 | 12800
8381 | 12 | 350 | 4 | 0 | 0 | 0.37084 | 12800
8382 | 12 | 350 | 5 | 0 | 0 | 0.38383 | 12800
8383 | 12 | 350 | 6 | 0 | 0 | 0.46538 | 12800
8384 | 12 | 350 | 7 | 1 | 0.050678 | 0.49771 | 12600
8385 | 12 | 350 | 8 | 1 | 0.35541 | 0.49104 | 12400
8386 | 12 | 350 | 9 | 0 | 0.71397 | 0.38274 | 12400
8387 | 12 | 350 | 10 | 0 | 1 | 0.46584 | 12400
8388 | 12 | 350 | 11 | 0 | 1 | 0.44065 | 12400
8389 | 12 | 350 | 12 | 0 | 1 | 0.54676 | 12400
8390 | 12 | 350 | 13 | 0 | 1 | 0.61266 | 12400
8391 | 12 | 350 | 14 | 0 | 1 | 0.64682 | 12400
8392 | 12 | 350 | 15 | 0 | 0.71397 | 0.57652 | 12400
8393 | 12 | 350 | 16 | 0 | 0.35541 | 0.3267 | 12400
8394 | 12 | 350 | 17 | 0 | 0.050678 | 0.30601 | 12400
8395 | 12 | 350 | 18 | 0 | 0 | 0.28684 | 12400
8396 | 12 | 350 | 19 | 1 | 0 | 0.41072 | 12200
8397 | 12 | 350 | 20 | 1 | 0 | 0.51972 | 12000
8398 | 12 | 350 | 21 | 0 | 0 | 0.35861 | 12000
8399 | 12 | 350 | 22 | 0 | 0 | 0.43261 | 12000
8400 | 12 | 350 | 23 | 0 | 0 | 0.45038 | 12000
8401 | 12 | 351 | 0 | 0 | 0 | 0.6182 | 12000
8402 | 12 | 351 | 1 | 0 | 0 | 0.3841 | 12000
8403 | 12 | 351 | 2 | 0 | 0 | 0.38717 | 12000
8404 | 12 | 351 | 3 | 0 | 0 | 0.56245 | 12000
8405 | 12 | 351 | 4 | 0 | 0 | 0.7583 | 12000
8406 | 12 | 351 | 5 | 0 | 0 | 0.74627 | 12000
8407 | 12 | 351 | 6 | 0 | 0 | 0.68721 | 12000
8408 | 12 | 351 | 7 | 1 | 0.048306 | 0.58671 | 11800
8409 | 12 | 351 | 8 | 1 | 0.33877 | 0.9486 | 11600
8410 | 12 | 351 | 9 | 0 | 0.68056 | 0.69359 | 11600
8411 | 12 | 351 | 10 | 0 | 0.9863 | 0.8041 | 11600
8412 | 12 | 351 | 11 | 0 | 1 | 0.8645 | 11600
8413 | 12 | 351 | 12 | 0 | 1 | 0.86191 | 11600
8414 | 12 | 351 | 13 | 0 | 1 | 1 | 11600
8415 | 12 | 351 | 14 | 0 | 0.9863 | 0.85506 | 11600
8416 | 12 | 351 | 15 | 0 | 0.68056 | 0.84236 | 11600
8417 | 12 | 351 | 16 | 0 | 0.33877 | 0.94192 | 11600
8418 | 12 | 351 | 17 | 0 | 0.048306 | 0.72948 | 11600
8419 | 12 | 351 | 18 | 0 | 0 | 0.70486 | 11600
8420 | 12 | 351 | 19 | 1 | 0 | 0.95558 | 11400
8421 | 12 | 351 | 20 | 1 | 0 | 1 | 11200
8422 | 12 | 351 | 21 | 0 | 0 | 1 | 11200
8423 | 12 | 351 | 22 | 0 | 0 | 0.68462 | 11200
8424 | 12 | 351 | 23 | 0 | 0 | 0.8819 | 11200
8425 | 12 | 352 | 0 | 0 | 0 | 0.65883 | 11200
8426 | 12 | 352 | 1 | 0 | 0 | 0.61424 | 11200
8427 | 12 | 352 | 2 | 0 | 0 | 0.29859 | 11200
8428 | 12 | 352 | 3 | 0 | 0 | 0.5572 | 11200
8429 | 12 | 352 | 4 | 0 | 0 | 0.53127 | 11200
8430 | 12 | 352 | 5 | 0 | 0 | 0.22859 | 11200
8431 | 12 | 352 | 6 | 0 | 0 | 0.25724 | 11200
8432 | 12 | 352 | 7 | 1 | 0.047079 | 0.35067 | 11000
8433 | 12 | 352 | 8 | 1 | 0.33017 | 0.38844 | 10800
8434 | 12 | 352 | 9 | 0 | 0.66327 | 0.25157 | 10800
8435 | 12 | 352 | 10 | 0 | 0.96125 | 0.22179 | 10800
8436 | 12 | 352 | 11 | 0 | 1 | 0.21743 | 10800
8437 | 12 | 352 | 12 | 0 | 1 | 0.22224 | 10800
8438 | 12 | 352 | 13 | 0 | 1 | 0.23962 | 10800
8439 | 12 | 352 | 14 | 0 | 0.96125 | 0.2255 | 10800
8440 | 12 | 352 | 15 | 0 | 0.66327 | 0.26996 | 10800
8441 | 12 | 352 | 16 | 0 | 0.33017 | 0.29217 | 10800
8442 | 12 | 352 | 17 | 0 | 0.047079 | 0.34341 | 10800
8443 | 12 | 352 | 18 | 0 | 0 | 0.32438 | 10800
8444 | 12 | 352 | 19 | 1 | 0 | 0.49476 | 10600
8445 | 12 | 352 | 20 | 1 | 0 | 0.71731 | 10400
8446 | 12 | 352 | 21 | 0 | 0 | 0.77326 | 10400
8447 | 12 | 352 | 22 | 0 | 0 | 0.93383 | 10400
8448 | 12 | 352 | 23 | 0 | 0 | 0.61146 | 10400
8449 | 12 | 353 | 0 | 0 | 0 | 0.80353 | 10400
8450 | 12 | 353 | 1 | 0 | 0 | 0.72158 | 10400
8451 | 12 | 353 | 2 | 0 | 0 | 0.45314 | 10400
8452 | 12 | 353 | 3 | 0 | 0 | 0.57394 | 10400
8453 | 12 | 353 | 4 | 0 | 0 | 0.41225 | 10400
8454 | 12 | 353 | 5 | 0 | 0 | 0.49851 | 10400
8455 | 12 | 353 | 6 | 0 | 0 | 0.5175 | 10400
8456 | 12 | 353 | 7 | 1 | 0.04072 | 0.48864 | 10200
8457 | 12 | 353 | 8 | 1 | 0.28557 | 0.62917 | 10000
8458 | 12 | 353 | 9 | 0 | 0.57368 | 0.49966 | 10000
8459 | 12 | 353 | 10 | 0 | 0.83141 | 0.37782 | 10000
8460 | 12 | 353 | 11 | 0 | 1 | 0.29809 | 10000
8461 | 12 | 353 | 12 | 0 | 1 | 0.306 | 10000
8462 | 12 | 353 | 13 | 0 | 1 | 0.31799 | 10000
8463 | 12 | 353 | 14 | 0 | 0.83141 | 0.19975 | 10000
8464 | 12 | 353 | 15 | 0 | 0.57368 | 0.24738 | 10000
8465 | 12 | 353 | 16 | 0 | 0.28557 | 0.3007 | 10000
8466 | 12 | 353 | 17 | 0 | 0.04072 | 0.31901 | 10000
8467 | 12 | 353 | 18 | 0 | 0 | 0.41926 | 10000
8468 | 12 | 353 | 19 | 1 | 0 | 0.34808 | 9800
8469 | 12 | 353 | 20 | 1 | 0 | 0.16925 | 9600
8470 | 12 | 353 | 21 | 0 | 0 | 0.14568 | 9600
8471 | 12 | 353 | 22 | 0 | 0 | 0.16419 | 9600
8472 | 12 | 353 | 23 | 0 | 0 | 0.15491 | 9600
8473 | 12 | 354 | 0 | 0 | 0 | 0.183 | 9600
8474 | 12 | 354 | 1 | 0 | 0 | 0.22849 | 9600
8475 | 12 | 354 | 2 | 0 | 0 | 0.21172 | 9600
8476 | 12 | 354 | 3 | 0 | 0 | 0.18586 | 9600
8477 | 12 | 354 | 4 | 0 | 0 | 0.24449 | 9600
8478 | 12 | 354 | 5 | 0 | 0 | 0.38452 | 9600
8479 | 12 | 354 | 6 | 0 | 0 | 0.45467 | 9600
8480 | 12 | 354 | 7 | 1 | 0.057668 | 0.40034 | 9400
8481 | 12 | 354 | 8 | 1 | 0.40443 | 0.36922 | 9200
8482 | 12 | 354 | 9 | 0 | 0.81246 | 0.34794 | 9200
8483 | 12 | 354 | 10 | 0 | 1 | 0.4272 | 9200
8484 | 12 | 354 | 11 | 0 | 1 | 0.4453 | 9200
8485 | 12 | 354 | 12 | 0 | 1 | 0.31848 | 9200
8486 | 12 | 354 | 13 | 0 | 1 | 0.38539 | 9200
8487 | 12 | 354 | 14 | 0 | 1 | 0.34553 | 9200
8488 | 12 | 354 | 15 | 0 | 0.81246 | 0.34372 | 9200
8489 | 12 | 354 | 16 | 0 | 0.40443 | 0.28979 | 9200
8490 | 12 | 354 | 17 | 0 | 0.057668 | 0.33632 | 9200
8491 | 12 | 354 | 18 | 0 | 0 | 0.24726 | 9200
8492 | 12 | 354 | 19 | 1 | 0 | 0.25164 | 9000
8493 | 12 | 354 | 20 | 1 | 0 | 0.19244 | 8800
8494 | 12 | 354 | 21 | 0 | 0 | 0.21525 | 8800
8495 | 12 | 354 | 22 | 0 | 0 | 0.21427 | 8800
8496 | 12 | 354 | 23 | 0 | 0 | 0.20926 | 8800
8497 | 12 | 355 | 0 | 0 | 0 | 0.21857 | 8800
8498 | 12 | 355 | 1 | 0 | 0 | 0.1824 | 8800
8499 | 12 | 355 | 2 | 0 | 0 | 0.078375 | 8800
8500 | 12 | 355 | 3 | 0 | 0 | 0.066924 | 8800
8501 | 12 | 355 | 4 | 0 | 0 | 0.12698 | 8800
8502 | 12 | 355 | 5 | 0 | 0 | 0.091422 | 8800
8503 | 12 | 355 | 6 | 0 | 0 | 0.067932 | 8800
8504 | 12 | 355 | 7 | 1 | 0.046812 | 0.12818 | 8600
8505 | 12 | 355 | 8 | 1 | 0.32829 | 0.1343 | 8400
8506 | 12 | 355 | 9 | 0 | 0.6595 | 0.1432 | 8400
8507 | 12 | 355 | 10 | 0 | 0.95578 | 0.16142 | 8400
8508 | 12 | 355 | 11 | 0 | 1 | 0.24778 | 8400
8509 | 12 | 355 | 12 | 0 | 1 | 0.18262 | 8400
8510 | 12 | 355 | 13 | 0 | 1 | 0.30285 | 8400
8511 | 12 | 355 | 14 | 0 | 0.95578 | 0.31099 | 8400
8512 | 12 | 355 | 15 | 0 | 0.6595 | 0.32765 | 8400
8513 | 12 | 355 | 16 | 0 | 0.32829 | 0.22529 | 8400
8514 | 12 | 355 | 17 | 0 | 0.046812 | 0.18465 | 8400
8515 | 12 | 355 | 18 | 0 | 0 | 0.1731 | 8400
8516 | 12 | 355 | 19 | 1 | 0 | 0.24108 | 8200
8517 | 12 | 355 | 20 | 1 | 0 | 0.21609 | 8000
8518 | 12 | 355 | 21 | 0 | 0 | 0.16078 | 8000
8519 | 12 | 355 | 22 | 0 | 0 | 0.14054 | 8000
8520 | 12 | 355 | 23 | 0 | 0 | 0.12649 | 8000
8521 | 12 | 356 | 0 | 0 | 0 | 0.16467 | 8000
8522 | 12 | 356 | 1 | 0 | 0 | 0.1312 | 8000
8523 | 12 | 356 | 2 | 0 | 0 | 0.11621 | 8000
8524 | 12 | 356 | 3 | 0 | 0 | 0.19475 | 8000
8525 | 12 | 356 | 4 | 0 | 0 | 0.1459 | 8000
8526 | 12 | 356 | 5 | 0 | 0 | 0.1816 | 8000
8527 | 12 | 356 | 6 | 0 | 0 | 0.15878 | 8000
8528 | 12 | 356 | 7 | 1 | 0.047949 | 0.26334 | 7800
8529 | 12 | 356 | 8 | 1 | 0.33626 | 0.24992 | 7600
8530 | 12 | 356 | 9 | 0 | 0.67552 | 0.19502 | 7600
8531 | 12 | 356 | 10 | 0 | 0.97899 | 0.17064 | 7600
8532 | 12 | 356 | 11 | 0 | 1 | 0.36373 | 7600
8533 | 12 | 356 | 12 | 0 | 1 | 0.39725 | 7600
8534 | 12 | 356 | 13 | 0 | 1 | 0.23947 | 7600
8535 | 12 | 356 | 14 | 0 | 0.97899 | 0.23378 | 7600
8536 | 12 | 356 | 15 | 0 | 0.67552 | 0.21718 | 7600
8537 | 12 | 356 | 16 | 0 | 0.33626 | 0.20654 | 7600
8538 | 12 | 356 | 17 | 0 | 0.047949 | 0.12955 | 7600
8539 | 12 | 356 | 18 | 0 | 0 | 0.12008 | 7600
8540 | 12 | 356 | 19 | 1 | 0 | 0.073291 | 7400
8541 | 12 | 356 | 20 | 1 | 0 | 0.083103 | 7200
8542 | 12 | 356 | 21 | 0 | 0 | 0.059217 | 7200
8543 | 12 | 356 | 22 | 0 | 0 | 0.051552 | 7200
8544 | 12 | 356 | 23 | 0 | 0 | 0.046521 | 7200
8545 | 12 | 357 | 0 | 0 | 0 | 0.038508 | 7200
8546 | 12 | 357 | 1 | 0 | 0 | 0.034105 | 7200
8547 | 12 | 357 | 2 | 0 | 0 | 0.048888 | 7200
8548 | 12 | 357 | 3 | 0 | 0 | 0.04047 | 7200
8549 | 12 | 357 | 4 | 0 | 0 | 0.042614 | 7200
8550 | 12 | 357 | 5 | 0 | 0 | 0.050977 | 7200
8551 | 12 | 357 | 6 | 0 | 0 | 0.067275 | 7200
8552 | 12 | 357 | 7 | 1 | 0.047182 | 0.092138 | 7000
8553 | 12 | 357 | 8 | 1 | 0.33089 | 0.14724 | 6800
8554 | 12 | 357 | 9 | 0 | 0.66473 | 0.14584 | 6800
8555 | 12 | 357 | 10 | 0 | 0.96335 | 0.14588 | 6800
8556 | 12 | 357 | 11 | 0 | 1 | 0.1401 | 6800
8557 | 12 | 357 | 12 | 0 | 1 | 0.1725 | 6800
8558 | 12 | 357 | 13 | 0 | 1 | 0.20875 | 6800
8559 | 12 | 357 | 14 | 0 | 0.96335 | 0.25559 | 6800
8560 | 12 | 357 | 15 | 0 | 0.66473 | 0.24551 | 6800
8561 | 12 | 357 | 16 | 0 | 0.33089 | 0.20984 | 6800
8562 | 12 | 357 | 17 | 0 | 0.047182 | 0.16108 | 6800
8563 | 12 | 357 | 18 | 0 | 0 | 0.21926 | 6800
8564 | 12 | 357 | 19 | 1 | 0 | 0.19875 | 6600
8565 | 12 | 357 | 20 | 1 | 0 | 0.20371 | 6400
8566 | 12 | 357 | 21 | 0 | 0 | 0.11255 | 6400
8567 | 12 | 357 | 22 | 0 | 0 | 0.10601 | 6400
8568 | 12 | 357 | 23 | 0 | 0 | 0.088403 | 6400
8569 | 12 | 358 | 0 | 0 | 0 | 0.080097 | 6400
8570 | 12 | 358 | 1 | 0 | 0 | 0.12343 | 6400
8571 | 12 | 358 | 2 | 0 | 0 | 0.13991 | 6400
8572 | 12 | 358 | 3 | 0 | 0 | 0.15924 | 6400
8573 | 12 | 358 | 4 | 0 | 0 | 0.11034 | 6400
8574 | 12 | 358 | 5 | 0 | 0 | 0.12722 | 6400
8575 | 12 | 358 | 6 | 0 | 0 | 0.11559 | 6400
8576 | 12 | 358 | 7 | 1 | 0.047298 | 0.10937 | 6200
8577 | 12 | 358 | 8 | 1 | 0.3317 | 0.089773 | 6000
8578 | 12 | 358 | 9 | 0 | 0.66635 | 0.11242 | 6000
8579 | 12 | 358 | 10 | 0 | 0.96571 | 0.14352 | 6000
8580 | 12 | 358 | 11 | 0 | 1 | 0.1448 | 6000
8581 | 12 | 358 | 12 | 0 | 1 | 0.21417 | 6000
8582 | 12 | 358 | 13 | 0 | 1 | 0.27356 | 6000
8583 | 12 | 358 | 14 | 0 | 0.96571 | 0.21671 | 6000
8584 | 12 | 358 | 15 | 0 | 0.66635 | 0.29249 | 6000
8585 | 12 | 358 | 16 | 0 | 0.3317 | 0.33994 | 6000
8586 | 12 | 358 | 17 | 0 | 0.047298 | 0.28033 | 6000
8587 | 12 | 358 | 18 | 0 | 0 | 0.15009 | 6000
8588 | 12 | 358 | 19 | 1 | 0 | 0.09968 | 5800
8589 | 12 | 358 | 20 | 1 | 0 | 0.18334 | 5600
8590 | 12 | 358 | 21 | 0 | 0 | 0.22945 | 5600
8591 | 12 | 358 | 22 | 0 | 0 | 0.34266 | 5600
8592 | 12 | 358 | 23 | 0 | 0 | 0.30177 | 5600
8593 | 12 | 359 | 0 | 0 | 0 | 0.24531 | 5600
8594 | 12 | 359 | 1 | 0 | 0 | 0.193 | 5600
8595 | 12 | 359 | 2 | 0 | 0 | 0.11801 | 5600
8596 | 12 | 359 | 3 | 0 | 0 | 0.18057 | 5600
8597 | 12 | 359 | 4 | 0 | 0 | 0.20021 | 5600
8598 | 12 | 359 | 5 | 0 | 0 | 0.2048 | 5600
8599 | 12 | 359 | 6 | 0 | 0 | 0.15611 | 5600
8600 | 12 | 359 | 7 | 1 | 0.049659 | 0.17541 | 5400
8601 | 12 | 359 | 8 | 1 | 0.34826 | 0.20783 | 5200
8602 | 12 | 359 | 9 | 0 | 0.69961 | 0.22714 | 5200
8603 | 12 | 359 | 10 | 0 | 1 | 0.18462 | 5200
8604 | 12 | 359 | 11 | 0 | 1 | 0.30308 | 5200
8605 | 12 | 359 | 12 | 0 | 1 | 0.56861 | 5200
8606 | 12 | 359 | 13 | 0 | 1 | 0.69425 | 5200
8607 | 12 | 359 | 14 | 0 | 1 | 0.78611 | 5200
8608 | 12 | 359 | 15 | 0 | 0.69961 | 0.64677 | 5200
8609 | 12 | 359 | 16 | 0 | 0.34826 | 0.79957 | 5200
8610 | 12 | 359 | 17 | 0 | 0.049659 | 0.6043 | 5200
8611 | 12 | 359 | 18 | 0 | 0 | 0.58468 | 5200
8612 | 12 | 359 | 19 | 1 | 0 | 0.46172 | 5000
8613 | 12 | 359 | 20 | 1 | 0 | 0.28552 | 4800
8614 | 12 | 359 | 21 | 0 | 0 | 0.21743 | 4800
8615 | 12 | 359 | 22 | 0 | 0 | 0.14197 | 4800
8616 | 12 | 359 | 23 | 0 | 0 | 0.16521 | 4800
8617 | 12 | 360 | 0 | 0 | 0 | 0.11887 | 4800
8618 | 12 | 360 | 1 | 0 | 0 | 0.12855 | 4800
8619 | 12 | 360 | 2 | 0 | 0 | 0.13989 | 4800
8620 | 12 | 360 | 3 | 0 | 0 | 0.12337 | 4800
8621 | 12 | 360 | 4 | 0 | 0 | 0.18207 | 4800
8622 | 12 | 360 | 5 | 0 | 0 | 0.18023 | 4800
8623 | 12 | 360 | 6 | 0 | 0 | 0.12593 | 4800
8624 | 12 | 360 | 7 | 1 | 0.04719 | 0.10645 | 4600
8625 | 12 | 360 | 8 | 1 | 0.33094 | 0.11725 | 4400
8626 | 12 | 360 | 9 | 0 | 0.66483 | 0.10253 | 4400
8627 | 12 | 360 | 10 | 0 | 0.96351 | 0.08744 | 4400
8628 | 12 | 360 | 11 | 0 | 1 | 0.12708 | 4400
8629 | 12 | 360 | 12 | 0 | 1 | 0.11587 | 4400
8630 | 12 | 360 | 13 | 0 | 1 | 0.13821 | 4400
8631 | 12 | 360 | 14 | 0 | 0.96351 | 0.14209 | 4400
8632 | 12 | 360 | 15 | 0 | 0.66483 | 0.13133 | 4400
8633 | 12 | 360 | 16 | 0 | 0.33094 | 0.13531 | 4400
8634 | 12 | 360 | 17 | 0 | 0.04719 | 0.1844 | 4400
8635 | 12 | 360 | 18 | 0 | 0 | 0.17471 | 4400
8636 | 12 | 360 | 19 | 1 | 0 | 0.177 | 4200
8637 | 12 | 360 | 20 | 1 | 0 | 0.20231 | 4000
8638 | 12 | 360 | 21 | 0 | 0 | 0.17422 | 4000
8639 | 12 | 360 | 22 | 0 | 0 | 0.1675 | 4000
8640 | 12 | 360 | 23 | 0 | 0 | 0.30304 | 4000
8641 | 12 | 361 | 0 | 0 | 0 | 0.24112 | 4000
8642 | 12 | 361 | 1 | 0 | 0 | 0.28027 | 4000
8643 | 12 | 361 | 2 | 0 | 0 | 0.29697 | 4000
8644 | 12 | 361 | 3 | 0 | 0 | 0.40456 | 4000
8645 | 12 | 361 | 4 | 0 | 0 | 0.22659 | 4000
8646 | 12 | 361 | 5 | 0 | 0 | 0.1898 | 4000
8647 | 12 | 361 | 6 | 0 | 0 | 0.25191 | 4000
8648 | 12 | 361 | 7 | 1 | 0.050948 | 0.32499 | 3800
8649 | 12 | 361 | 8 | 1 | 0.3573 | 0.44539 | 3600
8650 | 12 | 361 | 9 | 0 | 0.71778 | 0.39405 | 3600
8651 | 12 | 361 | 10 | 0 | 1 | 0.36091 | 3600
8652 | 12 | 361 | 11 | 0 | 1 | 0.32468 | 3600
8653 | 12 | 361 | 12 | 0 | 1 | 0.44458 | 3600
8654 | 12 | 361 | 13 | 0 | 1 | 0.43339 | 3600
8655 | 12 | 361 | 14 | 0 | 1 | 0.33848 | 3600
8656 | 12 | 361 | 15 | 0 | 0.71778 | 0.2452 | 3600
8657 | 12 | 361 | 16 | 0 | 0.3573 | 0.37716 | 3600
8658 | 12 | 361 | 17 | 0 | 0.050948 | 0.60783 | 3600
8659 | 12 | 361 | 18 | 0 | 0 | 0.46564 | 3600
8660 | 12 | 361 | 19 | 1 | 0 | 0.48796 | 3400
8661 | 12 | 361 | 20 | 1 | 0 | 0.40214 | 3200
8662 | 12 | 361 | 21 | 0 | 0 | 0.3513 | 3200
8663 | 12 | 361 | 22 | 0 | 0 | 0.25943 | 3200
8664 | 12 | 361 | 23 | 0 | 0 | 0.30845 | 3200
8665 | 12 | 362 | 0 | 0 | 0 | 0.19444 | 3200
8666 | 12 | 362 | 1 | 0 | 0 | 0.17387 | 3200
8667 | 12 | 362 | 2 | 0 | 0 | 0.18154 | 3200
8668 | 12 | 362 | 3 | 0 | 0 | 0.17173 | 3200
8669 | 12 | 362 | 4 | 0 | 0 | 0.18614 | 3200
8670 | 12 | 362 | 5 | 0 | 0 | 0.25829 | 3200
8671 | 12 | 362 | 6 | 0 | 0 | 0.40399 | 3200
8672 | 12 | 362 | 7 | 1 | 0.048409 | 0.51305 | 3000
8673 | 12 | 362 | 8 | 1 | 0.33949 | 0.45846 | 2800
8674 | 12 | 362 | 9 | 0 | 0.682 | 0.59146 | 2800
8675 | 12 | 362 | 10 | 0 | 0.98839 | 0.64711 | 2800
8676 | 12 | 362 | 11 | 0 | 1 | 0.35403 | 2800
8677 | 12 | 362 | 12 | 0 | 1 | 0.24984 | 2800
8678 | 12 | 362 | 13 | 0 | 1 | 0.14531 | 2800
8679 | 12 | 362 | 14 | 0 | 0.98839 | 0.17979 | 2800
8680 | 12 | 362 | 15 | 0 | 0.682 | 0.13472 | 2800
8681 | 12 | 362 | 16 | 0 | 0.33949 | 0.12603 | 2800
8682 | 12 | 362 | 17 | 0 | 0.048409 | 0.10127 | 2800
8683 | 12 | 362 | 18 | 0 | 0 | 0.088117 | 2800
8684 | 12 | 362 | 19 | 1 | 0 | 0.074527 | 2600
8685 | 12 | 362 | 20 | 1 | 0 | 0.09577 | 2400
8686 | 12 | 362 | 21 | 0 | 0 | 0.089516 | 2400
8687 | 12 | 362 | 22 | 0 | 0 | 0.11774 | 2400
8688 | 12 | 362 | 23 | 0 | 0 | 0.11252 | 2400
8689 | 12 | 363 | 0 | 0 | 0 | 0.11683 | 2400
8690 | 12 | 363 | 1 | 0 | 0 | 0.15321 | 2400
8691 | 12 | 363 | 2 | 0 | 0 | 0.20074 | 2400
8692 | 12 | 363 | 3 | 0 | 0 | 0.29053 | 2400
8693 | 12 | 363 | 4 | 0 | 0 | 0.21358 | 2400
8694 | 12 | 363 | 5 | 0 | 0 | 0.18831 | 2400
8695 | 12 | 363 | 6 | 0 | 0 | 0.13836 | 2400
8696 | 12 | 363 | 7 | 1 | 0.050409 | 0.1145 | 2200
8697 | 12 | 363 | 8 | 1 | 0.35352 | 0.11737 | 2000
8698 | 12 | 363 | 9 | 0 | 0.71018 | 0.15257 | 2000
8699 | 12 | 363 | 10 | 0 | 1 | 0.14379 | 2000
8700 | 12 | 363 | 11 | 0 | 1 | 0.15339 | 2000
8701 | 12 | 363 | 12 | 0 | 1 | 0.19476 | 2000
8702 | 12 | 363 | 13 | 0 | 1 | 0.24349 | 2000
8703 | 12 | 363 | 14 | 0 | 1 | 0.27309 | 2000
8704 | 12 | 363 | 15 | 0 | 0.71018 | 0.28055 | 2000
8705 | 12 | 363 | 16 | 0 | 0.35352 | 0.2246 | 2000
8706 | 12 | 363 | 17 | 0 | 0.050409 | 0.12801 | 2000
8707 | 12 | 363 | 18 | 0 | 0 | 0.19898 | 2000
8708 | 12 | 363 | 19 | 1 | 0 | 0.16925 | 1800
8709 | 12 | 363 | 20 | 1 | 0 | 0.24308 | 1600
8710 | 12 | 363 | 21 | 0 | 0 | 0.27155 | 1600
8711 | 12 | 363 | 22 | 0 | 0 | 0.24222 | 1600
8712 | 12 | 363 | 23 | 0 | 0 | 0.26469 | 1600
8713 | 12 | 364 | 0 | 0 | 0 | 0.23332 | 1600
8714 | 12 | 364 | 1 | 0 | 0 | 0.28435 | 1600
8715 | 12 | 364 | 2 | 0 | 0 | 0.33746 | 1600
8716 | 12 | 364 | 3 | 0 | 0 | 0.22421 | 1600
8717 | 12 | 364 | 4 | 0 | 0 | 0.22037 | 1600
8718 | 12 | 364 | 5 | 0 | 0 | 0.12846 | 1600
8719 | 12 | 364 | 6 | 0 | 0 | 0.086746 | 1600
8720 | 12 | 364 | 7 | 1 | 0.049427 | 0.098033 | 1400
8721 | 12 | 364 | 8 | 1 | 0.34663 | 0.15279 | 1200
8722 | 12 | 364 | 9 | 0 | 0.69635 | 0.15406 | 1200
8723 | 12 | 364 | 10 | 0 | 1 | 0.14887 | 1200
8724 | 12 | 364 | 11 | 0 | 1 | 0.20443 | 1200
8725 | 12 | 364 | 12 | 0 | 1 | 0.17883 | 1200
8726 | 12 | 364 | 13 | 0 | 1 | 0.25997 | 1200
8727 | 12 | 364 | 14 | 0 | 1 | 0.34544 | 1200
8728 | 12 | 364 | 15 | 0 | 0.69635 | 0.24843 | 1200
8729 | 12 | 364 | 16 | 0 | 0.34663 | 0.2235 | 1200
8730 | 12 | 364 | 17 | 0 | 0.049427 | 0.21833 | 1200
8731 | 12 | 364 | 18 | 0 | 0 | 0.21695 | 1200
8732 | 12 | 364 | 19 | 1 | 0 | 0.2398 | 1000
8733 | 12 | 364 | 20 | 1 | 0 | 0.16043 | 800
8734 | 12 | 364 | 21 | 0 | 0 | 0.19434 | 800
8735 | 12 | 364 | 22 | 0 | 0 | 0.12651 | 800
8736 | 12 | 364 | 23 | 0 | 0 | 0.10202 | 800
8737 | 12 | 365 | 0 | 0 | 0 | 0.15772 | 800
8738 | 12 | 365 | 1 | 0 | 0 | 0.15724 | 800
8739 | 12 | 365 | 2 | 0 | 0 | 0.16304 | 800
8740 | 12 | 365 | 3 | 0 | 0 | 0.13335 | 800
8741 | 12 | 365 | 4 | 0 | 0 | 0.10872 | 800
8742 | 12 | 365 | 5 | 0 | 0 | 0.077065 | 800
8743 | 12 | 365 | 6 | 0 | 0 | 0.12951 | 800
8744 | 12 | 365 | 7 | 1 | 0.048842 | 0.14157 | 600
8745 | 12 | 365 | 8 | 1 | 0.34253 | 0.178 | 400
8746 | 12 | 365 | 9 | 0 | 0.6881 | 0.14668 | 400
8747 | 12 | 365 | 10 | 0 | 0.99723 | 0.22571 | 400
8748 | 12 | 365 | 11 | 0 | 1 | 0.40257 | 400
8749 | 12 | 365 | 12 | 0 | 1 | 0.57929 | 400
8750 | 12 | 365 | 13 | 0 | 1 | 0.34419 | 400
8751 | 12 | 365 | 14 | 0 | 0.99723 | 0.38695 | 400
8752 | 12 | 365 | 15 | 0 | 0.6881 | 0.26571 | 400
8753 | 12 | 365 | 16 | 0 | 0.34253 | 0.29403 | 400
8754 | 12 | 365 | 17 | 0 | 0.048842 | 0.32129 | 400
8755 | 12 | 365 | 18 | 0 | 0 | 0.45891 | 400
8756 | 12 | 365 | 19 | 1 | 0 | 0.45656 | 200
8757 | 12 | 365 | 20 | 1 | 0 | 0.72592 | 0
8758 | 12 | 365 | 21 | 0 | 0 | 0.73267 | 0
8759 | 12 | 365 | 22 | 0 | 0 | 0.90682 | 0
8760 | 12 | 365 | 23 | 0 | 0 | 0.85764 | 0

## 25Y Hourly Validation
25-Year Exact Hourly Validation — engine full-term dispatch (8,760 h/yr, degradation + BESS ageing + year-11 augmentation)
Engine exact mode, measured-yield calibrated profiles, green support enabled (RfS 5% allowance). Values in cols C–J; checks are formulas.
Year | Usable BESS MWh | RTE | Solar deg factor | Wind deg factor | PPA MWh (project) | PPA CUF | CUF in band? | Min month avail (delivered) | Green MWh | Green % annual | Green <= 5%? | Avail incl. green | Avail >= 90%?
1 | 510.81 | 86.68% | 1 | 1 | 771408 | 44% | PASS | 82.41% | 4556.8 | 0.5907% | PASS | 90% | PASS
2 | 488.59 | 86.68% | 0.995 | 0.998 | 771408 | 44% | PASS | 79.6% | 7332.6 | 0.9505% | PASS | 90% | PASS
3 | 477.2 | 86.12% | 0.99003 | 0.996 | 771408 | 44% | PASS | 78.12% | 9176.1 | 1.19% | PASS | 90% | PASS
4 | 467.45 | 86.12% | 0.98507 | 0.99401 | 771408 | 44% | PASS | 76.84% | 10764.5 | 1.395% | PASS | 90% | PASS
5 | 458.71 | 86.12% | 0.98015 | 0.99202 | 771408 | 44% | PASS | 75.68% | 12476.7 | 1.617% | PASS | 90% | PASS
6 | 450.57 | 86.12% | 0.97525 | 0.99004 | 771408 | 44% | PASS | 74.6% | 14091.8 | 1.827% | PASS | 90% | PASS
7 | 443.03 | 85.57% | 0.97037 | 0.98806 | 771408 | 44% | PASS | 73.6% | 15703.1 | 2.036% | PASS | 90% | PASS
8 | 435.88 | 85.57% | 0.96552 | 0.98608 | 771408 | 44% | PASS | 72.64% | 17471.6 | 2.265% | PASS | 90% | PASS
9 | 429.08 | 85.57% | 0.96069 | 0.98411 | 771408 | 44% | PASS | 71.72% | 19328.6 | 2.506% | PASS | 90% | PASS
10 | 422.54 | 85.57% | 0.95589 | 0.98214 | 771408 | 44% | PASS | 70.84% | 21204.5 | 2.749% | PASS | 90% | PASS
11 | 510.81 | 86.68% | 0.95111 | 0.98018 | 771408 | 44% | PASS | 81.57% | 5611.8 | 0.7275% | PASS | 90% | PASS
12 | 488.59 | 86.68% | 0.94635 | 0.97822 | 771408 | 44% | PASS | 78.77% | 8680 | 1.125% | PASS | 90% | PASS
13 | 477.2 | 86.12% | 0.94162 | 0.97626 | 771408 | 44% | PASS | 77.29% | 10523.7 | 1.364% | PASS | 90% | PASS
14 | 467.45 | 86.12% | 0.93691 | 0.97431 | 771408 | 44% | PASS | 76.02% | 12390.7 | 1.606% | PASS | 90% | PASS
15 | 458.71 | 86.12% | 0.93223 | 0.97236 | 771408 | 44% | PASS | 74.86% | 14104.1 | 1.828% | PASS | 90% | PASS
16 | 450.57 | 86.12% | 0.92757 | 0.97042 | 771408 | 44% | PASS | 73.79% | 15909.1 | 2.062% | PASS | 90% | PASS
17 | 443.03 | 85.57% | 0.92293 | 0.96848 | 771408 | 44% | PASS | 72.78% | 17820.8 | 2.31% | PASS | 90% | PASS
18 | 435.88 | 85.57% | 0.91832 | 0.96654 | 771408 | 44% | PASS | 71.83% | 19748.1 | 2.56% | PASS | 90% | PASS
19 | 429.08 | 85.57% | 0.91372 | 0.96461 | 771408 | 44% | PASS | 70.91% | 21756.2 | 2.82% | PASS | 90% | PASS
20 | 422.54 | 85.57% | 0.90916 | 0.96268 | 771408 | 44% | PASS | 70.03% | 23762.5 | 3.08% | PASS | 90% | PASS
21 | 422.54 | 85.57% | 0.90461 | 0.96075 | 769463.4 | 43.89% | PASS | 69.92% | 24001.2 | 3.119% | PASS | 90% | PASS
22 | 422.54 | 85.57% | 0.90009 | 0.95883 | 767285.4 | 43.76% | PASS | 69.84% | 24230.4 | 3.158% | PASS | 90% | PASS
23 | 422.54 | 85.57% | 0.89559 | 0.95691 | 765110.8 | 43.64% | PASS | 69.77% | 24458.3 | 3.197% | PASS | 90% | PASS
24 | 422.54 | 85.57% | 0.89111 | 0.955 | 762938.7 | 43.52% | PASS | 69.69% | 24685.8 | 3.236% | PASS | 90% | PASS
25 | 422.54 | 85.57% | 0.88665 | 0.95309 | 760767.2 | 43.39% | PASS | 69.61% | 24915 | 3.275% | PASS | 90% | PASS
ALL YEARS | [6 empty] | PASS — CUF within +10%/-15% band, 25/25 years
PASS — availability >= 90%, 300/300 months
PASS — green support within 5% allowance
Reconciliation: the project physically delivers PPA energy at the +10% offtake cap (44% CUF) with peak availability held at the 90% floor via green
support (max 3.2% of annual vs 5% allowed). The Financial Model conservatively bills at the declared 40% CUF (offtake lever = 1.00); set the lever
to 1.10 to price full-cap offtake. Availability incl. green = engine result after allocating green to monthly peak shortfalls (fills exactly to floor).
Monthly peak availability delivered by the project (before green support) — engine hourly results
Year | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Min
1 | 82.41% | 88.86% | 97.12% | 98.21% | 98.87% | 99% | 98.71% | 97.96% | 95.31% | 92.83% | 86.55% | 83.58% | 82.41%
2 | 79.6% | 86.02% | 95.48% | 98.17% | 98.86% | 98.92% | 97.73% | 96.46% | 92.9% | 89.98% | 83.51% | 80.72% | 79.6%
3 | 78.12% | 84.51% | 94.19% | 98.05% | 98.86% | 98.65% | 96.76% | 95.25% | 91.39% | 88.46% | 81.89% | 79.22% | 78.12%
4 | 76.84% | 83.2% | 92.93% | 97.84% | 98.86% | 98.29% | 95.65% | 94.06% | 90.06% | 87.14% | 80.52% | 77.92% | 76.84%
5 | 75.68% | 82.02% | 91.76% | 97.53% | 98.85% | 97.81% | 94.62% | 92.91% | 88.86% | 85.95% | 79.32% | 76.72% | 75.68%
6 | 74.6% | 80.91% | 90.65% | 97.15% | 98.85% | 97.19% | 93.59% | 91.78% | 87.73% | 84.83% | 78.23% | 75.55% | 74.6%
7 | 73.6% | 79.87% | 89.59% | 96.64% | 98.82% | 96.58% | 92.56% | 90.72% | 86.68% | 83.78% | 77.21% | 74.46% | 73.6%
8 | 72.64% | 78.88% | 88.57% | 96% | 98.77% | 95.96% | 91.54% | 89.71% | 85.67% | 82.78% | 76.24% | 73.4% | 72.64%
9 | 71.72% | 77.94% | 87.59% | 95.2% | 98.65% | 95.29% | 90.57% | 88.75% | 84.72% | 81.83% | 75.31% | 72.39% | 71.72%
10 | 70.84% | 77.03% | 86.64% | 94.38% | 98.49% | 94.6% | 89.62% | 87.82% | 83.8% | 80.9% | 74.42% | 71.47% | 70.84%
11 | 81.57% | 87.73% | 96.42% | 98.18% | 98.83% | 98.95% | 98.26% | 97.32% | 94.3% | 91.6% | 85.14% | 82.56% | 81.57%
12 | 78.77% | 84.9% | 94.23% | 98.01% | 98.83% | 98.59% | 96.8% | 95.49% | 91.64% | 88.75% | 82.32% | 79.52% | 78.77%
13 | 77.29% | 83.39% | 92.81% | 97.72% | 98.83% | 98.14% | 95.6% | 94.14% | 90.12% | 87.24% | 80.83% | 77.87% | 77.29%
14 | 76.02% | 82.09% | 91.51% | 97.34% | 98.82% | 97.54% | 94.48% | 92.86% | 88.8% | 85.93% | 79.55% | 76.51% | 76.02%
15 | 74.86% | 80.91% | 90.33% | 96.86% | 98.81% | 96.88% | 93.38% | 91.66% | 87.62% | 84.74% | 78.39% | 75.28% | 74.86%
16 | 73.79% | 79.81% | 89.19% | 96.24% | 98.77% | 96.23% | 92.32% | 90.54% | 86.5% | 83.62% | 77.3% | 74.13% | 73.79%
17 | 72.78% | 78.77% | 88.12% | 95.49% | 98.66% | 95.49% | 91.28% | 89.49% | 85.45% | 82.58% | 76.28% | 72.99% | 72.78%
18 | 71.83% | 77.79% | 87.1% | 94.63% | 98.49% | 94.75% | 90.27% | 88.49% | 84.46% | 81.59% | 75.32% | 71.96% | 71.83%
19 | 70.91% | 76.85% | 86.13% | 93.78% | 98.31% | 94.01% | 89.33% | 87.54% | 83.5% | 80.64% | 74.39% | 70.98% | 70.91%
20 | 70.03% | 75.94% | 85.18% | 92.86% | 98.06% | 93.19% | 88.41% | 86.63% | 82.59% | 79.72% | 73.5% | 70.04% | 70.03%
21 | 69.92% | 75.84% | 85.04% | 92.7% | 98% | 93.04% | 88.29% | 86.52% | 82.47% | 79.61% | 73.42% | 69.97% | 69.92%
22 | 69.84% | 75.73% | 84.9% | 92.53% | 97.94% | 92.88% | 88.17% | 86.42% | 82.35% | 79.49% | 73.33% | 69.9% | 69.84%
23 | 69.77% | 75.63% | 84.76% | 92.37% | 97.88% | 92.72% | 88.06% | 86.32% | 82.23% | 79.38% | 73.24% | 69.82% | 69.77%
24 | 69.69% | 75.52% | 84.62% | 92.19% | 97.82% | 92.57% | 87.94% | 86.21% | 82.11% | 79.27% | 73.15% | 69.75% | 69.69%
25 | 69.61% | 75.42% | 84.48% | 92.02% | 97.75% | 92.42% | 87.81% | 86.11% | 81.99% | 79.15% | 73.06% | 69.68% | 69.61%

## Hourly Dispatch
HOURLY DISPATCH — formula-driven 8,760-hour dispatch for the SELECTED YEAR, with that year's degradation, BESS state-of-health (incl. year-11 augmentation reset) and RTE.
Single-aggregated-node replica of the engine dispatch (node interconnection limits not modelled per-hour); cross-checked against the engine below. Change B4 to any year 1-25.
SELECTED YEAR | 1 | [15 empty] | MONTHLY PEAK COMPLIANCE — selected year
Usable BESS (MWh) | 510.81 | [15 empty] | Month | Obligation MWh | Delivered MWh | Availability | Green to floor MWh | Avail incl. green | >=90%?
RTE (year) | 86.68% | [15 empty] | 1 | 24800 | 22819.2067 | 92.01% | 0 | 92.01% | PASS
Solar degradation factor | 1 | [15 empty] | 2 | 22400 | 21524.0608 | 96.09% | 0 | 96.09% | PASS
Wind degradation factor | 1 | [15 empty] | 3 | 24800 | 24357.772 | 98.22% | 0 | 98.22% | PASS
Opening SOC (50% usable) | 255.405 | [15 empty] | 4 | 24000 | 23569.9641 | 98.21% | 0 | 98.21% | PASS
Annual PPA cap (MWh, 110% x declared) | 771408 | [15 empty] | 5 | 24800 | 24519.3021 | 98.87% | 0 | 98.87% | PASS
[17 empty] | 6 | 24000 | 23760.5962 | 99% | 0 | 99% | PASS
[17 empty] | 7 | 24800 | 24603.1025 | 99.21% | 0 | 99.21% | PASS
Hour | Month | Peak | SolarCF | WindCF | RE MW | Peak target | RE→peak | BESS discharge | Peak delivered | BESS charge | Non-peak PPA | Rem peak obl | PPA total | Cum PPA | SOC | Surplus | 8 | 24800 | 24672.4781 | 99.49% | 0 | 99.49% | PASS
1 | 1 | 0 | 0 | 0.20912 | 8.5529 | 0 | 0 | 0 | 0 | 8.5529 | 0 | 292000 | 0 | 0 | 262.8186 | 0 | 9 | 24000 | 23700.3552 | 98.75% | 0 | 98.75% | PASS
2 | 1 | 0 | 0 | 0.25758 | 10.5351 | 0 | 0 | 0 | 0 | 10.5351 | 0 | 292000 | 0 | 0 | 271.9505 | 0 | 10 | 24800 | 24348.7238 | 98.18% | 0 | 98.18% | PASS
3 | 1 | 0 | 0 | 0.2741 | 11.2108 | 0 | 0 | 0 | 0 | 11.2108 | 0 | 292000 | 0 | 0 | 281.668 | 0 | 11 | 24000 | 22914.5153 | 95.48% | 0 | 95.48% | PASS
4 | 1 | 0 | 0 | 0.36883 | 15.0852 | 0 | 0 | 0 | 0 | 15.0852 | 0 | 292000 | 0 | 0 | 294.7438 | 0 | 12 | 24800 | 23046.0296 | 92.93% | 0 | 92.93% | PASS
5 | 1 | 0 | 0 | 0.29228 | 11.9541 | 0 | 0 | 0 | 0 | 11.9541 | 0 | 292000 | 0 | 0 | 305.1057 | 0 | YEAR | 292000 | 283836.1066 | 92.01% | 0 |  | ALL PASS
6 | 1 | 0 | 0 | 0.1936 | 7.9184 | 0 | 0 | 0 | 0 | 7.9184 | 0 | 292000 | 0 | 0 | 311.9694 | 0
7 | 1 | 0 | 0 | 0.15759 | 6.4455 | 0 | 0 | 0 | 0 | 6.4455 | 0 | 292000 | 0 | 0 | 317.5563 | 0
8 | 1 | 1 | 0.06852 | 0.20751 | 28.2757 | 200 | 28.2757 | 171.7243 | 200 | 0 | 0 | 291800 | 200 | 200 | 145.832 | 0 | ANNUAL RESULT & ENGINE CROSS-CHECK
9 | 1 | 1 | 0.3592 | 0.34747 | 117.949 | 200 | 117.949 | 82.051 | 200 | 0 | 0 | 291600 | 200 | 400 | 63.781 | 0 | Metric | This sheet | Engine (exact) | Delta %
10 | 1 | 0 | 0.69059 | 0.29144 | 211.3633 | 0 | 0 | 0 | 0 | 180 | 31.3633 | 291600 | 31.3633 | 431.3633 | 219.805 | 0 | PPA energy MWh (project, before green) | 771406.6734 | 771408 | -0.000172%
11 | 1 | 0 | 0.9839 | 0.30514 | 296.6302 | 0 | 0 | 0 | 0 | 180 | 116.6302 | 291600 | 116.6302 | 547.9935 | 375.829 | 0 | Annual PPA CUF | 44% | 44% | -0.000172%
12 | 1 | 0 | 1 | 0.30696 | 301.3547 | 0 | 0 | 0 | 0 | 155.7234 | 145.6314 | 291600 | 145.6314 | 693.6248 | 510.81 | 0 | Min monthly availability (delivered) | 92.01% | 82.41% | 11.65%
13 | 1 | 0 | 1 | 0.49278 | 308.9546 | 0 | 0 | 0 | 0 | 0 | 200 | 291600 | 200 | 893.6248 | 510.81 | 108.9546 | Green support needed (MWh) | 0 | 4556.8 | -100%
14 | 1 | 0 | 1 | 0.50808 | 309.5805 | 0 | 0 | 0 | 0 | 0 | 200 | 291600 | 200 | 1093.6248 | 510.81 | 109.5805
15 | 1 | 0 | 0.9839 | 0.48747 | 304.0874 | 0 | 0 | 0 | 0 | 0 | 200 | 291600 | 200 | 1293.6248 | 510.81 | 104.0874 | CUF band check (this sheet) | PASS
16 | 1 | 0 | 0.69059 | 0.42084 | 216.6557 | 0 | 0 | 0 | 0 | 0 | 200 | 291600 | 200 | 1493.6248 | 510.81 | 16.6557 | Deltas vs engine arise from single-node aggregation (engine enforces per-node interconnection limits, e.g. 30 MW at Fatehgarh wind).
17 | 1 | 0 | 0.3592 | 0.49704 | 124.0662 | 0 | 0 | 0 | 0 | 0 | 124.0662 | 291600 | 124.0662 | 1617.691 | 510.81 | 0
18 | 1 | 0 | 0.06852 | 0.33241 | 33.3839 | 0 | 0 | 0 | 0 | 0 | 33.3839 | 291600 | 33.3839 | 1651.075 | 510.81 | 0
19 | 1 | 0 | 0 | 0.2532 | 10.3557 | 0 | 0 | 0 | 0 | 0 | 10.3557 | 291600 | 10.3557 | 1661.4307 | 510.81 | 0
20 | 1 | 1 | 0 | 0.31906 | 13.0495 | 200 | 13.0495 | 180 | 193.0495 | 0 | 0 | 291400 | 193.0495 | 1854.4802 | 330.81 | 0
21 | 1 | 1 | 0 | 0.20144 | 8.2391 | 200 | 8.2391 | 180 | 188.2391 | 0 | 0 | 291200 | 188.2391 | 2042.7192 | 150.81 | 0
22 | 1 | 0 | 0 | 0.16257 | 6.6489 | 0 | 0 | 0 | 0 | 6.6489 | 0 | 291200 | 0 | 2042.7192 | 156.5733 | 0
23 | 1 | 0 | 0 | 0.092644 | 3.7891 | 0 | 0 | 0 | 0 | 3.7891 | 0 | 291200 | 0 | 2042.7192 | 159.8577 | 0
24 | 1 | 0 | 0 | 0.063263 | 2.5875 | 0 | 0 | 0 | 0 | 2.5875 | 0 | 291200 | 0 | 2042.7192 | 162.1005 | 0
25 | 1 | 0 | 0 | 0.073818 | 3.0192 | 0 | 0 | 0 | 0 | 3.0192 | 0 | 291200 | 0 | 2042.7192 | 164.7175 | 0
26 | 1 | 0 | 0 | 0.059784 | 2.4452 | 0 | 0 | 0 | 0 | 2.4452 | 0 | 291200 | 0 | 2042.7192 | 166.837 | 0
27 | 1 | 0 | 0 | 0.052314 | 2.1396 | 0 | 0 | 0 | 0 | 2.1396 | 0 | 291200 | 0 | 2042.7192 | 168.6917 | 0
28 | 1 | 0 | 0 | 0.053166 | 2.1745 | 0 | 0 | 0 | 0 | 2.1745 | 0 | 291200 | 0 | 2042.7192 | 170.5765 | 0
29 | 1 | 0 | 0 | 0.060345 | 2.4681 | 0 | 0 | 0 | 0 | 2.4681 | 0 | 291200 | 0 | 2042.7192 | 172.7159 | 0
30 | 1 | 0 | 0 | 0.062616 | 2.561 | 0 | 0 | 0 | 0 | 2.561 | 0 | 291200 | 0 | 2042.7192 | 174.9357 | 0
31 | 1 | 0 | 0 | 0.10278 | 4.2036 | 0 | 0 | 0 | 0 | 4.2036 | 0 | 291200 | 0 | 2042.7192 | 178.5794 | 0
32 | 1 | 1 | 0.063687 | 0.10952 | 22.8722 | 200 | 22.8722 | 177.1278 | 200 | 0 | 0 | 291000 | 200 | 2242.7192 | 1.4516 | 0
33 | 1 | 1 | 0.33386 | 0.077773 | 99.6008 | 200 | 99.6008 | 1.4516 | 101.0525 | 0 | 0 | 290800 | 101.0525 | 2343.7717 | 0 | 0
34 | 1 | 0 | 0.64188 | 0.049638 | 187.4054 | 0 | 0 | 0 | 0 | 180 | 7.4054 | 290800 | 7.4054 | 2351.1771 | 156.024 | 0
35 | 1 | 0 | 0.9145 | 0.076102 | 267.2193 | 0 | 0 | 0 | 0 | 180 | 87.2193 | 290800 | 87.2193 | 2438.3964 | 312.048 | 0
36 | 1 | 0 | 1 | 0.080285 | 292.0837 | 0 | 0 | 0 | 0 | 180 | 112.0837 | 290800 | 112.0837 | 2550.4801 | 468.072 | 0
37 | 1 | 0 | 1 | 0.10496 | 293.0929 | 0 | 0 | 0 | 0 | 49.3055 | 200 | 290800 | 200 | 2750.4801 | 510.81 | 43.7874
38 | 1 | 0 | 1 | 0.12122 | 293.7578 | 0 | 0 | 0 | 0 | 0 | 200 | 290800 | 200 | 2950.4801 | 510.81 | 93.7578
39 | 1 | 0 | 0.9145 | 0.11806 | 268.9356 | 0 | 0 | 0 | 0 | 0 | 200 | 290800 | 200 | 3150.4801 | 510.81 | 68.9356
40 | 1 | 0 | 0.64188 | 0.10212 | 189.5518 | 0 | 0 | 0 | 0 | 0 | 189.5518 | 290800 | 189.5518 | 3340.0319 | 510.81 | 0
41 | 1 | 0 | 0.33386 | 0.12391 | 101.4879 | 0 | 0 | 0 | 0 | 0 | 101.4879 | 290800 | 101.4879 | 3441.5198 | 510.81 | 0
42 | 1 | 0 | 0.063687 | 0.11653 | 23.1588 | 0 | 0 | 0 | 0 | 0 | 23.1588 | 290800 | 23.1588 | 3464.6786 | 510.81 | 0
43 | 1 | 0 | 0 | 0.14041 | 5.7427 | 0 | 0 | 0 | 0 | 0 | 5.7427 | 290800 | 5.7427 | 3470.4213 | 510.81 | 0
44 | 1 | 1 | 0 | 0.11957 | 4.8905 | 200 | 4.8905 | 180 | 184.8905 | 0 | 0 | 290600 | 184.8905 | 3655.3118 | 330.81 | 0
45 | 1 | 1 | 0 | 0.1327 | 5.4274 | 200 | 5.4274 | 180 | 185.4274 | 0 | 0 | 290400 | 185.4274 | 3840.7392 | 150.81 | 0
46 | 1 | 0 | 0 | 0.13877 | 5.6757 | 0 | 0 | 0 | 0 | 5.6757 | 0 | 290400 | 0 | 3840.7392 | 155.7297 | 0
47 | 1 | 0 | 0 | 0.12178 | 4.9807 | 0 | 0 | 0 | 0 | 4.9807 | 0 | 290400 | 0 | 3840.7392 | 160.047 | 0
48 | 1 | 0 | 0 | 0.098675 | 4.0358 | 0 | 0 | 0 | 0 | 4.0358 | 0 | 290400 | 0 | 3840.7392 | 163.5452 | 0
49 | 1 | 0 | 0 | 0.081514 | 3.3339 | 0 | 0 | 0 | 0 | 3.3339 | 0 | 290400 | 0 | 3840.7392 | 166.4351 | 0
50 | 1 | 0 | 0 | 0.08203 | 3.355 | 0 | 0 | 0 | 0 | 3.355 | 0 | 290400 | 0 | 3840.7392 | 169.3432 | 0
51 | 1 | 0 | 0 | 0.10307 | 4.2158 | 0 | 0 | 0 | 0 | 4.2158 | 0 | 290400 | 0 | 3840.7392 | 172.9974 | 0
52 | 1 | 0 | 0 | 0.081672 | 3.3404 | 0 | 0 | 0 | 0 | 3.3404 | 0 | 290400 | 0 | 3840.7392 | 175.8929 | 0
53 | 1 | 0 | 0 | 0.10234 | 4.1857 | 0 | 0 | 0 | 0 | 4.1857 | 0 | 290400 | 0 | 3840.7392 | 179.521 | 0
54 | 1 | 0 | 0 | 0.099462 | 4.068 | 0 | 0 | 0 | 0 | 4.068 | 0 | 290400 | 0 | 3840.7392 | 183.0472 | 0
55 | 1 | 0 | 0 | 0.092949 | 3.8016 | 0 | 0 | 0 | 0 | 3.8016 | 0 | 290400 | 0 | 3840.7392 | 186.3424 | 0
56 | 1 | 1 | 0.073744 | 0.15113 | 27.4786 | 200 | 27.4786 | 172.5214 | 200 | 0 | 0 | 290200 | 200 | 4040.7392 | 13.8211 | 0
57 | 1 | 1 | 0.38658 | 0.10248 | 115.837 | 200 | 115.837 | 13.8211 | 129.658 | 0 | 0 | 290000 | 129.658 | 4170.3973 | 0 | 0
58 | 1 | 0 | 0.74324 | 0.10133 | 218.7917 | 0 | 0 | 0 | 0 | 180 | 38.7917 | 290000 | 38.7917 | 4209.189 | 156.024 | 0
59 | 1 | 0 | 1 | 0.088836 | 292.4334 | 0 | 0 | 0 | 0 | 180 | 112.4334 | 290000 | 112.4334 | 4321.6223 | 312.048 | 0
60 | 1 | 0 | 1 | 0.13721 | 294.4117 | 0 | 0 | 0 | 0 | 180 | 114.4117 | 290000 | 114.4117 | 4436.0341 | 468.072 | 0
61 | 1 | 0 | 1 | 0.13067 | 294.1445 | 0 | 0 | 0 | 0 | 49.3055 | 200 | 290000 | 200 | 4636.0341 | 510.81 | 44.839
62 | 1 | 0 | 1 | 0.1828 | 296.2766 | 0 | 0 | 0 | 0 | 0 | 200 | 290000 | 200 | 4836.0341 | 510.81 | 96.2766
63 | 1 | 0 | 1 | 0.15624 | 295.19 | 0 | 0 | 0 | 0 | 0 | 200 | 290000 | 200 | 5036.0341 | 510.81 | 95.19
64 | 1 | 0 | 0.74324 | 0.10882 | 219.0982 | 0 | 0 | 0 | 0 | 0 | 200 | 290000 | 200 | 5236.0341 | 510.81 | 19.0982
65 | 1 | 0 | 0.38658 | 0.075816 | 114.7463 | 0 | 0 | 0 | 0 | 0 | 114.7463 | 290000 | 114.7463 | 5350.7804 | 510.81 | 0
66 | 1 | 0 | 0.073744 | 0.057936 | 23.6668 | 0 | 0 | 0 | 0 | 0 | 23.6668 | 290000 | 23.6668 | 5374.4473 | 510.81 | 0
67 | 1 | 0 | 0 | 0.055017 | 2.2502 | 0 | 0 | 0 | 0 | 0 | 2.2502 | 290000 | 2.2502 | 5376.6974 | 510.81 | 0
68 | 1 | 1 | 0 | 0.061255 | 2.5053 | 200 | 2.5053 | 180 | 182.5053 | 0 | 0 | 289800 | 182.5053 | 5559.2028 | 330.81 | 0
69 | 1 | 1 | 0 | 0.07735 | 3.1636 | 200 | 3.1636 | 180 | 183.1636 | 0 | 0 | 289600 | 183.1636 | 5742.3664 | 150.81 | 0
70 | 1 | 0 | 0 | 0.064554 | 2.6403 | 0 | 0 | 0 | 0 | 2.6403 | 0 | 289600 | 0 | 5742.3664 | 153.0986 | 0
71 | 1 | 0 | 0 | 0.054754 | 2.2394 | 0 | 0 | 0 | 0 | 2.2394 | 0 | 289600 | 0 | 5742.3664 | 155.0397 | 0
72 | 1 | 0 | 0 | 0.058559 | 2.3951 | 0 | 0 | 0 | 0 | 2.3951 | 0 | 289600 | 0 | 5742.3664 | 157.1158 | 0
73 | 1 | 0 | 0 | 0.085639 | 3.5026 | 0 | 0 | 0 | 0 | 3.5026 | 0 | 289600 | 0 | 5742.3664 | 160.1518 | 0
74 | 1 | 0 | 0 | 0.069102 | 2.8263 | 0 | 0 | 0 | 0 | 2.8263 | 0 | 289600 | 0 | 5742.3664 | 162.6017 | 0
75 | 1 | 0 | 0 | 0.13126 | 5.3685 | 0 | 0 | 0 | 0 | 5.3685 | 0 | 289600 | 0 | 5742.3664 | 167.255 | 0
76 | 1 | 0 | 0 | 0.16451 | 6.7284 | 0 | 0 | 0 | 0 | 6.7284 | 0 | 289600 | 0 | 5742.3664 | 173.0872 | 0
77 | 1 | 0 | 0 | 0.14173 | 5.7968 | 0 | 0 | 0 | 0 | 5.7968 | 0 | 289600 | 0 | 5742.3664 | 178.1119 | 0
78 | 1 | 0 | 0 | 0.097928 | 4.0053 | 0 | 0 | 0 | 0 | 4.0053 | 0 | 289600 | 0 | 5742.3664 | 181.5836 | 0
79 | 1 | 0 | 0 | 0.10806 | 4.4198 | 0 | 0 | 0 | 0 | 4.4198 | 0 | 289600 | 0 | 5742.3664 | 185.4147 | 0
80 | 1 | 1 | 0.060581 | 0.1318 | 22.8863 | 200 | 22.8863 | 177.1137 | 200 | 0 | 0 | 289400 | 200 | 5942.3664 | 8.301 | 0
81 | 1 | 1 | 0.31758 | 0.11686 | 96.4966 | 200 | 96.4966 | 8.301 | 104.7975 | 0 | 0 | 289200 | 104.7975 | 6047.1639 | 0 | 0
82 | 1 | 0 | 0.61057 | 0.10551 | 180.6483 | 0 | 0 | 0 | 0 | 180 | 0.6483 | 289200 | 0.6483 | 6047.8122 | 156.024 | 0
83 | 1 | 0 | 0.86989 | 0.11338 | 255.8614 | 0 | 0 | 0 | 0 | 180 | 75.8614 | 289200 | 75.8614 | 6123.6736 | 312.048 | 0
84 | 1 | 0 | 1 | 0.1277 | 294.0229 | 0 | 0 | 0 | 0 | 180 | 114.0229 | 289200 | 114.0229 | 6237.6965 | 468.072 | 0
85 | 1 | 0 | 1 | 0.15649 | 295.2006 | 0 | 0 | 0 | 0 | 49.3055 | 200 | 289200 | 200 | 6437.6965 | 510.81 | 45.8951
86 | 1 | 0 | 1 | 0.14027 | 294.5372 | 0 | 0 | 0 | 0 | 0 | 200 | 289200 | 200 | 6637.6965 | 510.81 | 94.5372
87 | 1 | 0 | 0.86989 | 0.12754 | 256.4405 | 0 | 0 | 0 | 0 | 0 | 200 | 289200 | 200 | 6837.6965 | 510.81 | 56.4405
88 | 1 | 0 | 0.61057 | 0.11178 | 180.9046 | 0 | 0 | 0 | 0 | 0 | 180.9046 | 289200 | 180.9046 | 7018.6011 | 510.81 | 0
89 | 1 | 0 | 0.31758 | 0.16136 | 98.3164 | 0 | 0 | 0 | 0 | 0 | 98.3164 | 289200 | 98.3164 | 7116.9175 | 510.81 | 0
90 | 1 | 0 | 0.060581 | 0.1453 | 23.4386 | 0 | 0 | 0 | 0 | 0 | 23.4386 | 289200 | 23.4386 | 7140.3561 | 510.81 | 0
91 | 1 | 0 | 0 | 0.15119 | 6.1837 | 0 | 0 | 0 | 0 | 0 | 6.1837 | 289200 | 6.1837 | 7146.5398 | 510.81 | 0
92 | 1 | 1 | 0 | 0.14401 | 5.8899 | 200 | 5.8899 | 180 | 185.8899 | 0 | 0 | 289000 | 185.8899 | 7332.4296 | 330.81 | 0
93 | 1 | 1 | 0 | 0.17249 | 7.0549 | 200 | 7.0549 | 180 | 187.0549 | 0 | 0 | 288800 | 187.0549 | 7519.4845 | 150.81 | 0
94 | 1 | 0 | 0 | 0.17181 | 7.0272 | 0 | 0 | 0 | 0 | 7.0272 | 0 | 288800 | 0 | 7519.4845 | 156.9012 | 0
95 | 1 | 0 | 0 | 0.14578 | 5.9624 | 0 | 0 | 0 | 0 | 5.9624 | 0 | 288800 | 0 | 7519.4845 | 162.0695 | 0
96 | 1 | 0 | 0 | 0.15439 | 6.3145 | 0 | 0 | 0 | 0 | 6.3145 | 0 | 288800 | 0 | 7519.4845 | 167.5428 | 0
97 | 1 | 0 | 0 | 0.16487 | 6.7432 | 0 | 0 | 0 | 0 | 6.7432 | 0 | 288800 | 0 | 7519.4845 | 173.3878 | 0
98 | 1 | 0 | 0 | 0.31706 | 12.9676 | 0 | 0 | 0 | 0 | 12.9676 | 0 | 288800 | 0 | 7519.4845 | 184.6281 | 0
99 | 1 | 0 | 0 | 0.23361 | 9.5546 | 0 | 0 | 0 | 0 | 9.5546 | 0 | 288800 | 0 | 7519.4845 | 192.91 | 0
100 | 1 | 0 | 0 | 0.26 | 10.6338 | 0 | 0 | 0 | 0 | 10.6338 | 0 | 288800 | 0 | 7519.4845 | 202.1274 | 0
101 | 1 | 0 | 0 | 0.22125 | 9.0491 | 0 | 0 | 0 | 0 | 9.0491 | 0 | 288800 | 0 | 7519.4845 | 209.9712 | 0
102 | 1 | 0 | 0 | 0.25858 | 10.5761 | 0 | 0 | 0 | 0 | 10.5761 | 0 | 288800 | 0 | 7519.4845 | 219.1385 | 0
103 | 1 | 0 | 0 | 0.35301 | 14.4379 | 0 | 0 | 0 | 0 | 14.4379 | 0 | 288800 | 0 | 7519.4845 | 231.6533 | 0
104 | 1 | 1 | 0.068012 | 0.43665 | 37.501 | 200 | 37.501 | 162.499 | 200 | 0 | 0 | 288600 | 200 | 7719.4845 | 69.1543 | 0
105 | 1 | 1 | 0.35654 | 0.5624 | 125.9706 | 200 | 125.9706 | 69.1543 | 195.1249 | 0 | 0 | 288400 | 195.1249 | 7914.6094 | 0 | 0
106 | 1 | 0 | 0.68547 | 0.55143 | 220.5185 | 0 | 0 | 0 | 0 | 180 | 40.5185 | 288400 | 40.5185 | 7955.1279 | 156.024 | 0
107 | 1 | 0 | 0.97661 | 0.52821 | 303.6478 | 0 | 0 | 0 | 0 | 180 | 123.6478 | 288400 | 123.6478 | 8078.7757 | 312.048 | 0
108 | 1 | 0 | 1 | 0.32378 | 302.0427 | 0 | 0 | 0 | 0 | 180 | 122.0427 | 288400 | 122.0427 | 8200.8184 | 468.072 | 0
109 | 1 | 0 | 1 | 0.34473 | 302.8993 | 0 | 0 | 0 | 0 | 49.3055 | 200 | 288400 | 200 | 8400.8184 | 510.81 | 53.5938
110 | 1 | 0 | 1 | 0.3692 | 303.9001 | 0 | 0 | 0 | 0 | 0 | 200 | 288400 | 200 | 8600.8184 | 510.81 | 103.9001
111 | 1 | 0 | 0.97661 | 0.40466 | 298.5949 | 0 | 0 | 0 | 0 | 0 | 200 | 288400 | 200 | 8800.8184 | 510.81 | 98.5949
112 | 1 | 0 | 0.68547 | 0.42448 | 215.3263 | 0 | 0 | 0 | 0 | 0 | 200 | 288400 | 200 | 9000.8184 | 510.81 | 15.3263
113 | 1 | 0 | 0.35654 | 0.7223 | 132.5105 | 0 | 0 | 0 | 0 | 0 | 132.5105 | 288400 | 132.5105 | 9133.3289 | 510.81 | 0
114 | 1 | 0 | 0.068012 | 0.51668 | 40.7741 | 0 | 0 | 0 | 0 | 0 | 40.7741 | 288400 | 40.7741 | 9174.103 | 510.81 | 0
115 | 1 | 0 | 0 | 0.39184 | 16.0262 | 0 | 0 | 0 | 0 | 0 | 16.0262 | 288400 | 16.0262 | 9190.1292 | 510.81 | 0
116 | 1 | 1 | 0 | 0.28721 | 11.747 | 200 | 11.747 | 180 | 191.747 | 0 | 0 | 288200 | 191.747 | 9381.8762 | 330.81 | 0
117 | 1 | 1 | 0 | 0.48003 | 19.6333 | 200 | 19.6333 | 180 | 199.6333 | 0 | 0 | 288000 | 199.6333 | 9581.5095 | 150.81 | 0
118 | 1 | 0 | 0 | 0.51072 | 20.8886 | 0 | 0 | 0 | 0 | 20.8886 | 0 | 288000 | 0 | 9581.5095 | 168.9162 | 0
119 | 1 | 0 | 0 | 0.40887 | 16.7227 | 0 | 0 | 0 | 0 | 16.7227 | 0 | 288000 | 0 | 9581.5095 | 183.4115 | 0
120 | 1 | 0 | 0 | 0.35703 | 14.6025 | 0 | 0 | 0 | 0 | 14.6025 | 0 | 288000 | 0 | 9581.5095 | 196.0689 | 0
121 | 1 | 0 | 0 | 0.36582 | 14.9621 | 0 | 0 | 0 | 0 | 14.9621 | 0 | 288000 | 0 | 9581.5095 | 209.0381 | 0
122 | 1 | 0 | 0 | 0.36 | 14.7238 | 0 | 0 | 0 | 0 | 14.7238 | 0 | 288000 | 0 | 9581.5095 | 221.8006 | 0
123 | 1 | 0 | 0 | 0.34817 | 14.2399 | 0 | 0 | 0 | 0 | 14.2399 | 0 | 288000 | 0 | 9581.5095 | 234.1438 | 0
124 | 1 | 0 | 0 | 0.3159 | 12.9202 | 0 | 0 | 0 | 0 | 12.9202 | 0 | 288000 | 0 | 9581.5095 | 245.343 | 0
125 | 1 | 0 | 0 | 0.32531 | 13.3051 | 0 | 0 | 0 | 0 | 13.3051 | 0 | 288000 | 0 | 9581.5095 | 256.8759 | 0
126 | 1 | 0 | 0 | 0.28956 | 11.843 | 0 | 0 | 0 | 0 | 11.843 | 0 | 288000 | 0 | 9581.5095 | 267.1414 | 0
127 | 1 | 0 | 0 | 0.36933 | 15.1058 | 0 | 0 | 0 | 0 | 15.1058 | 0 | 288000 | 0 | 9581.5095 | 280.2351 | 0
128 | 1 | 1 | 0.070155 | 0.54188 | 42.4237 | 200 | 42.4237 | 157.5763 | 200 | 0 | 0 | 287800 | 200 | 9781.5095 | 122.6588 | 0
129 | 1 | 1 | 0.36777 | 0.37265 | 121.4542 | 200 | 121.4542 | 78.5458 | 200 | 0 | 0 | 287600 | 200 | 9981.5095 | 44.1131 | 0
130 | 1 | 0 | 0.70707 | 0.24128 | 214.0715 | 0 | 0 | 0 | 0 | 180 | 34.0715 | 287600 | 34.0715 | 10015.5811 | 200.1371 | 0
131 | 1 | 0 | 1 | 0.16837 | 295.6864 | 0 | 0 | 0 | 0 | 180 | 115.6864 | 287600 | 115.6864 | 10131.2675 | 356.1611 | 0
132 | 1 | 0 | 1 | 0.18144 | 296.2209 | 0 | 0 | 0 | 0 | 178.4136 | 117.8073 | 287600 | 117.8073 | 10249.0748 | 510.81 | 0
133 | 1 | 0 | 1 | 0.23378 | 298.3614 | 0 | 0 | 0 | 0 | 0 | 200 | 287600 | 200 | 10449.0748 | 510.81 | 98.3614
134 | 1 | 0 | 1 | 0.35331 | 303.2503 | 0 | 0 | 0 | 0 | 0 | 200 | 287600 | 200 | 10649.0748 | 510.81 | 103.2503
135 | 1 | 0 | 1 | 0.164 | 295.5075 | 0 | 0 | 0 | 0 | 0 | 200 | 287600 | 200 | 10849.0748 | 510.81 | 95.5075
136 | 1 | 0 | 0.70707 | 0.1124 | 208.8 | 0 | 0 | 0 | 0 | 0 | 200 | 287600 | 200 | 11049.0748 | 510.81 | 8.8
137 | 1 | 0 | 0.36777 | 0.11934 | 111.0939 | 0 | 0 | 0 | 0 | 0 | 111.0939 | 287600 | 111.0939 | 11160.1687 | 510.81 | 0
138 | 1 | 0 | 0.070155 | 0.10483 | 24.5481 | 0 | 0 | 0 | 0 | 0 | 24.5481 | 287600 | 24.5481 | 11184.7168 | 510.81 | 0
139 | 1 | 0 | 0 | 0.13971 | 5.7141 | 0 | 0 | 0 | 0 | 0 | 5.7141 | 287600 | 5.7141 | 11190.4309 | 510.81 | 0
140 | 1 | 1 | 0 | 0.12531 | 5.1252 | 200 | 5.1252 | 180 | 185.1252 | 0 | 0 | 287400 | 185.1252 | 11375.5561 | 330.81 | 0
141 | 1 | 1 | 0 | 0.19037 | 7.7861 | 200 | 7.7861 | 180 | 187.7861 | 0 | 0 | 287200 | 187.7861 | 11563.3422 | 150.81 | 0
142 | 1 | 0 | 0 | 0.17192 | 7.0317 | 0 | 0 | 0 | 0 | 7.0317 | 0 | 287200 | 0 | 11563.3422 | 156.9051 | 0
143 | 1 | 0 | 0 | 0.1525 | 6.2371 | 0 | 0 | 0 | 0 | 6.2371 | 0 | 287200 | 0 | 11563.3422 | 162.3114 | 0
144 | 1 | 0 | 0 | 0.08038 | 3.2875 | 0 | 0 | 0 | 0 | 3.2875 | 0 | 287200 | 0 | 11563.3422 | 165.161 | 0
145 | 1 | 0 | 0 | 0.15282 | 6.2504 | 0 | 0 | 0 | 0 | 6.2504 | 0 | 287200 | 0 | 11563.3422 | 170.5788 | 0
146 | 1 | 0 | 0 | 0.14298 | 5.8479 | 0 | 0 | 0 | 0 | 5.8479 | 0 | 287200 | 0 | 11563.3422 | 175.6478 | 0
147 | 1 | 0 | 0 | 0.13876 | 5.6752 | 0 | 0 | 0 | 0 | 5.6752 | 0 | 287200 | 0 | 11563.3422 | 180.5671 | 0
148 | 1 | 0 | 0 | 0.12431 | 5.0844 | 0 | 0 | 0 | 0 | 5.0844 | 0 | 287200 | 0 | 11563.3422 | 184.9743 | 0
149 | 1 | 0 | 0 | 0.14117 | 5.7736 | 0 | 0 | 0 | 0 | 5.7736 | 0 | 287200 | 0 | 11563.3422 | 189.9788 | 0
150 | 1 | 0 | 0 | 0.17033 | 6.9666 | 0 | 0 | 0 | 0 | 6.9666 | 0 | 287200 | 0 | 11563.3422 | 196.0175 | 0
151 | 1 | 0 | 0 | 0.18613 | 7.6125 | 0 | 0 | 0 | 0 | 7.6125 | 0 | 287200 | 0 | 11563.3422 | 202.616 | 0
152 | 1 | 1 | 0.070027 | 0.20562 | 28.6335 | 200 | 28.6335 | 171.3665 | 200 | 0 | 0 | 287000 | 200 | 11763.3422 | 31.2495 | 0
153 | 1 | 1 | 0.3671 | 0.18722 | 113.6757 | 200 | 113.6757 | 31.2495 | 144.9253 | 0 | 0 | 286800 | 144.9253 | 11908.2675 | 0 | 0
154 | 1 | 0 | 0.70578 | 0.25102 | 214.0961 | 0 | 0 | 0 | 0 | 180 | 34.0961 | 286800 | 34.0961 | 11942.3636 | 156.024 | 0
155 | 1 | 0 | 1 | 0.18001 | 296.1624 | 0 | 0 | 0 | 0 | 180 | 116.1624 | 286800 | 116.1624 | 12058.526 | 312.048 | 0
156 | 1 | 0 | 1 | 0.29399 | 300.8242 | 0 | 0 | 0 | 0 | 180 | 120.8242 | 286800 | 120.8242 | 12179.3502 | 468.072 | 0
157 | 1 | 0 | 1 | 0.35726 | 303.4119 | 0 | 0 | 0 | 0 | 49.3055 | 200 | 286800 | 200 | 12379.3502 | 510.81 | 54.1064
158 | 1 | 0 | 1 | 0.43879 | 306.7465 | 0 | 0 | 0 | 0 | 0 | 200 | 286800 | 200 | 12579.3502 | 510.81 | 106.7465
159 | 1 | 0 | 1 | 0.74728 | 319.364 | 0 | 0 | 0 | 0 | 0 | 200 | 286800 | 200 | 12779.3502 | 510.81 | 119.364
160 | 1 | 0 | 0.70578 | 0.46832 | 222.9836 | 0 | 0 | 0 | 0 | 0 | 200 | 286800 | 200 | 12979.3502 | 510.81 | 22.9836
161 | 1 | 0 | 0.3671 | 0.38363 | 121.7089 | 0 | 0 | 0 | 0 | 0 | 121.7089 | 286800 | 121.7089 | 13101.0591 | 510.81 | 0
162 | 1 | 0 | 0.070027 | 0.29725 | 32.3813 | 0 | 0 | 0 | 0 | 0 | 32.3813 | 286800 | 32.3813 | 13133.4404 | 510.81 | 0
163 | 1 | 0 | 0 | 0.30254 | 12.3738 | 0 | 0 | 0 | 0 | 0 | 12.3738 | 286800 | 12.3738 | 13145.8142 | 510.81 | 0
164 | 1 | 1 | 0 | 0.22073 | 9.0279 | 200 | 9.0279 | 180 | 189.0279 | 0 | 0 | 286600 | 189.0279 | 13334.842 | 330.81 | 0
165 | 1 | 1 | 0 | 0.18366 | 7.5119 | 200 | 7.5119 | 180 | 187.5119 | 0 | 0 | 286400 | 187.5119 | 13522.3539 | 150.81 | 0
166 | 1 | 0 | 0 | 0.11926 | 4.8779 | 0 | 0 | 0 | 0 | 4.8779 | 0 | 286400 | 0 | 13522.3539 | 155.0381 | 0
167 | 1 | 0 | 0 | 0.13641 | 5.579 | 0 | 0 | 0 | 0 | 5.579 | 0 | 286400 | 0 | 13522.3539 | 159.874 | 0
168 | 1 | 0 | 0 | 0.077229 | 3.1587 | 0 | 0 | 0 | 0 | 3.1587 | 0 | 286400 | 0 | 13522.3539 | 162.6119 | 0
169 | 1 | 0 | 0 | 0.079571 | 3.2545 | 0 | 0 | 0 | 0 | 3.2545 | 0 | 286400 | 0 | 13522.3539 | 165.4329 | 0
170 | 1 | 0 | 0 | 0.094036 | 3.8461 | 0 | 0 | 0 | 0 | 3.8461 | 0 | 286400 | 0 | 13522.3539 | 168.7667 | 0
171 | 1 | 0 | 0 | 0.18655 | 7.63 | 0 | 0 | 0 | 0 | 7.63 | 0 | 286400 | 0 | 13522.3539 | 175.3804 | 0
172 | 1 | 0 | 0 | 0.17437 | 7.1316 | 0 | 0 | 0 | 0 | 7.1316 | 0 | 286400 | 0 | 13522.3539 | 181.5621 | 0
173 | 1 | 0 | 0 | 0.1837 | 7.5132 | 0 | 0 | 0 | 0 | 7.5132 | 0 | 286400 | 0 | 13522.3539 | 188.0745 | 0
174 | 1 | 0 | 0 | 0.16262 | 6.6512 | 0 | 0 | 0 | 0 | 6.6512 | 0 | 286400 | 0 | 13522.3539 | 193.8397 | 0
175 | 1 | 0 | 0 | 0.18756 | 7.6712 | 0 | 0 | 0 | 0 | 7.6712 | 0 | 286400 | 0 | 13522.3539 | 200.4892 | 0
176 | 1 | 1 | 0.074872 | 0.1349 | 27.1406 | 200 | 27.1406 | 172.8594 | 200 | 0 | 0 | 286200 | 200 | 13722.3539 | 27.6298 | 0
177 | 1 | 1 | 0.3925 | 0.15883 | 119.8499 | 200 | 119.8499 | 27.6298 | 147.4797 | 0 | 0 | 286000 | 147.4797 | 13869.8336 | 0 | 0
178 | 1 | 0 | 0.75461 | 0.19381 | 225.8584 | 0 | 0 | 0 | 0 | 180 | 45.8584 | 286000 | 45.8584 | 13915.692 | 156.024 | 0
179 | 1 | 0 | 1 | 0.20247 | 297.0809 | 0 | 0 | 0 | 0 | 180 | 117.0809 | 286000 | 117.0809 | 14032.773 | 312.048 | 0
180 | 1 | 0 | 1 | 0.18782 | 296.4819 | 0 | 0 | 0 | 0 | 180 | 116.4819 | 286000 | 116.4819 | 14149.2549 | 468.072 | 0
181 | 1 | 0 | 1 | 0.17899 | 296.1206 | 0 | 0 | 0 | 0 | 49.3055 | 200 | 286000 | 200 | 14349.2549 | 510.81 | 46.8151
182 | 1 | 0 | 1 | 0.14974 | 294.9243 | 0 | 0 | 0 | 0 | 0 | 200 | 286000 | 200 | 14549.2549 | 510.81 | 94.9243
183 | 1 | 0 | 1 | 0.15885 | 295.2969 | 0 | 0 | 0 | 0 | 0 | 200 | 286000 | 200 | 14749.2549 | 510.81 | 95.2969
184 | 1 | 0 | 0.75461 | 0.13814 | 223.5817 | 0 | 0 | 0 | 0 | 0 | 200 | 286000 | 200 | 14949.2549 | 510.81 | 23.5817
185 | 1 | 0 | 0.3925 | 0.136 | 118.916 | 0 | 0 | 0 | 0 | 0 | 118.916 | 286000 | 118.916 | 15068.1709 | 510.81 | 0
186 | 1 | 0 | 0.074872 | 0.17307 | 28.7017 | 0 | 0 | 0 | 0 | 0 | 28.7017 | 286000 | 28.7017 | 15096.8726 | 510.81 | 0
187 | 1 | 0 | 0 | 0.1634 | 6.6833 | 0 | 0 | 0 | 0 | 0 | 6.6833 | 286000 | 6.6833 | 15103.5558 | 510.81 | 0
188 | 1 | 1 | 0 | 0.22064 | 9.0241 | 200 | 9.0241 | 180 | 189.0241 | 0 | 0 | 285800 | 189.0241 | 15292.58 | 330.81 | 0
189 | 1 | 1 | 0 | 0.22491 | 9.1987 | 200 | 9.1987 | 180 | 189.1987 | 0 | 0 | 285600 | 189.1987 | 15481.7787 | 150.81 | 0
190 | 1 | 0 | 0 | 0.1726 | 7.0593 | 0 | 0 | 0 | 0 | 7.0593 | 0 | 285600 | 0 | 15481.7787 | 156.929 | 0
191 | 1 | 0 | 0 | 0.21505 | 8.7957 | 0 | 0 | 0 | 0 | 8.7957 | 0 | 285600 | 0 | 15481.7787 | 164.5531 | 0
192 | 1 | 0 | 0 | 0.20361 | 8.3278 | 0 | 0 | 0 | 0 | 8.3278 | 0 | 285600 | 0 | 15481.7787 | 171.7716 | 0
193 | 1 | 0 | 0 | 0.20289 | 8.2982 | 0 | 0 | 0 | 0 | 8.2982 | 0 | 285600 | 0 | 15481.7787 | 178.9645 | 0
194 | 1 | 0 | 0 | 0.30118 | 12.3183 | 0 | 0 | 0 | 0 | 12.3183 | 0 | 285600 | 0 | 15481.7787 | 189.6421 | 0
195 | 1 | 0 | 0 | 0.27349 | 11.1858 | 0 | 0 | 0 | 0 | 11.1858 | 0 | 285600 | 0 | 15481.7787 | 199.3379 | 0
196 | 1 | 0 | 0 | 0.25787 | 10.5468 | 0 | 0 | 0 | 0 | 10.5468 | 0 | 285600 | 0 | 15481.7787 | 208.4799 | 0
197 | 1 | 0 | 0 | 0.26526 | 10.8493 | 0 | 0 | 0 | 0 | 10.8493 | 0 | 285600 | 0 | 15481.7787 | 217.8841 | 0
198 | 1 | 0 | 0 | 0.28565 | 11.683 | 0 | 0 | 0 | 0 | 11.683 | 0 | 285600 | 0 | 15481.7787 | 228.011 | 0
199 | 1 | 0 | 0 | 0.20209 | 8.2654 | 0 | 0 | 0 | 0 | 8.2654 | 0 | 285600 | 0 | 15481.7787 | 235.1754 | 0
200 | 1 | 1 | 0.077571 | 0.22433 | 31.5777 | 200 | 31.5777 | 168.4223 | 200 | 0 | 0 | 285400 | 200 | 15681.7787 | 66.7531 | 0
201 | 1 | 1 | 0.40665 | 0.12948 | 122.7359 | 200 | 122.7359 | 66.7531 | 189.489 | 0 | 0 | 285200 | 189.489 | 15871.2677 | 0 | 0
202 | 1 | 0 | 0.78182 | 0.12031 | 230.7088 | 0 | 0 | 0 | 0 | 180 | 50.7088 | 285200 | 50.7088 | 15921.9765 | 156.024 | 0
203 | 1 | 0 | 1 | 0.14123 | 294.5763 | 0 | 0 | 0 | 0 | 180 | 114.5763 | 285200 | 114.5763 | 16036.5527 | 312.048 | 0
204 | 1 | 0 | 1 | 0.13556 | 294.3444 | 0 | 0 | 0 | 0 | 180 | 114.3444 | 285200 | 114.3444 | 16150.8971 | 468.072 | 0
205 | 1 | 0 | 1 | 0.10484 | 293.0881 | 0 | 0 | 0 | 0 | 49.3055 | 200 | 285200 | 200 | 16350.8971 | 510.81 | 43.7826
206 | 1 | 0 | 1 | 0.11274 | 293.4112 | 0 | 0 | 0 | 0 | 0 | 200 | 285200 | 200 | 16550.8971 | 510.81 | 93.4112
207 | 1 | 0 | 1 | 0.12424 | 293.8814 | 0 | 0 | 0 | 0 | 0 | 200 | 285200 | 200 | 16750.8971 | 510.81 | 93.8814
208 | 1 | 0 | 0.78182 | 0.14552 | 231.74 | 0 | 0 | 0 | 0 | 0 | 200 | 285200 | 200 | 16950.8971 | 510.81 | 31.74
209 | 1 | 0 | 0.40665 | 0.11869 | 122.2945 | 0 | 0 | 0 | 0 | 0 | 122.2945 | 285200 | 122.2945 | 17073.1916 | 510.81 | 0
210 | 1 | 0 | 0.077571 | 0.12423 | 27.4835 | 0 | 0 | 0 | 0 | 0 | 27.4835 | 285200 | 27.4835 | 17100.6751 | 510.81 | 0
211 | 1 | 0 | 0 | 0.13035 | 5.3312 | 0 | 0 | 0 | 0 | 0 | 5.3312 | 285200 | 5.3312 | 17106.0062 | 510.81 | 0
212 | 1 | 1 | 0 | 0.11569 | 4.7318 | 200 | 4.7318 | 180 | 184.7318 | 0 | 0 | 285000 | 184.7318 | 17290.738 | 330.81 | 0
213 | 1 | 1 | 0 | 0.14288 | 5.8436 | 200 | 5.8436 | 180 | 185.8436 | 0 | 0 | 284800 | 185.8436 | 17476.5816 | 150.81 | 0
214 | 1 | 0 | 0 | 0.10556 | 4.3172 | 0 | 0 | 0 | 0 | 4.3172 | 0 | 284800 | 0 | 17476.5816 | 154.5522 | 0
215 | 1 | 0 | 0 | 0.11871 | 4.8551 | 0 | 0 | 0 | 0 | 4.8551 | 0 | 284800 | 0 | 17476.5816 | 158.7606 | 0
216 | 1 | 0 | 0 | 0.16006 | 6.5465 | 0 | 0 | 0 | 0 | 6.5465 | 0 | 284800 | 0 | 17476.5816 | 164.4351 | 0
217 | 1 | 0 | 0 | 0.2982 | 12.1962 | 0 | 0 | 0 | 0 | 12.1962 | 0 | 284800 | 0 | 17476.5816 | 175.0067 | 0
218 | 1 | 0 | 0 | 0.25864 | 10.5783 | 0 | 0 | 0 | 0 | 10.5783 | 0 | 284800 | 0 | 17476.5816 | 184.176 | 0
219 | 1 | 0 | 0 | 0.28506 | 11.6589 | 0 | 0 | 0 | 0 | 11.6589 | 0 | 284800 | 0 | 17476.5816 | 194.282 | 0
220 | 1 | 0 | 0 | 0.34726 | 14.2031 | 0 | 0 | 0 | 0 | 14.2031 | 0 | 284800 | 0 | 17476.5816 | 206.5932 | 0
221 | 1 | 0 | 0 | 0.35564 | 14.5455 | 0 | 0 | 0 | 0 | 14.5455 | 0 | 284800 | 0 | 17476.5816 | 219.2012 | 0
222 | 1 | 0 | 0 | 0.2916 | 11.9263 | 0 | 0 | 0 | 0 | 11.9263 | 0 | 284800 | 0 | 17476.5816 | 229.5389 | 0
223 | 1 | 0 | 0 | 0.40126 | 16.4116 | 0 | 0 | 0 | 0 | 16.4116 | 0 | 284800 | 0 | 17476.5816 | 243.7645 | 0
224 | 1 | 1 | 0.064139 | 0.49262 | 38.6713 | 200 | 38.6713 | 161.3287 | 200 | 0 | 0 | 284600 | 200 | 17676.5816 | 82.4359 | 0
225 | 1 | 1 | 0.33624 | 0.41637 | 114.1345 | 200 | 114.1345 | 82.4359 | 196.5704 | 0 | 0 | 284400 | 196.5704 | 17873.152 | 0 | 0
226 | 1 | 0 | 0.64644 | 0.55287 | 209.3046 | 0 | 0 | 0 | 0 | 180 | 29.3046 | 284400 | 29.3046 | 17902.4566 | 156.024 | 0
227 | 1 | 0 | 0.92099 | 0.34199 | 279.9703 | 0 | 0 | 0 | 0 | 180 | 99.9703 | 284400 | 99.9703 | 18002.4269 | 312.048 | 0
228 | 1 | 0 | 1 | 0.43657 | 306.6557 | 0 | 0 | 0 | 0 | 180 | 126.6557 | 284400 | 126.6557 | 18129.0826 | 468.072 | 0
229 | 1 | 0 | 1 | 0.40784 | 305.4807 | 0 | 0 | 0 | 0 | 49.3055 | 200 | 284400 | 200 | 18329.0826 | 510.81 | 56.1752
230 | 1 | 0 | 1 | 0.41356 | 305.7146 | 0 | 0 | 0 | 0 | 0 | 200 | 284400 | 200 | 18529.0826 | 510.81 | 105.7146
231 | 1 | 0 | 0.92099 | 0.46241 | 284.8956 | 0 | 0 | 0 | 0 | 0 | 200 | 284400 | 200 | 18729.0826 | 510.81 | 84.8956
232 | 1 | 0 | 0.64644 | 0.42963 | 204.2641 | 0 | 0 | 0 | 0 | 0 | 200 | 284400 | 200 | 18929.0826 | 510.81 | 4.2641
233 | 1 | 0 | 0.33624 | 0.31187 | 109.8603 | 0 | 0 | 0 | 0 | 0 | 109.8603 | 284400 | 109.8603 | 19038.9429 | 510.81 | 0
234 | 1 | 0 | 0.064139 | 0.25495 | 28.9508 | 0 | 0 | 0 | 0 | 0 | 28.9508 | 284400 | 28.9508 | 19067.8937 | 510.81 | 0
235 | 1 | 0 | 0 | 0.20843 | 8.5248 | 0 | 0 | 0 | 0 | 0 | 8.5248 | 284400 | 8.5248 | 19076.4185 | 510.81 | 0
236 | 1 | 1 | 0 | 0.22939 | 9.3823 | 200 | 9.3823 | 180 | 189.3823 | 0 | 0 | 284200 | 189.3823 | 19265.8007 | 330.81 | 0
237 | 1 | 1 | 0 | 0.1668 | 6.822 | 200 | 6.822 | 180 | 186.822 | 0 | 0 | 284000 | 186.822 | 19452.6227 | 150.81 | 0
238 | 1 | 0 | 0 | 0.12068 | 4.9358 | 0 | 0 | 0 | 0 | 4.9358 | 0 | 284000 | 0 | 19452.6227 | 155.0883 | 0
239 | 1 | 0 | 0 | 0.097817 | 4.0007 | 0 | 0 | 0 | 0 | 4.0007 | 0 | 284000 | 0 | 19452.6227 | 158.5561 | 0
240 | 1 | 0 | 0 | 0.064717 | 2.6469 | 0 | 0 | 0 | 0 | 2.6469 | 0 | 284000 | 0 | 19452.6227 | 160.8505 | 0
241 | 1 | 0 | 0 | 0.093353 | 3.8181 | 0 | 0 | 0 | 0 | 3.8181 | 0 | 284000 | 0 | 19452.6227 | 164.1601 | 0
242 | 1 | 0 | 0 | 0.10057 | 4.1131 | 0 | 0 | 0 | 0 | 4.1131 | 0 | 284000 | 0 | 19452.6227 | 167.7253 | 0
243 | 1 | 0 | 0 | 0.1395 | 5.7055 | 0 | 0 | 0 | 0 | 5.7055 | 0 | 284000 | 0 | 19452.6227 | 172.6709 | 0
244 | 1 | 0 | 0 | 0.11911 | 4.8716 | 0 | 0 | 0 | 0 | 4.8716 | 0 | 284000 | 0 | 19452.6227 | 176.8936 | 0
245 | 1 | 0 | 0 | 0.095534 | 3.9073 | 0 | 0 | 0 | 0 | 3.9073 | 0 | 284000 | 0 | 19452.6227 | 180.2805 | 0
246 | 1 | 0 | 0 | 0.16616 | 6.796 | 0 | 0 | 0 | 0 | 6.796 | 0 | 284000 | 0 | 19452.6227 | 186.1713 | 0
247 | 1 | 0 | 0 | 0.17681 | 7.2314 | 0 | 0 | 0 | 0 | 7.2314 | 0 | 284000 | 0 | 19452.6227 | 192.4395 | 0
248 | 1 | 1 | 0.064296 | 0.15851 | 25.0517 | 200 | 25.0517 | 174.9483 | 200 | 0 | 0 | 283800 | 200 | 19652.6227 | 17.4911 | 0
249 | 1 | 1 | 0.33705 | 0.15128 | 103.5287 | 200 | 103.5287 | 17.4911 | 121.0198 | 0 | 0 | 283600 | 121.0198 | 19773.6426 | 0 | 0
250 | 1 | 0 | 0.64802 | 0.14451 | 193.057 | 0 | 0 | 0 | 0 | 180 | 13.057 | 283600 | 13.057 | 19786.6996 | 156.024 | 0
251 | 1 | 0 | 0.92324 | 0.12261 | 271.6458 | 0 | 0 | 0 | 0 | 180 | 91.6458 | 283600 | 91.6458 | 19878.3453 | 312.048 | 0
252 | 1 | 0 | 1 | 0.10038 | 292.9053 | 0 | 0 | 0 | 0 | 180 | 112.9053 | 283600 | 112.9053 | 19991.2507 | 468.072 | 0
253 | 1 | 0 | 1 | 0.10443 | 293.0711 | 0 | 0 | 0 | 0 | 49.3055 | 200 | 283600 | 200 | 20191.2507 | 510.81 | 43.7656
254 | 1 | 0 | 1 | 0.065506 | 291.4792 | 0 | 0 | 0 | 0 | 0 | 200 | 283600 | 200 | 20391.2507 | 510.81 | 91.4792
255 | 1 | 0 | 0.92324 | 0.057244 | 268.9721 | 0 | 0 | 0 | 0 | 0 | 200 | 283600 | 200 | 20591.2507 | 510.81 | 68.9721
256 | 1 | 0 | 0.64802 | 0.058509 | 189.5398 | 0 | 0 | 0 | 0 | 0 | 189.5398 | 283600 | 189.5398 | 20780.7904 | 510.81 | 0
257 | 1 | 0 | 0.33705 | 0.095894 | 101.2635 | 0 | 0 | 0 | 0 | 0 | 101.2635 | 283600 | 101.2635 | 20882.054 | 510.81 | 0
258 | 1 | 0 | 0.064296 | 0.082966 | 21.962 | 0 | 0 | 0 | 0 | 0 | 21.962 | 283600 | 21.962 | 20904.016 | 510.81 | 0
259 | 1 | 0 | 0 | 0.063839 | 2.611 | 0 | 0 | 0 | 0 | 0 | 2.611 | 283600 | 2.611 | 20906.627 | 510.81 | 0
260 | 1 | 1 | 0 | 0.084924 | 3.4734 | 200 | 3.4734 | 180 | 183.4734 | 0 | 0 | 283400 | 183.4734 | 21090.1004 | 330.81 | 0
261 | 1 | 1 | 0 | 0.077845 | 3.1839 | 200 | 3.1839 | 180 | 183.1839 | 0 | 0 | 283200 | 183.1839 | 21273.2842 | 150.81 | 0
262 | 1 | 0 | 0 | 0.080505 | 3.2927 | 0 | 0 | 0 | 0 | 3.2927 | 0 | 283200 | 0 | 21273.2842 | 153.6641 | 0
263 | 1 | 0 | 0 | 0.10303 | 4.214 | 0 | 0 | 0 | 0 | 4.214 | 0 | 283200 | 0 | 21273.2842 | 157.3167 | 0
264 | 1 | 0 | 0 | 0.10531 | 4.3071 | 0 | 0 | 0 | 0 | 4.3071 | 0 | 283200 | 0 | 21273.2842 | 161.0502 | 0
265 | 1 | 0 | 0 | 0.12678 | 5.1852 | 0 | 0 | 0 | 0 | 5.1852 | 0 | 283200 | 0 | 21273.2842 | 165.5447 | 0
266 | 1 | 0 | 0 | 0.16161 | 6.6097 | 0 | 0 | 0 | 0 | 6.6097 | 0 | 283200 | 0 | 21273.2842 | 171.274 | 0
267 | 1 | 0 | 0 | 0.13865 | 5.6708 | 0 | 0 | 0 | 0 | 5.6708 | 0 | 283200 | 0 | 21273.2842 | 176.1894 | 0
268 | 1 | 0 | 0 | 0.1522 | 6.2249 | 0 | 0 | 0 | 0 | 6.2249 | 0 | 283200 | 0 | 21273.2842 | 181.5852 | 0
269 | 1 | 0 | 0 | 0.17899 | 7.3208 | 0 | 0 | 0 | 0 | 7.3208 | 0 | 283200 | 0 | 21273.2842 | 187.9309 | 0
270 | 1 | 0 | 0 | 0.23905 | 9.7769 | 0 | 0 | 0 | 0 | 9.7769 | 0 | 283200 | 0 | 21273.2842 | 196.4055 | 0
271 | 1 | 0 | 0 | 0.30418 | 12.4411 | 0 | 0 | 0 | 0 | 12.4411 | 0 | 283200 | 0 | 21273.2842 | 207.1895 | 0
272 | 1 | 1 | 0.068931 | 0.28765 | 31.6723 | 200 | 31.6723 | 168.3277 | 200 | 0 | 0 | 283000 | 200 | 21473.2842 | 38.8618 | 0
273 | 1 | 1 | 0.36135 | 0.42283 | 121.6527 | 200 | 121.6527 | 38.8618 | 160.5145 | 0 | 0 | 282800 | 160.5145 | 21633.7988 | 0 | 0
274 | 1 | 0 | 0.69473 | 0.41757 | 217.7172 | 0 | 0 | 0 | 0 | 180 | 37.7172 | 282800 | 37.7172 | 21671.516 | 156.024 | 0
275 | 1 | 0 | 0.98979 | 0.45341 | 304.3974 | 0 | 0 | 0 | 0 | 180 | 124.3974 | 282800 | 124.3974 | 21795.9134 | 312.048 | 0
276 | 1 | 0 | 1 | 0.40932 | 305.5414 | 0 | 0 | 0 | 0 | 180 | 125.5414 | 282800 | 125.5414 | 21921.4547 | 468.072 | 0
277 | 1 | 0 | 1 | 0.43666 | 306.6593 | 0 | 0 | 0 | 0 | 49.3055 | 200 | 282800 | 200 | 22121.4547 | 510.81 | 57.3538
278 | 1 | 0 | 1 | 0.47127 | 308.0748 | 0 | 0 | 0 | 0 | 0 | 200 | 282800 | 200 | 22321.4547 | 510.81 | 108.0748
279 | 1 | 0 | 0.98979 | 0.37801 | 301.3134 | 0 | 0 | 0 | 0 | 0 | 200 | 282800 | 200 | 22521.4547 | 510.81 | 101.3134
280 | 1 | 0 | 0.69473 | 0.30614 | 213.1599 | 0 | 0 | 0 | 0 | 0 | 200 | 282800 | 200 | 22721.4547 | 510.81 | 13.1599
281 | 1 | 0 | 0.36135 | 0.35951 | 119.0629 | 0 | 0 | 0 | 0 | 0 | 119.0629 | 282800 | 119.0629 | 22840.5176 | 510.81 | 0
282 | 1 | 0 | 0.068931 | 0.34448 | 33.9966 | 0 | 0 | 0 | 0 | 0 | 33.9966 | 282800 | 33.9966 | 22874.5143 | 510.81 | 0
283 | 1 | 0 | 0 | 0.42611 | 17.428 | 0 | 0 | 0 | 0 | 0 | 17.428 | 282800 | 17.428 | 22891.9423 | 510.81 | 0
284 | 1 | 1 | 0 | 0.54307 | 22.2117 | 200 | 22.2117 | 177.7883 | 200 | 0 | 0 | 282600 | 200 | 23091.9423 | 333.0217 | 0
285 | 1 | 1 | 0 | 0.41805 | 17.0983 | 200 | 17.0983 | 180 | 197.0983 | 0 | 0 | 282400 | 197.0983 | 23289.0406 | 153.0217 | 0
286 | 1 | 0 | 0 | 0.45891 | 18.7694 | 0 | 0 | 0 | 0 | 18.7694 | 0 | 282400 | 0 | 23289.0406 | 169.291 | 0
287 | 1 | 0 | 0 | 0.35218 | 14.4042 | 0 | 0 | 0 | 0 | 14.4042 | 0 | 282400 | 0 | 23289.0406 | 181.7765 | 0
288 | 1 | 0 | 0 | 0.34512 | 14.1152 | 0 | 0 | 0 | 0 | 14.1152 | 0 | 282400 | 0 | 23289.0406 | 194.0116 | 0
289 | 1 | 0 | 0 | 0.36236 | 14.8204 | 0 | 0 | 0 | 0 | 14.8204 | 0 | 282400 | 0 | 23289.0406 | 206.858 | 0
290 | 1 | 0 | 0 | 0.26271 | 10.7448 | 0 | 0 | 0 | 0 | 10.7448 | 0 | 282400 | 0 | 23289.0406 | 216.1716 | 0
291 | 1 | 0 | 0 | 0.29619 | 12.1141 | 0 | 0 | 0 | 0 | 12.1141 | 0 | 282400 | 0 | 23289.0406 | 226.6721 | 0
292 | 1 | 0 | 0 | 0.37792 | 15.4569 | 0 | 0 | 0 | 0 | 15.4569 | 0 | 282400 | 0 | 23289.0406 | 240.0701 | 0
293 | 1 | 0 | 0 | 0.32461 | 13.2767 | 0 | 0 | 0 | 0 | 13.2767 | 0 | 282400 | 0 | 23289.0406 | 251.5783 | 0
294 | 1 | 0 | 0 | 0.26443 | 10.8152 | 0 | 0 | 0 | 0 | 10.8152 | 0 | 282400 | 0 | 23289.0406 | 260.9529 | 0
295 | 1 | 0 | 0 | 0.27627 | 11.2994 | 0 | 0 | 0 | 0 | 11.2994 | 0 | 282400 | 0 | 23289.0406 | 270.7473 | 0
296 | 1 | 1 | 0.069828 | 0.29478 | 32.2229 | 200 | 32.2229 | 167.7771 | 200 | 0 | 0 | 282200 | 200 | 23489.0406 | 102.9702 | 0
297 | 1 | 1 | 0.36605 | 0.18943 | 113.464 | 200 | 113.464 | 86.536 | 200 | 0 | 0 | 282000 | 200 | 23689.0406 | 16.4342 | 0
298 | 1 | 0 | 0.70377 | 0.21844 | 212.1825 | 0 | 0 | 0 | 0 | 180 | 32.1825 | 282000 | 32.1825 | 23721.2231 | 172.4582 | 0
299 | 1 | 0 | 1 | 0.34929 | 303.0859 | 0 | 0 | 0 | 0 | 180 | 123.0859 | 282000 | 123.0859 | 23844.309 | 328.4822 | 0
300 | 1 | 0 | 1 | 0.29868 | 301.016 | 0 | 0 | 0 | 0 | 180 | 121.016 | 282000 | 121.016 | 23965.325 | 484.5062 | 0
301 | 1 | 0 | 1 | 0.37883 | 304.2939 | 0 | 0 | 0 | 0 | 30.3458 | 200 | 282000 | 200 | 24165.325 | 510.81 | 73.9481
302 | 1 | 0 | 1 | 0.20182 | 297.0546 | 0 | 0 | 0 | 0 | 0 | 200 | 282000 | 200 | 24365.325 | 510.81 | 97.0546
303 | 1 | 0 | 1 | 0.292 | 300.7428 | 0 | 0 | 0 | 0 | 0 | 200 | 282000 | 200 | 24565.325 | 510.81 | 100.7428
304 | 1 | 0 | 0.70377 | 0.29608 | 215.3582 | 0 | 0 | 0 | 0 | 0 | 200 | 282000 | 200 | 24765.325 | 510.81 | 15.3582
305 | 1 | 0 | 0.36605 | 0.24562 | 115.7622 | 0 | 0 | 0 | 0 | 0 | 115.7622 | 282000 | 115.7622 | 24881.0872 | 510.81 | 0
306 | 1 | 0 | 0.069828 | 0.35411 | 34.6493 | 0 | 0 | 0 | 0 | 0 | 34.6493 | 282000 | 34.6493 | 24915.7366 | 510.81 | 0
307 | 1 | 0 | 0 | 0.28681 | 11.7306 | 0 | 0 | 0 | 0 | 0 | 11.7306 | 282000 | 11.7306 | 24927.4672 | 510.81 | 0
308 | 1 | 1 | 0 | 0.25184 | 10.3004 | 200 | 10.3004 | 180 | 190.3004 | 0 | 0 | 281800 | 190.3004 | 25117.7676 | 330.81 | 0
309 | 1 | 1 | 0 | 0.31663 | 12.95 | 200 | 12.95 | 180 | 192.95 | 0 | 0 | 281600 | 192.95 | 25310.7176 | 150.81 | 0
310 | 1 | 0 | 0 | 0.33657 | 13.7657 | 0 | 0 | 0 | 0 | 13.7657 | 0 | 281600 | 0 | 25310.7176 | 162.7421 | 0
311 | 1 | 0 | 0 | 0.25208 | 10.3099 | 0 | 0 | 0 | 0 | 10.3099 | 0 | 281600 | 0 | 25310.7176 | 171.6787 | 0
312 | 1 | 0 | 0 | 0.2678 | 10.9531 | 0 | 0 | 0 | 0 | 10.9531 | 0 | 281600 | 0 | 25310.7176 | 181.1728 | 0
313 | 1 | 0 | 0 | 0.17561 | 7.1823 | 0 | 0 | 0 | 0 | 7.1823 | 0 | 281600 | 0 | 25310.7176 | 187.3984 | 0
314 | 1 | 0 | 0 | 0.19782 | 8.091 | 0 | 0 | 0 | 0 | 8.091 | 0 | 281600 | 0 | 25310.7176 | 194.4117 | 0
315 | 1 | 0 | 0 | 0.12129 | 4.9608 | 0 | 0 | 0 | 0 | 4.9608 | 0 | 281600 | 0 | 25310.7176 | 198.7117 | 0
316 | 1 | 0 | 0 | 0.11347 | 4.641 | 0 | 0 | 0 | 0 | 4.641 | 0 | 281600 | 0 | 25310.7176 | 202.7345 | 0
317 | 1 | 0 | 0 | 0.11697 | 4.7842 | 0 | 0 | 0 | 0 | 4.7842 | 0 | 281600 | 0 | 25310.7176 | 206.8815 | 0
318 | 1 | 0 | 0 | 0.1206 | 4.9324 | 0 | 0 | 0 | 0 | 4.9324 | 0 | 281600 | 0 | 25310.7176 | 211.1569 | 0
319 | 1 | 0 | 0 | 0.082422 | 3.3711 | 0 | 0 | 0 | 0 | 3.3711 | 0 | 281600 | 0 | 25310.7176 | 214.0789 | 0
320 | 1 | 1 | 0.070068 | 0.044803 | 22.0681 | 200 | 22.0681 | 177.9319 | 200 | 0 | 0 | 281400 | 200 | 25510.7176 | 36.147 | 0
321 | 1 | 1 | 0.36732 | 0.090204 | 109.7699 | 200 | 109.7699 | 36.147 | 145.9169 | 0 | 0 | 281200 | 145.9169 | 25656.6345 | 0 | 0
322 | 1 | 0 | 0.70619 | 0.099098 | 208.0016 | 0 | 0 | 0 | 0 | 180 | 28.0016 | 281200 | 28.0016 | 25684.6362 | 156.024 | 0
323 | 1 | 0 | 1 | 0.11712 | 293.5903 | 0 | 0 | 0 | 0 | 180 | 113.5903 | 281200 | 113.5903 | 25798.2265 | 312.048 | 0
324 | 1 | 0 | 1 | 0.073552 | 291.8083 | 0 | 0 | 0 | 0 | 180 | 111.8083 | 281200 | 111.8083 | 25910.0348 | 468.072 | 0
325 | 1 | 0 | 1 | 0.11209 | 293.3845 | 0 | 0 | 0 | 0 | 49.3055 | 200 | 281200 | 200 | 26110.0348 | 510.81 | 44.079
326 | 1 | 0 | 1 | 0.094031 | 292.6459 | 0 | 0 | 0 | 0 | 0 | 200 | 281200 | 200 | 26310.0348 | 510.81 | 92.6459
327 | 1 | 0 | 1 | 0.097692 | 292.7956 | 0 | 0 | 0 | 0 | 0 | 200 | 281200 | 200 | 26510.0348 | 510.81 | 92.7956
328 | 1 | 0 | 0.70619 | 0.089633 | 207.6145 | 0 | 0 | 0 | 0 | 0 | 200 | 281200 | 200 | 26710.0348 | 510.81 | 7.6145
329 | 1 | 0 | 0.36732 | 0.097496 | 110.0682 | 0 | 0 | 0 | 0 | 0 | 110.0682 | 281200 | 110.0682 | 26820.1029 | 510.81 | 0
330 | 1 | 0 | 0.070068 | 0.12671 | 25.4181 | 0 | 0 | 0 | 0 | 0 | 25.4181 | 281200 | 25.4181 | 26845.5211 | 510.81 | 0
331 | 1 | 0 | 0 | 0.11192 | 4.5774 | 0 | 0 | 0 | 0 | 0 | 4.5774 | 281200 | 4.5774 | 26850.0984 | 510.81 | 0
332 | 1 | 1 | 0 | 0.1576 | 6.446 | 200 | 6.446 | 180 | 186.446 | 0 | 0 | 281000 | 186.446 | 27036.5445 | 330.81 | 0
333 | 1 | 1 | 0 | 0.11252 | 4.602 | 200 | 4.602 | 180 | 184.602 | 0 | 0 | 280800 | 184.602 | 27221.1464 | 150.81 | 0
334 | 1 | 0 | 0 | 0.094772 | 3.8762 | 0 | 0 | 0 | 0 | 3.8762 | 0 | 280800 | 0 | 27221.1464 | 154.1699 | 0
335 | 1 | 0 | 0 | 0.13118 | 5.3653 | 0 | 0 | 0 | 0 | 5.3653 | 0 | 280800 | 0 | 27221.1464 | 158.8205 | 0
336 | 1 | 0 | 0 | 0.091592 | 3.7461 | 0 | 0 | 0 | 0 | 3.7461 | 0 | 280800 | 0 | 27221.1464 | 162.0676 | 0
337 | 1 | 0 | 0 | 0.099778 | 4.0809 | 0 | 0 | 0 | 0 | 4.0809 | 0 | 280800 | 0 | 27221.1464 | 165.6049 | 0
338 | 1 | 0 | 0 | 0.093175 | 3.8109 | 0 | 0 | 0 | 0 | 3.8109 | 0 | 280800 | 0 | 27221.1464 | 168.9082 | 0
339 | 1 | 0 | 0 | 0.058883 | 2.4083 | 0 | 0 | 0 | 0 | 2.4083 | 0 | 280800 | 0 | 27221.1464 | 170.9957 | 0
340 | 1 | 0 | 0 | 0.054819 | 2.2421 | 0 | 0 | 0 | 0 | 2.2421 | 0 | 280800 | 0 | 27221.1464 | 172.9392 | 0
341 | 1 | 0 | 0 | 0.042322 | 1.731 | 0 | 0 | 0 | 0 | 1.731 | 0 | 280800 | 0 | 27221.1464 | 174.4396 | 0
342 | 1 | 0 | 0 | 0.044167 | 1.8064 | 0 | 0 | 0 | 0 | 1.8064 | 0 | 280800 | 0 | 27221.1464 | 176.0054 | 0
343 | 1 | 0 | 0 | 0.043905 | 1.7957 | 0 | 0 | 0 | 0 | 1.7957 | 0 | 280800 | 0 | 27221.1464 | 177.5619 | 0
344 | 1 | 1 | 0.056982 | 0.04886 | 18.4548 | 200 | 18.4548 | 177.5619 | 196.0167 | 0 | 0 | 280600 | 196.0167 | 27417.1631 | 0 | 0
345 | 1 | 1 | 0.29872 | 0.039039 | 87.8659 | 200 | 87.8659 | 0 | 87.8659 | 0 | 0 | 280400 | 87.8659 | 27505.029 | 0 | 0
346 | 1 | 0 | 0.57431 | 0.05766 | 168.2179 | 0 | 0 | 0 | 0 | 168.2179 | 0 | 280400 | 0 | 27505.029 | 145.8112 | 0
347 | 1 | 0 | 0.81822 | 0.046518 | 238.2051 | 0 | 0 | 0 | 0 | 180 | 58.2051 | 280400 | 58.2051 | 27563.2341 | 301.8352 | 0
348 | 1 | 0 | 0.98421 | 0.047762 | 286.1942 | 0 | 0 | 0 | 0 | 180 | 106.1942 | 280400 | 106.1942 | 27669.4283 | 457.8592 | 0
349 | 1 | 0 | 1 | 0.070158 | 291.6695 | 0 | 0 | 0 | 0 | 61.0876 | 200 | 280400 | 200 | 27869.4283 | 510.81 | 30.5818
350 | 1 | 0 | 0.98421 | 0.089387 | 287.8966 | 0 | 0 | 0 | 0 | 0 | 200 | 280400 | 200 | 28069.4283 | 510.81 | 87.8966
351 | 1 | 0 | 0.81822 | 0.095571 | 240.2114 | 0 | 0 | 0 | 0 | 0 | 200 | 280400 | 200 | 28269.4283 | 510.81 | 40.2114
352 | 1 | 0 | 0.57431 | 0.086816 | 169.4103 | 0 | 0 | 0 | 0 | 0 | 169.4103 | 280400 | 169.4103 | 28438.8386 | 510.81 | 0
353 | 1 | 0 | 0.29872 | 0.10906 | 90.7297 | 0 | 0 | 0 | 0 | 0 | 90.7297 | 280400 | 90.7297 | 28529.5683 | 510.81 | 0
354 | 1 | 0 | 0.056982 | 0.090772 | 20.169 | 0 | 0 | 0 | 0 | 0 | 20.169 | 280400 | 20.169 | 28549.7373 | 510.81 | 0
355 | 1 | 0 | 0 | 0.061738 | 2.5251 | 0 | 0 | 0 | 0 | 0 | 2.5251 | 280400 | 2.5251 | 28552.2624 | 510.81 | 0
356 | 1 | 1 | 0 | 0.095819 | 3.919 | 200 | 3.919 | 180 | 183.919 | 0 | 0 | 280200 | 183.919 | 28736.1814 | 330.81 | 0
357 | 1 | 1 | 0 | 0.09046 | 3.6998 | 200 | 3.6998 | 180 | 183.6998 | 0 | 0 | 280000 | 183.6998 | 28919.8812 | 150.81 | 0
358 | 1 | 0 | 0 | 0.088916 | 3.6367 | 0 | 0 | 0 | 0 | 3.6367 | 0 | 280000 | 0 | 28919.8812 | 153.9623 | 0
359 | 1 | 0 | 0 | 0.088965 | 3.6387 | 0 | 0 | 0 | 0 | 3.6387 | 0 | 280000 | 0 | 28919.8812 | 157.1163 | 0
360 | 1 | 0 | 0 | 0.076083 | 3.1118 | 0 | 0 | 0 | 0 | 3.1118 | 0 | 280000 | 0 | 28919.8812 | 159.8136 | 0
361 | 1 | 0 | 0 | 0.076552 | 3.131 | 0 | 0 | 0 | 0 | 3.131 | 0 | 280000 | 0 | 28919.8812 | 162.5275 | 0
362 | 1 | 0 | 0 | 0.071772 | 2.9355 | 0 | 0 | 0 | 0 | 2.9355 | 0 | 280000 | 0 | 28919.8812 | 165.072 | 0
363 | 1 | 0 | 0 | 0.05185 | 2.1207 | 0 | 0 | 0 | 0 | 2.1207 | 0 | 280000 | 0 | 28919.8812 | 166.9102 | 0
364 | 1 | 0 | 0 | 0.073075 | 2.9888 | 0 | 0 | 0 | 0 | 2.9888 | 0 | 280000 | 0 | 28919.8812 | 169.5008 | 0
365 | 1 | 0 | 0 | 0.088517 | 3.6203 | 0 | 0 | 0 | 0 | 3.6203 | 0 | 280000 | 0 | 28919.8812 | 172.6389 | 0
366 | 1 | 0 | 0 | 0.092293 | 3.7748 | 0 | 0 | 0 | 0 | 3.7748 | 0 | 280000 | 0 | 28919.8812 | 175.9109 | 0
367 | 1 | 0 | 0 | 0.098391 | 4.0242 | 0 | 0 | 0 | 0 | 4.0242 | 0 | 280000 | 0 | 28919.8812 | 179.3991 | 0
368 | 1 | 1 | 0.074729 | 0.14041 | 27.3244 | 200 | 27.3244 | 172.6756 | 200 | 0 | 0 | 279800 | 200 | 29119.8812 | 6.7235 | 0
369 | 1 | 1 | 0.39175 | 0.14823 | 119.2 | 200 | 119.2 | 6.7235 | 125.9235 | 0 | 0 | 279600 | 125.9235 | 29245.8046 | 0 | 0
370 | 1 | 0 | 0.75317 | 0.21393 | 226.2657 | 0 | 0 | 0 | 0 | 180 | 46.2657 | 279600 | 46.2657 | 29292.0703 | 156.024 | 0
371 | 1 | 0 | 1 | 0.2227 | 297.9084 | 0 | 0 | 0 | 0 | 180 | 117.9084 | 279600 | 117.9084 | 29409.9788 | 312.048 | 0
372 | 1 | 0 | 1 | 0.16146 | 295.4039 | 0 | 0 | 0 | 0 | 180 | 115.4039 | 279600 | 115.4039 | 29525.3827 | 468.072 | 0
373 | 1 | 0 | 1 | 0.2576 | 299.3359 | 0 | 0 | 0 | 0 | 49.3055 | 200 | 279600 | 200 | 29725.3827 | 510.81 | 50.0304
374 | 1 | 0 | 1 | 0.20073 | 297.01 | 0 | 0 | 0 | 0 | 0 | 200 | 279600 | 200 | 29925.3827 | 510.81 | 97.01
375 | 1 | 0 | 1 | 0.30743 | 301.3738 | 0 | 0 | 0 | 0 | 0 | 200 | 279600 | 200 | 30125.3827 | 510.81 | 101.3738
376 | 1 | 0 | 0.75317 | 0.36574 | 232.4748 | 0 | 0 | 0 | 0 | 0 | 200 | 279600 | 200 | 30325.3827 | 510.81 | 32.4748
377 | 1 | 0 | 0.39175 | 0.30246 | 125.508 | 0 | 0 | 0 | 0 | 0 | 125.508 | 279600 | 125.508 | 30450.8907 | 510.81 | 0
378 | 1 | 0 | 0.074729 | 0.31159 | 34.3259 | 0 | 0 | 0 | 0 | 0 | 34.3259 | 279600 | 34.3259 | 30485.2166 | 510.81 | 0
379 | 1 | 0 | 0 | 0.24192 | 9.8946 | 0 | 0 | 0 | 0 | 0 | 9.8946 | 279600 | 9.8946 | 30495.1112 | 510.81 | 0
380 | 1 | 1 | 0 | 0.30302 | 12.3936 | 200 | 12.3936 | 180 | 192.3936 | 0 | 0 | 279400 | 192.3936 | 30687.5048 | 330.81 | 0
381 | 1 | 1 | 0 | 0.33533 | 13.715 | 200 | 13.715 | 180 | 193.715 | 0 | 0 | 279200 | 193.715 | 30881.2199 | 150.81 | 0
382 | 1 | 0 | 0 | 0.35012 | 14.32 | 0 | 0 | 0 | 0 | 14.32 | 0 | 279200 | 0 | 30881.2199 | 163.2226 | 0
383 | 1 | 0 | 0 | 0.36772 | 15.0396 | 0 | 0 | 0 | 0 | 15.0396 | 0 | 279200 | 0 | 30881.2199 | 176.2589 | 0
384 | 1 | 0 | 0 | 0.328 | 13.415 | 0 | 0 | 0 | 0 | 13.415 | 0 | 279200 | 0 | 30881.2199 | 187.8871 | 0
385 | 1 | 0 | 0 | 0.30001 | 12.2704 | 0 | 0 | 0 | 0 | 12.2704 | 0 | 279200 | 0 | 30881.2199 | 198.523 | 0
386 | 1 | 0 | 0 | 0.2964 | 12.1229 | 0 | 0 | 0 | 0 | 12.1229 | 0 | 279200 | 0 | 30881.2199 | 209.0312 | 0
387 | 1 | 0 | 0 | 0.34253 | 14.0095 | 0 | 0 | 0 | 0 | 14.0095 | 0 | 279200 | 0 | 30881.2199 | 221.1746 | 0
388 | 1 | 0 | 0 | 0.23658 | 9.6761 | 0 | 0 | 0 | 0 | 9.6761 | 0 | 279200 | 0 | 30881.2199 | 229.5619 | 0
389 | 1 | 0 | 0 | 0.21863 | 8.9421 | 0 | 0 | 0 | 0 | 8.9421 | 0 | 279200 | 0 | 30881.2199 | 237.3129 | 0
390 | 1 | 0 | 0 | 0.18004 | 7.3638 | 0 | 0 | 0 | 0 | 7.3638 | 0 | 279200 | 0 | 30881.2199 | 243.6958 | 0
391 | 1 | 0 | 0 | 0.10318 | 4.2201 | 0 | 0 | 0 | 0 | 4.2201 | 0 | 279200 | 0 | 30881.2199 | 247.3538 | 0
392 | 1 | 1 | 0.07419 | 0.1345 | 26.9271 | 200 | 26.9271 | 173.0729 | 200 | 0 | 0 | 279000 | 200 | 31081.2199 | 74.2809 | 0
393 | 1 | 1 | 0.38892 | 0.17534 | 119.4922 | 200 | 119.4922 | 74.2809 | 193.7731 | 0 | 0 | 278800 | 193.7731 | 31274.993 | 0 | 0
394 | 1 | 0 | 0.74774 | 0.13695 | 221.5472 | 0 | 0 | 0 | 0 | 180 | 41.5472 | 278800 | 41.5472 | 31316.5401 | 156.024 | 0
395 | 1 | 0 | 1 | 0.14884 | 294.8876 | 0 | 0 | 0 | 0 | 180 | 114.8876 | 278800 | 114.8876 | 31431.4278 | 312.048 | 0
396 | 1 | 0 | 1 | 0.15163 | 295.0018 | 0 | 0 | 0 | 0 | 180 | 115.0018 | 278800 | 115.0018 | 31546.4296 | 468.072 | 0
397 | 1 | 0 | 1 | 0.14271 | 294.6367 | 0 | 0 | 0 | 0 | 49.3055 | 200 | 278800 | 200 | 31746.4296 | 510.81 | 45.3312
398 | 1 | 0 | 1 | 0.10367 | 293.0401 | 0 | 0 | 0 | 0 | 0 | 200 | 278800 | 200 | 31946.4296 | 510.81 | 93.0401
399 | 1 | 0 | 1 | 0.11511 | 293.508 | 0 | 0 | 0 | 0 | 0 | 200 | 278800 | 200 | 32146.4296 | 510.81 | 93.508
400 | 1 | 0 | 0.74774 | 0.13573 | 221.4973 | 0 | 0 | 0 | 0 | 0 | 200 | 278800 | 200 | 32346.4296 | 510.81 | 21.4973
401 | 1 | 0 | 0.38892 | 0.15001 | 118.4562 | 0 | 0 | 0 | 0 | 0 | 118.4562 | 278800 | 118.4562 | 32464.8858 | 510.81 | 0
402 | 1 | 0 | 0.07419 | 0.14707 | 27.4411 | 0 | 0 | 0 | 0 | 0 | 27.4411 | 278800 | 27.4411 | 32492.3269 | 510.81 | 0
403 | 1 | 0 | 0 | 0.16584 | 6.7828 | 0 | 0 | 0 | 0 | 0 | 6.7828 | 278800 | 6.7828 | 32499.1097 | 510.81 | 0
404 | 1 | 1 | 0 | 0.15299 | 6.2571 | 200 | 6.2571 | 180 | 186.2571 | 0 | 0 | 278600 | 186.2571 | 32685.3668 | 330.81 | 0
405 | 1 | 1 | 0 | 0.1758 | 7.1903 | 200 | 7.1903 | 180 | 187.1903 | 0 | 0 | 278400 | 187.1903 | 32872.5571 | 150.81 | 0
406 | 1 | 0 | 0 | 0.20337 | 8.3178 | 0 | 0 | 0 | 0 | 8.3178 | 0 | 278400 | 0 | 32872.5571 | 158.0199 | 0
407 | 1 | 0 | 0 | 0.25461 | 10.4134 | 0 | 0 | 0 | 0 | 10.4134 | 0 | 278400 | 0 | 32872.5571 | 167.0462 | 0
408 | 1 | 0 | 0 | 0.24121 | 9.8654 | 0 | 0 | 0 | 0 | 9.8654 | 0 | 278400 | 0 | 32872.5571 | 175.5975 | 0
409 | 1 | 0 | 0 | 0.19678 | 8.0483 | 0 | 0 | 0 | 0 | 8.0483 | 0 | 278400 | 0 | 32872.5571 | 182.5737 | 0
410 | 1 | 0 | 0 | 0.19997 | 8.1787 | 0 | 0 | 0 | 0 | 8.1787 | 0 | 278400 | 0 | 32872.5571 | 189.663 | 0
411 | 1 | 0 | 0 | 0.18407 | 7.5283 | 0 | 0 | 0 | 0 | 7.5283 | 0 | 278400 | 0 | 32872.5571 | 196.1886 | 0
412 | 1 | 0 | 0 | 0.11474 | 4.6928 | 0 | 0 | 0 | 0 | 4.6928 | 0 | 278400 | 0 | 32872.5571 | 200.2563 | 0
413 | 1 | 0 | 0 | 0.11978 | 4.8991 | 0 | 0 | 0 | 0 | 4.8991 | 0 | 278400 | 0 | 32872.5571 | 204.5029 | 0
414 | 1 | 0 | 0 | 0.094292 | 3.8565 | 0 | 0 | 0 | 0 | 3.8565 | 0 | 278400 | 0 | 32872.5571 | 207.8457 | 0
415 | 1 | 0 | 0 | 0.12277 | 5.0213 | 0 | 0 | 0 | 0 | 5.0213 | 0 | 278400 | 0 | 32872.5571 | 212.1982 | 0
416 | 1 | 1 | 0.079353 | 0.13192 | 28.3127 | 200 | 28.3127 | 171.6873 | 200 | 0 | 0 | 278200 | 200 | 33072.5571 | 40.5109 | 0
417 | 1 | 1 | 0.41599 | 0.11194 | 124.7162 | 200 | 124.7162 | 40.5109 | 165.2271 | 0 | 0 | 278000 | 165.2271 | 33237.7842 | 0 | 0
418 | 1 | 0 | 0.79978 | 0.12604 | 236.1303 | 0 | 0 | 0 | 0 | 180 | 56.1303 | 278000 | 56.1303 | 33293.9145 | 156.024 | 0
419 | 1 | 0 | 1 | 0.15585 | 295.1744 | 0 | 0 | 0 | 0 | 180 | 115.1744 | 278000 | 115.1744 | 33409.0889 | 312.048 | 0
420 | 1 | 0 | 1 | 0.18807 | 296.492 | 0 | 0 | 0 | 0 | 180 | 116.492 | 278000 | 116.492 | 33525.5809 | 468.072 | 0
421 | 1 | 0 | 1 | 0.15105 | 294.9781 | 0 | 0 | 0 | 0 | 49.3055 | 200 | 278000 | 200 | 33725.5809 | 510.81 | 45.6726
422 | 1 | 0 | 1 | 0.13663 | 294.3882 | 0 | 0 | 0 | 0 | 0 | 200 | 278000 | 200 | 33925.5809 | 510.81 | 94.3882
423 | 1 | 0 | 1 | 0.12432 | 293.8847 | 0 | 0 | 0 | 0 | 0 | 200 | 278000 | 200 | 34125.5809 | 510.81 | 93.8847
424 | 1 | 0 | 0.79978 | 0.099266 | 235.035 | 0 | 0 | 0 | 0 | 0 | 200 | 278000 | 200 | 34325.5809 | 510.81 | 35.035
425 | 1 | 0 | 0.41599 | 0.088424 | 123.7545 | 0 | 0 | 0 | 0 | 0 | 123.7545 | 278000 | 123.7545 | 34449.3354 | 510.81 | 0
426 | 1 | 0 | 0.079353 | 0.1188 | 27.7761 | 0 | 0 | 0 | 0 | 0 | 27.7761 | 278000 | 27.7761 | 34477.1115 | 510.81 | 0
427 | 1 | 0 | 0 | 0.12695 | 5.1921 | 0 | 0 | 0 | 0 | 0 | 5.1921 | 278000 | 5.1921 | 34482.3036 | 510.81 | 0
428 | 1 | 1 | 0 | 0.11224 | 4.5904 | 200 | 4.5904 | 180 | 184.5904 | 0 | 0 | 277800 | 184.5904 | 34666.894 | 330.81 | 0
429 | 1 | 1 | 0 | 0.10473 | 4.2833 | 200 | 4.2833 | 180 | 184.2833 | 0 | 0 | 277600 | 184.2833 | 34851.1773 | 150.81 | 0
430 | 1 | 0 | 0 | 0.093044 | 3.8055 | 0 | 0 | 0 | 0 | 3.8055 | 0 | 277600 | 0 | 34851.1773 | 154.1086 | 0
431 | 1 | 0 | 0 | 0.074738 | 3.0568 | 0 | 0 | 0 | 0 | 3.0568 | 0 | 277600 | 0 | 34851.1773 | 156.7582 | 0
432 | 1 | 0 | 0 | 0.064234 | 2.6272 | 0 | 0 | 0 | 0 | 2.6272 | 0 | 277600 | 0 | 34851.1773 | 159.0355 | 0
433 | 1 | 0 | 0 | 0.058036 | 2.3737 | 0 | 0 | 0 | 0 | 2.3737 | 0 | 277600 | 0 | 34851.1773 | 161.093 | 0
434 | 1 | 0 | 0 | 0.075183 | 3.075 | 0 | 0 | 0 | 0 | 3.075 | 0 | 277600 | 0 | 34851.1773 | 163.7584 | 0
435 | 1 | 0 | 0 | 0.085871 | 3.5121 | 0 | 0 | 0 | 0 | 3.5121 | 0 | 277600 | 0 | 34851.1773 | 166.8027 | 0
436 | 1 | 0 | 0 | 0.095468 | 3.9046 | 0 | 0 | 0 | 0 | 3.9046 | 0 | 277600 | 0 | 34851.1773 | 170.1872 | 0
437 | 1 | 0 | 0 | 0.14338 | 5.8642 | 0 | 0 | 0 | 0 | 5.8642 | 0 | 277600 | 0 | 34851.1773 | 175.2703 | 0
438 | 1 | 0 | 0 | 0.17817 | 7.2871 | 0 | 0 | 0 | 0 | 7.2871 | 0 | 277600 | 0 | 34851.1773 | 181.5867 | 0
439 | 1 | 0 | 0 | 0.22283 | 9.1137 | 0 | 0 | 0 | 0 | 9.1137 | 0 | 277600 | 0 | 34851.1773 | 189.4865 | 0
440 | 1 | 1 | 0.065066 | 0.1726 | 25.8504 | 200 | 25.8504 | 174.1496 | 200 | 0 | 0 | 277400 | 200 | 35051.1773 | 15.3369 | 0
441 | 1 | 1 | 0.34109 | 0.20576 | 106.923 | 200 | 106.923 | 15.3369 | 122.2599 | 0 | 0 | 277200 | 122.2599 | 35173.4372 | 0 | 0
442 | 1 | 0 | 0.65578 | 0.33872 | 203.2422 | 0 | 0 | 0 | 0 | 180 | 23.2422 | 277200 | 23.2422 | 35196.6793 | 156.024 | 0
443 | 1 | 0 | 0.93429 | 0.39138 | 285.8319 | 0 | 0 | 0 | 0 | 180 | 105.8319 | 277200 | 105.8319 | 35302.5112 | 312.048 | 0
444 | 1 | 0 | 1 | 0.22695 | 298.0821 | 0 | 0 | 0 | 0 | 180 | 118.0821 | 277200 | 118.0821 | 35420.5933 | 468.072 | 0
445 | 1 | 0 | 1 | 0.15963 | 295.3287 | 0 | 0 | 0 | 0 | 49.3055 | 200 | 277200 | 200 | 35620.5933 | 510.81 | 46.0233
446 | 1 | 0 | 1 | 0.21 | 297.3889 | 0 | 0 | 0 | 0 | 0 | 200 | 277200 | 200 | 35820.5933 | 510.81 | 97.3889
447 | 1 | 0 | 0.93429 | 0.31692 | 282.7866 | 0 | 0 | 0 | 0 | 0 | 200 | 277200 | 200 | 36020.5933 | 510.81 | 82.7866
448 | 1 | 0 | 0.65578 | 0.4407 | 207.4131 | 0 | 0 | 0 | 0 | 0 | 200 | 277200 | 200 | 36220.5933 | 510.81 | 7.4131
449 | 1 | 0 | 0.34109 | 0.29404 | 110.5337 | 0 | 0 | 0 | 0 | 0 | 110.5337 | 277200 | 110.5337 | 36331.127 | 510.81 | 0
450 | 1 | 0 | 0.065066 | 0.25442 | 29.1968 | 0 | 0 | 0 | 0 | 0 | 29.1968 | 277200 | 29.1968 | 36360.3237 | 510.81 | 0
451 | 1 | 0 | 0 | 0.23135 | 9.4623 | 0 | 0 | 0 | 0 | 0 | 9.4623 | 277200 | 9.4623 | 36369.786 | 510.81 | 0
452 | 1 | 1 | 0 | 0.11757 | 4.8087 | 200 | 4.8087 | 180 | 184.8087 | 0 | 0 | 277000 | 184.8087 | 36554.5947 | 330.81 | 0
453 | 1 | 1 | 0 | 0.10834 | 4.431 | 200 | 4.431 | 180 | 184.431 | 0 | 0 | 276800 | 184.431 | 36739.0258 | 150.81 | 0
454 | 1 | 0 | 0 | 0.10148 | 4.1504 | 0 | 0 | 0 | 0 | 4.1504 | 0 | 276800 | 0 | 36739.0258 | 154.4076 | 0
455 | 1 | 0 | 0 | 0.12718 | 5.2015 | 0 | 0 | 0 | 0 | 5.2015 | 0 | 276800 | 0 | 36739.0258 | 158.9162 | 0
456 | 1 | 0 | 0 | 0.1355 | 5.5421 | 0 | 0 | 0 | 0 | 5.5421 | 0 | 276800 | 0 | 36739.0258 | 163.7201 | 0
457 | 1 | 0 | 0 | 0.095073 | 3.8885 | 0 | 0 | 0 | 0 | 3.8885 | 0 | 276800 | 0 | 36739.0258 | 167.0906 | 0
458 | 1 | 0 | 0 | 0.074406 | 3.0432 | 0 | 0 | 0 | 0 | 3.0432 | 0 | 276800 | 0 | 36739.0258 | 169.7285 | 0
459 | 1 | 0 | 0 | 0.11065 | 4.5255 | 0 | 0 | 0 | 0 | 4.5255 | 0 | 276800 | 0 | 36739.0258 | 173.6512 | 0
460 | 1 | 0 | 0 | 0.090249 | 3.6912 | 0 | 0 | 0 | 0 | 3.6912 | 0 | 276800 | 0 | 36739.0258 | 176.8507 | 0
461 | 1 | 0 | 0 | 0.10906 | 4.4605 | 0 | 0 | 0 | 0 | 4.4605 | 0 | 276800 | 0 | 36739.0258 | 180.7171 | 0
462 | 1 | 0 | 0 | 0.098419 | 4.0253 | 0 | 0 | 0 | 0 | 4.0253 | 0 | 276800 | 0 | 36739.0258 | 184.2063 | 0
463 | 1 | 0 | 0 | 0.11445 | 4.6809 | 0 | 0 | 0 | 0 | 4.6809 | 0 | 276800 | 0 | 36739.0258 | 188.2637 | 0
464 | 1 | 1 | 0.065477 | 0.13977 | 24.6264 | 200 | 24.6264 | 175.3736 | 200 | 0 | 0 | 276600 | 200 | 36939.0258 | 12.89 | 0
465 | 1 | 1 | 0.34325 | 0.19198 | 106.9823 | 200 | 106.9823 | 12.89 | 119.8723 | 0 | 0 | 276400 | 119.8723 | 37058.8981 | 0 | 0
466 | 1 | 0 | 0.65992 | 0.20434 | 198.9434 | 0 | 0 | 0 | 0 | 180 | 18.9434 | 276400 | 18.9434 | 37077.8415 | 156.024 | 0
467 | 1 | 0 | 0.9402 | 0.3032 | 283.9315 | 0 | 0 | 0 | 0 | 180 | 103.9315 | 276400 | 103.9315 | 37181.7731 | 312.048 | 0
468 | 1 | 0 | 1 | 0.42595 | 306.2214 | 0 | 0 | 0 | 0 | 180 | 126.2214 | 276400 | 126.2214 | 37307.9944 | 468.072 | 0
469 | 1 | 0 | 1 | 0.5768 | 312.391 | 0 | 0 | 0 | 0 | 49.3055 | 200 | 276400 | 200 | 37507.9944 | 510.81 | 63.0855
470 | 1 | 0 | 1 | 0.69369 | 317.172 | 0 | 0 | 0 | 0 | 0 | 200 | 276400 | 200 | 37707.9944 | 510.81 | 117.172
471 | 1 | 0 | 0.9402 | 0.54958 | 294.0084 | 0 | 0 | 0 | 0 | 0 | 200 | 276400 | 200 | 37907.9944 | 510.81 | 94.0084
472 | 1 | 0 | 0.65992 | 1 | 231.4861 | 0 | 0 | 0 | 0 | 0 | 200 | 276400 | 200 | 38107.9944 | 510.81 | 31.4861
473 | 1 | 0 | 0.34325 | 0.84836 | 133.8284 | 0 | 0 | 0 | 0 | 0 | 133.8284 | 276400 | 133.8284 | 38241.8228 | 510.81 | 0
474 | 1 | 0 | 0.065477 | 0.37539 | 34.2634 | 0 | 0 | 0 | 0 | 0 | 34.2634 | 276400 | 34.2634 | 38276.0862 | 510.81 | 0
475 | 1 | 0 | 0 | 0.26581 | 10.8715 | 0 | 0 | 0 | 0 | 0 | 10.8715 | 276400 | 10.8715 | 38286.9577 | 510.81 | 0
476 | 1 | 1 | 0 | 0.23798 | 9.7334 | 200 | 9.7334 | 180 | 189.7334 | 0 | 0 | 276200 | 189.7334 | 38476.6911 | 330.81 | 0
477 | 1 | 1 | 0 | 0.24145 | 9.8754 | 200 | 9.8754 | 180 | 189.8754 | 0 | 0 | 276000 | 189.8754 | 38666.5665 | 150.81 | 0
478 | 1 | 0 | 0 | 0.16172 | 6.6145 | 0 | 0 | 0 | 0 | 6.6145 | 0 | 276000 | 0 | 38666.5665 | 156.5435 | 0
479 | 1 | 0 | 0 | 0.21086 | 8.6241 | 0 | 0 | 0 | 0 | 8.6241 | 0 | 276000 | 0 | 38666.5665 | 164.0189 | 0
480 | 1 | 0 | 0 | 0.1772 | 7.2476 | 0 | 0 | 0 | 0 | 7.2476 | 0 | 276000 | 0 | 38666.5665 | 170.3011 | 0
481 | 1 | 0 | 0 | 0.14415 | 5.8957 | 0 | 0 | 0 | 0 | 5.8957 | 0 | 276000 | 0 | 38666.5665 | 175.4115 | 0
482 | 1 | 0 | 0 | 0.13178 | 5.3897 | 0 | 0 | 0 | 0 | 5.3897 | 0 | 276000 | 0 | 38666.5665 | 180.0833 | 0
483 | 1 | 0 | 0 | 0.18311 | 7.4892 | 0 | 0 | 0 | 0 | 7.4892 | 0 | 276000 | 0 | 38666.5665 | 186.5749 | 0
484 | 1 | 0 | 0 | 0.14827 | 6.0644 | 0 | 0 | 0 | 0 | 6.0644 | 0 | 276000 | 0 | 38666.5665 | 191.8315 | 0
485 | 1 | 0 | 0 | 0.16354 | 6.6886 | 0 | 0 | 0 | 0 | 6.6886 | 0 | 276000 | 0 | 38666.5665 | 197.6292 | 0
486 | 1 | 0 | 0 | 0.32094 | 13.1262 | 0 | 0 | 0 | 0 | 13.1262 | 0 | 276000 | 0 | 38666.5665 | 209.0071 | 0
487 | 1 | 0 | 0 | 0.22681 | 9.2763 | 0 | 0 | 0 | 0 | 9.2763 | 0 | 276000 | 0 | 38666.5665 | 217.0478 | 0
488 | 1 | 1 | 0.069937 | 0.16966 | 27.1369 | 200 | 27.1369 | 172.8631 | 200 | 0 | 0 | 275800 | 200 | 38866.5665 | 44.1847 | 0
489 | 1 | 1 | 0.36663 | 0.15832 | 112.3584 | 200 | 112.3584 | 44.1847 | 156.5431 | 0 | 0 | 275600 | 156.5431 | 39023.1097 | 0 | 0
490 | 1 | 0 | 0.70488 | 0.14898 | 209.6619 | 0 | 0 | 0 | 0 | 180 | 29.6619 | 275600 | 29.6619 | 39052.7716 | 156.024 | 0
491 | 1 | 0 | 1 | 0.19624 | 296.8263 | 0 | 0 | 0 | 0 | 180 | 116.8263 | 275600 | 116.8263 | 39169.5979 | 312.048 | 0
492 | 1 | 0 | 1 | 0.17336 | 295.8903 | 0 | 0 | 0 | 0 | 180 | 115.8903 | 275600 | 115.8903 | 39285.4882 | 468.072 | 0
493 | 1 | 0 | 1 | 0.2031 | 297.1069 | 0 | 0 | 0 | 0 | 49.3055 | 200 | 275600 | 200 | 39485.4882 | 510.81 | 47.8014
494 | 1 | 0 | 1 | 0.19266 | 296.6799 | 0 | 0 | 0 | 0 | 0 | 200 | 275600 | 200 | 39685.4882 | 510.81 | 96.6799
495 | 1 | 0 | 1 | 0.16381 | 295.5 | 0 | 0 | 0 | 0 | 0 | 200 | 275600 | 200 | 39885.4882 | 510.81 | 95.5
496 | 1 | 0 | 0.70488 | 0.18642 | 211.1931 | 0 | 0 | 0 | 0 | 0 | 200 | 275600 | 200 | 40085.4882 | 510.81 | 11.1931
497 | 1 | 0 | 0.36663 | 0.19301 | 113.7773 | 0 | 0 | 0 | 0 | 0 | 113.7773 | 275600 | 113.7773 | 40199.2655 | 510.81 | 0
498 | 1 | 0 | 0.069937 | 0.27209 | 31.3262 | 0 | 0 | 0 | 0 | 0 | 31.3262 | 275600 | 31.3262 | 40230.5917 | 510.81 | 0
499 | 1 | 0 | 0 | 0.19451 | 7.9553 | 0 | 0 | 0 | 0 | 0 | 7.9553 | 275600 | 7.9553 | 40238.5471 | 510.81 | 0
500 | 1 | 1 | 0 | 0.20881 | 8.5405 | 200 | 8.5405 | 180 | 188.5405 | 0 | 0 | 275400 | 188.5405 | 40427.0875 | 330.81 | 0
501 | 1 | 1 | 0 | 0.26183 | 10.7087 | 200 | 10.7087 | 180 | 190.7087 | 0 | 0 | 275200 | 190.7087 | 40617.7963 | 150.81 | 0
502 | 1 | 0 | 0 | 0.16991 | 6.9492 | 0 | 0 | 0 | 0 | 6.9492 | 0 | 275200 | 0 | 40617.7963 | 156.8335 | 0
503 | 1 | 0 | 0 | 0.16523 | 6.7579 | 0 | 0 | 0 | 0 | 6.7579 | 0 | 275200 | 0 | 40617.7963 | 162.6912 | 0
504 | 1 | 0 | 0 | 0.18227 | 7.455 | 0 | 0 | 0 | 0 | 7.455 | 0 | 275200 | 0 | 40617.7963 | 169.1532 | 0
505 | 1 | 0 | 0 | 0.15967 | 6.5303 | 0 | 0 | 0 | 0 | 6.5303 | 0 | 275200 | 0 | 40617.7963 | 174.8137 | 0
506 | 1 | 0 | 0 | 0.26395 | 10.7955 | 0 | 0 | 0 | 0 | 10.7955 | 0 | 275200 | 0 | 40617.7963 | 184.1713 | 0
507 | 1 | 0 | 0 | 0.37632 | 15.3913 | 0 | 0 | 0 | 0 | 15.3913 | 0 | 275200 | 0 | 40617.7963 | 197.5124 | 0
508 | 1 | 0 | 0 | 0.2979 | 12.1842 | 0 | 0 | 0 | 0 | 12.1842 | 0 | 275200 | 0 | 40617.7963 | 208.0737 | 0
509 | 1 | 0 | 0 | 0.25395 | 10.3864 | 0 | 0 | 0 | 0 | 10.3864 | 0 | 275200 | 0 | 40617.7963 | 217.0766 | 0
510 | 1 | 0 | 0 | 0.17731 | 7.2519 | 0 | 0 | 0 | 0 | 7.2519 | 0 | 275200 | 0 | 40617.7963 | 223.3626 | 0
511 | 1 | 0 | 0 | 0.14779 | 6.0446 | 0 | 0 | 0 | 0 | 6.0446 | 0 | 275200 | 0 | 40617.7963 | 228.6021 | 0
512 | 1 | 1 | 0.065556 | 0.16554 | 25.7034 | 200 | 25.7034 | 174.2966 | 200 | 0 | 0 | 275000 | 200 | 40817.7963 | 54.3054 | 0
513 | 1 | 1 | 0.34366 | 0.27527 | 110.508 | 200 | 110.508 | 54.3054 | 164.8135 | 0 | 0 | 274800 | 164.8135 | 40982.6097 | 0 | 0
514 | 1 | 0 | 0.66072 | 0.26108 | 201.4929 | 0 | 0 | 0 | 0 | 180 | 21.4929 | 274800 | 21.4929 | 41004.1026 | 156.024 | 0
515 | 1 | 0 | 0.94133 | 0.38838 | 287.7415 | 0 | 0 | 0 | 0 | 180 | 107.7415 | 274800 | 107.7415 | 41111.8441 | 312.048 | 0
516 | 1 | 0 | 1 | 0.37921 | 304.3097 | 0 | 0 | 0 | 0 | 180 | 124.3097 | 274800 | 124.3097 | 41236.1539 | 468.072 | 0
517 | 1 | 0 | 1 | 0.4015 | 305.2214 | 0 | 0 | 0 | 0 | 49.3055 | 200 | 274800 | 200 | 41436.1539 | 510.81 | 55.9159
518 | 1 | 0 | 1 | 0.2679 | 299.7571 | 0 | 0 | 0 | 0 | 0 | 200 | 274800 | 200 | 41636.1539 | 510.81 | 99.7571
519 | 1 | 0 | 0.94133 | 0.34069 | 285.791 | 0 | 0 | 0 | 0 | 0 | 200 | 274800 | 200 | 41836.1539 | 510.81 | 85.791
520 | 1 | 0 | 0.66072 | 0.29552 | 202.9015 | 0 | 0 | 0 | 0 | 0 | 200 | 274800 | 200 | 42036.1539 | 510.81 | 2.9015
521 | 1 | 0 | 0.34366 | 0.44691 | 117.528 | 0 | 0 | 0 | 0 | 0 | 117.528 | 274800 | 117.528 | 42153.6819 | 510.81 | 0
522 | 1 | 0 | 0.065556 | 0.42096 | 36.15 | 0 | 0 | 0 | 0 | 0 | 36.15 | 274800 | 36.15 | 42189.8319 | 510.81 | 0
523 | 1 | 0 | 0 | 0.33714 | 13.7892 | 0 | 0 | 0 | 0 | 0 | 13.7892 | 274800 | 13.7892 | 42203.6211 | 510.81 | 0
524 | 1 | 1 | 0 | 0.25669 | 10.4987 | 200 | 10.4987 | 180 | 190.4987 | 0 | 0 | 274600 | 190.4987 | 42394.1198 | 330.81 | 0
525 | 1 | 1 | 0 | 0.28058 | 11.4756 | 200 | 11.4756 | 180 | 191.4756 | 0 | 0 | 274400 | 191.4756 | 42585.5953 | 150.81 | 0
526 | 1 | 0 | 0 | 0.37686 | 15.4134 | 0 | 0 | 0 | 0 | 15.4134 | 0 | 274400 | 0 | 42585.5953 | 164.1703 | 0
527 | 1 | 0 | 0 | 0.30432 | 12.4466 | 0 | 0 | 0 | 0 | 12.4466 | 0 | 274400 | 0 | 42585.5953 | 174.9591 | 0
528 | 1 | 0 | 0 | 0.32446 | 13.2704 | 0 | 0 | 0 | 0 | 13.2704 | 0 | 274400 | 0 | 42585.5953 | 186.4619 | 0
529 | 1 | 0 | 0 | 0.35255 | 14.4191 | 0 | 0 | 0 | 0 | 14.4191 | 0 | 274400 | 0 | 42585.5953 | 198.9604 | 0
530 | 1 | 0 | 0 | 0.33431 | 13.6734 | 0 | 0 | 0 | 0 | 13.6734 | 0 | 274400 | 0 | 42585.5953 | 210.8124 | 0
531 | 1 | 0 | 0 | 0.34461 | 14.0944 | 0 | 0 | 0 | 0 | 14.0944 | 0 | 274400 | 0 | 42585.5953 | 223.0294 | 0
532 | 1 | 0 | 0 | 0.39155 | 16.0146 | 0 | 0 | 0 | 0 | 16.0146 | 0 | 274400 | 0 | 42585.5953 | 236.9109 | 0
533 | 1 | 0 | 0 | 0.53004 | 21.6788 | 0 | 0 | 0 | 0 | 21.6788 | 0 | 274400 | 0 | 42585.5953 | 255.7021 | 0
534 | 1 | 0 | 0 | 0.49321 | 20.1722 | 0 | 0 | 0 | 0 | 20.1722 | 0 | 274400 | 0 | 42585.5953 | 273.1874 | 0
535 | 1 | 0 | 0 | 0.61459 | 25.1367 | 0 | 0 | 0 | 0 | 25.1367 | 0 | 274400 | 0 | 42585.5953 | 294.9759 | 0
536 | 1 | 1 | 0.063027 | 0.59895 | 42.6993 | 200 | 42.6993 | 157.3007 | 200 | 0 | 0 | 274200 | 200 | 42785.5953 | 137.6752 | 0
537 | 1 | 1 | 0.33041 | 0.58812 | 119.4752 | 200 | 119.4752 | 80.5248 | 200 | 0 | 0 | 274000 | 200 | 42985.5953 | 57.1504 | 0
538 | 1 | 0 | 0.63523 | 0.60454 | 208.1802 | 0 | 0 | 0 | 0 | 180 | 28.1802 | 274000 | 28.1802 | 43013.7755 | 213.1744 | 0
539 | 1 | 0 | 0.90502 | 0.46227 | 280.2767 | 0 | 0 | 0 | 0 | 180 | 100.2767 | 274000 | 100.2767 | 43114.0523 | 369.1984 | 0
540 | 1 | 0 | 1 | 0.29633 | 300.9198 | 0 | 0 | 0 | 0 | 163.3728 | 137.547 | 274000 | 137.547 | 43251.5992 | 510.81 | 0
541 | 1 | 0 | 1 | 0.28268 | 300.3615 | 0 | 0 | 0 | 0 | 0 | 200 | 274000 | 200 | 43451.5992 | 510.81 | 100.3615
542 | 1 | 0 | 1 | 0.22923 | 298.1756 | 0 | 0 | 0 | 0 | 0 | 200 | 274000 | 200 | 43651.5992 | 510.81 | 98.1756
543 | 1 | 0 | 0.90502 | 0.31191 | 274.1271 | 0 | 0 | 0 | 0 | 0 | 200 | 274000 | 200 | 43851.5992 | 510.81 | 74.1271
544 | 1 | 0 | 0.63523 | 0.26641 | 194.3504 | 0 | 0 | 0 | 0 | 0 | 194.3504 | 274000 | 194.3504 | 44045.9496 | 510.81 | 0
545 | 1 | 0 | 0.33041 | 0.33068 | 108.9458 | 0 | 0 | 0 | 0 | 0 | 108.9458 | 274000 | 108.9458 | 44154.8954 | 510.81 | 0
546 | 1 | 0 | 0.063027 | 0.28922 | 30.0312 | 0 | 0 | 0 | 0 | 0 | 30.0312 | 274000 | 30.0312 | 44184.9266 | 510.81 | 0
547 | 1 | 0 | 0 | 0.33298 | 13.619 | 0 | 0 | 0 | 0 | 0 | 13.619 | 274000 | 13.619 | 44198.5456 | 510.81 | 0
548 | 1 | 1 | 0 | 0.27284 | 11.1591 | 200 | 11.1591 | 180 | 191.1591 | 0 | 0 | 273800 | 191.1591 | 44389.7047 | 330.81 | 0
549 | 1 | 1 | 0 | 0.18441 | 7.5422 | 200 | 7.5422 | 180 | 187.5422 | 0 | 0 | 273600 | 187.5422 | 44577.2469 | 150.81 | 0
550 | 1 | 0 | 0 | 0.22513 | 9.208 | 0 | 0 | 0 | 0 | 9.208 | 0 | 273600 | 0 | 44577.2469 | 158.7915 | 0
551 | 1 | 0 | 0 | 0.28459 | 11.6398 | 0 | 0 | 0 | 0 | 11.6398 | 0 | 273600 | 0 | 44577.2469 | 168.8808 | 0
552 | 1 | 0 | 0 | 0.30608 | 12.5187 | 0 | 0 | 0 | 0 | 12.5187 | 0 | 273600 | 0 | 44577.2469 | 179.732 | 0
553 | 1 | 0 | 0 | 0.38348 | 15.6843 | 0 | 0 | 0 | 0 | 15.6843 | 0 | 273600 | 0 | 44577.2469 | 193.3271 | 0
554 | 1 | 0 | 0 | 0.38794 | 15.8668 | 0 | 0 | 0 | 0 | 15.8668 | 0 | 273600 | 0 | 44577.2469 | 207.0805 | 0
555 | 1 | 0 | 0 | 0.49287 | 20.1584 | 0 | 0 | 0 | 0 | 20.1584 | 0 | 273600 | 0 | 44577.2469 | 224.5537 | 0
556 | 1 | 0 | 0 | 0.56144 | 22.9629 | 0 | 0 | 0 | 0 | 22.9629 | 0 | 273600 | 0 | 44577.2469 | 244.458 | 0
557 | 1 | 0 | 0 | 0.50369 | 20.6008 | 0 | 0 | 0 | 0 | 20.6008 | 0 | 273600 | 0 | 44577.2469 | 262.3148 | 0
558 | 1 | 0 | 0 | 0.35796 | 14.6404 | 0 | 0 | 0 | 0 | 14.6404 | 0 | 273600 | 0 | 44577.2469 | 275.0051 | 0
559 | 1 | 0 | 0 | 0.27278 | 11.1569 | 0 | 0 | 0 | 0 | 11.1569 | 0 | 273600 | 0 | 44577.2469 | 284.6759 | 0
560 | 1 | 1 | 0.064005 | 0.16932 | 25.41 | 200 | 25.41 | 174.59 | 200 | 0 | 0 | 273400 | 200 | 44777.2469 | 110.0859 | 0
561 | 1 | 1 | 0.33553 | 0.19601 | 104.9189 | 200 | 104.9189 | 95.0811 | 200 | 0 | 0 | 273200 | 200 | 44977.2469 | 15.0047 | 0
562 | 1 | 0 | 0.64509 | 0.23363 | 195.8574 | 0 | 0 | 0 | 0 | 180 | 15.8574 | 273200 | 15.8574 | 44993.1043 | 171.0287 | 0
563 | 1 | 0 | 0.91907 | 0.20997 | 274.0148 | 0 | 0 | 0 | 0 | 180 | 94.0148 | 273200 | 94.0148 | 45087.1191 | 327.0527 | 0
564 | 1 | 0 | 1 | 0.26925 | 299.8123 | 0 | 0 | 0 | 0 | 180 | 119.8123 | 273200 | 119.8123 | 45206.9314 | 483.0767 | 0
565 | 1 | 0 | 1 | 0.31356 | 301.6248 | 0 | 0 | 0 | 0 | 31.995 | 200 | 273200 | 200 | 45406.9314 | 510.81 | 69.6298
566 | 1 | 0 | 1 | 0.45096 | 307.2442 | 0 | 0 | 0 | 0 | 0 | 200 | 273200 | 200 | 45606.9314 | 510.81 | 107.2442
567 | 1 | 0 | 0.91907 | 0.46473 | 284.4346 | 0 | 0 | 0 | 0 | 0 | 200 | 273200 | 200 | 45806.9314 | 510.81 | 84.4346
568 | 1 | 0 | 0.64509 | 0.24255 | 196.2222 | 0 | 0 | 0 | 0 | 0 | 196.2222 | 273200 | 196.2222 | 46003.1535 | 510.81 | 0
569 | 1 | 0 | 0.33553 | 0.2087 | 105.4379 | 0 | 0 | 0 | 0 | 0 | 105.4379 | 273200 | 105.4379 | 46108.5914 | 510.81 | 0
570 | 1 | 0 | 0.064005 | 0.20504 | 26.8708 | 0 | 0 | 0 | 0 | 0 | 26.8708 | 273200 | 26.8708 | 46135.4622 | 510.81 | 0
571 | 1 | 0 | 0 | 0.27143 | 11.1014 | 0 | 0 | 0 | 0 | 0 | 11.1014 | 273200 | 11.1014 | 46146.5636 | 510.81 | 0
572 | 1 | 1 | 0 | 0.17769 | 7.2677 | 200 | 7.2677 | 180 | 187.2677 | 0 | 0 | 273000 | 187.2677 | 46333.8313 | 330.81 | 0
573 | 1 | 1 | 0 | 0.098934 | 4.0464 | 200 | 4.0464 | 180 | 184.0464 | 0 | 0 | 272800 | 184.0464 | 46517.8777 | 150.81 | 0
574 | 1 | 0 | 0 | 0.14322 | 5.8578 | 0 | 0 | 0 | 0 | 5.8578 | 0 | 272800 | 0 | 46517.8777 | 155.8875 | 0
575 | 1 | 0 | 0 | 0.16402 | 6.7085 | 0 | 0 | 0 | 0 | 6.7085 | 0 | 272800 | 0 | 46517.8777 | 161.7025 | 0
576 | 1 | 0 | 0 | 0.13384 | 5.474 | 0 | 0 | 0 | 0 | 5.474 | 0 | 272800 | 0 | 46517.8777 | 166.4473 | 0
577 | 1 | 0 | 0 | 0.22099 | 9.0383 | 0 | 0 | 0 | 0 | 9.0383 | 0 | 272800 | 0 | 46517.8777 | 174.2817 | 0
578 | 1 | 0 | 0 | 0.17323 | 7.0852 | 0 | 0 | 0 | 0 | 7.0852 | 0 | 272800 | 0 | 46517.8777 | 180.4232 | 0
579 | 1 | 0 | 0 | 0.22604 | 9.245 | 0 | 0 | 0 | 0 | 9.245 | 0 | 272800 | 0 | 46517.8777 | 188.4367 | 0
580 | 1 | 0 | 0 | 0.23728 | 9.7046 | 0 | 0 | 0 | 0 | 9.7046 | 0 | 272800 | 0 | 46517.8777 | 196.8487 | 0
581 | 1 | 0 | 0 | 0.34233 | 14.0013 | 0 | 0 | 0 | 0 | 14.0013 | 0 | 272800 | 0 | 46517.8777 | 208.985 | 0
582 | 1 | 0 | 0 | 0.45872 | 18.7616 | 0 | 0 | 0 | 0 | 18.7616 | 0 | 272800 | 0 | 46517.8777 | 225.2476 | 0
583 | 1 | 0 | 0 | 0.43958 | 17.9788 | 0 | 0 | 0 | 0 | 17.9788 | 0 | 272800 | 0 | 46517.8777 | 240.8317 | 0
584 | 1 | 1 | 0.063188 | 0.45205 | 36.7376 | 200 | 36.7376 | 163.2624 | 200 | 0 | 0 | 272600 | 200 | 46717.8777 | 77.5692 | 0
585 | 1 | 1 | 0.33125 | 0.34022 | 109.5793 | 200 | 109.5793 | 77.5692 | 187.1485 | 0 | 0 | 272400 | 187.1485 | 46905.0263 | 0 | 0
586 | 1 | 0 | 0.63685 | 0.32821 | 197.3461 | 0 | 0 | 0 | 0 | 180 | 17.3461 | 272400 | 17.3461 | 46922.3723 | 156.024 | 0
587 | 1 | 0 | 0.90733 | 0.31002 | 274.7168 | 0 | 0 | 0 | 0 | 180 | 94.7168 | 272400 | 94.7168 | 47017.0891 | 312.048 | 0
588 | 1 | 0 | 1 | 0.40596 | 305.4039 | 0 | 0 | 0 | 0 | 180 | 125.4039 | 272400 | 125.4039 | 47142.493 | 468.072 | 0
589 | 1 | 0 | 1 | 0.26971 | 299.8313 | 0 | 0 | 0 | 0 | 49.3055 | 200 | 272400 | 200 | 47342.493 | 510.81 | 50.5259
590 | 1 | 0 | 1 | 0.27223 | 299.9343 | 0 | 0 | 0 | 0 | 0 | 200 | 272400 | 200 | 47542.493 | 510.81 | 99.9343
591 | 1 | 0 | 0.90733 | 0.29009 | 273.9016 | 0 | 0 | 0 | 0 | 0 | 200 | 272400 | 200 | 47742.493 | 510.81 | 73.9016
592 | 1 | 0 | 0.63685 | 0.29522 | 195.9966 | 0 | 0 | 0 | 0 | 0 | 195.9966 | 272400 | 195.9966 | 47938.4896 | 510.81 | 0
593 | 1 | 0 | 0.33125 | 0.25846 | 106.2356 | 0 | 0 | 0 | 0 | 0 | 106.2356 | 272400 | 106.2356 | 48044.7252 | 510.81 | 0
594 | 1 | 0 | 0.063188 | 0.21269 | 26.9475 | 0 | 0 | 0 | 0 | 0 | 26.9475 | 272400 | 26.9475 | 48071.6727 | 510.81 | 0
595 | 1 | 0 | 0 | 0.18884 | 7.7236 | 0 | 0 | 0 | 0 | 0 | 7.7236 | 272400 | 7.7236 | 48079.3962 | 510.81 | 0
596 | 1 | 1 | 0 | 0.25453 | 10.4103 | 200 | 10.4103 | 180 | 190.4103 | 0 | 0 | 272200 | 190.4103 | 48269.8066 | 330.81 | 0
597 | 1 | 1 | 0 | 0.27571 | 11.2764 | 200 | 11.2764 | 180 | 191.2764 | 0 | 0 | 272000 | 191.2764 | 48461.0829 | 150.81 | 0
598 | 1 | 0 | 0 | 0.30907 | 12.6409 | 0 | 0 | 0 | 0 | 12.6409 | 0 | 272000 | 0 | 48461.0829 | 161.7672 | 0
599 | 1 | 0 | 0 | 0.37029 | 15.1449 | 0 | 0 | 0 | 0 | 15.1449 | 0 | 272000 | 0 | 48461.0829 | 174.8948 | 0
600 | 1 | 0 | 0 | 0.30286 | 12.3868 | 0 | 0 | 0 | 0 | 12.3868 | 0 | 272000 | 0 | 48461.0829 | 185.6316 | 0
601 | 1 | 0 | 0 | 0.20866 | 8.5344 | 0 | 0 | 0 | 0 | 8.5344 | 0 | 272000 | 0 | 48461.0829 | 193.0292 | 0
602 | 1 | 0 | 0 | 0.20701 | 8.4669 | 0 | 0 | 0 | 0 | 8.4669 | 0 | 272000 | 0 | 48461.0829 | 200.3683 | 0
603 | 1 | 0 | 0 | 0.29022 | 11.87 | 0 | 0 | 0 | 0 | 11.87 | 0 | 272000 | 0 | 48461.0829 | 210.6573 | 0
604 | 1 | 0 | 0 | 0.28451 | 11.6364 | 0 | 0 | 0 | 0 | 11.6364 | 0 | 272000 | 0 | 48461.0829 | 220.7437 | 0
605 | 1 | 0 | 0 | 0.3187 | 13.0348 | 0 | 0 | 0 | 0 | 13.0348 | 0 | 272000 | 0 | 48461.0829 | 232.0423 | 0
606 | 1 | 0 | 0 | 0.23491 | 9.6079 | 0 | 0 | 0 | 0 | 9.6079 | 0 | 272000 | 0 | 48461.0829 | 240.3704 | 0
607 | 1 | 0 | 0 | 0.22864 | 9.3515 | 0 | 0 | 0 | 0 | 9.3515 | 0 | 272000 | 0 | 48461.0829 | 248.4763 | 0
608 | 1 | 1 | 0.061826 | 0.27855 | 29.2479 | 200 | 29.2479 | 170.7521 | 200 | 0 | 0 | 271800 | 200 | 48661.0829 | 77.7241 | 0
609 | 1 | 1 | 0.32411 | 0.26926 | 104.6158 | 200 | 104.6158 | 77.7241 | 182.3399 | 0 | 0 | 271600 | 182.3399 | 48843.4229 | 0 | 0
610 | 1 | 0 | 0.62313 | 0.27675 | 191.2786 | 0 | 0 | 0 | 0 | 180 | 11.2786 | 271600 | 11.2786 | 48854.7015 | 156.024 | 0
611 | 1 | 0 | 0.88778 | 0.28147 | 267.9028 | 0 | 0 | 0 | 0 | 180 | 87.9028 | 271600 | 87.9028 | 48942.6043 | 312.048 | 0
612 | 1 | 0 | 1 | 0.43867 | 306.7417 | 0 | 0 | 0 | 0 | 180 | 126.7417 | 271600 | 126.7417 | 49069.346 | 468.072 | 0
613 | 1 | 0 | 1 | 0.49386 | 308.9988 | 0 | 0 | 0 | 0 | 49.3055 | 200 | 271600 | 200 | 49269.346 | 510.81 | 59.6933
614 | 1 | 0 | 1 | 0.4603 | 307.6264 | 0 | 0 | 0 | 0 | 0 | 200 | 271600 | 200 | 49469.346 | 510.81 | 107.6264
615 | 1 | 0 | 0.88778 | 0.55168 | 278.9547 | 0 | 0 | 0 | 0 | 0 | 200 | 271600 | 200 | 49669.346 | 510.81 | 78.9547
616 | 1 | 0 | 0.62313 | 0.51488 | 201.018 | 0 | 0 | 0 | 0 | 0 | 200 | 271600 | 200 | 49869.346 | 510.81 | 1.018
617 | 1 | 0 | 0.32411 | 0.48348 | 113.3773 | 0 | 0 | 0 | 0 | 0 | 113.3773 | 271600 | 113.3773 | 49982.7233 | 510.81 | 0
618 | 1 | 0 | 0.061826 | 0.44971 | 36.2487 | 0 | 0 | 0 | 0 | 0 | 36.2487 | 271600 | 36.2487 | 50018.9719 | 510.81 | 0
619 | 1 | 0 | 0 | 0.32952 | 13.4774 | 0 | 0 | 0 | 0 | 0 | 13.4774 | 271600 | 13.4774 | 50032.4493 | 510.81 | 0
620 | 1 | 1 | 0 | 0.42823 | 17.5147 | 200 | 17.5147 | 180 | 197.5147 | 0 | 0 | 271400 | 197.5147 | 50229.964 | 330.81 | 0
621 | 1 | 1 | 0 | 0.23736 | 9.7079 | 200 | 9.7079 | 180 | 189.7079 | 0 | 0 | 271200 | 189.7079 | 50419.6718 | 150.81 | 0
622 | 1 | 0 | 0 | 0.28027 | 11.4632 | 0 | 0 | 0 | 0 | 11.4632 | 0 | 271200 | 0 | 50419.6718 | 160.7463 | 0
623 | 1 | 0 | 0 | 0.24644 | 10.0794 | 0 | 0 | 0 | 0 | 10.0794 | 0 | 271200 | 0 | 50419.6718 | 169.4831 | 0
624 | 1 | 0 | 0 | 0.16135 | 6.5991 | 0 | 0 | 0 | 0 | 6.5991 | 0 | 271200 | 0 | 50419.6718 | 175.2033 | 0
625 | 1 | 0 | 0 | 0.1715 | 7.0142 | 0 | 0 | 0 | 0 | 7.0142 | 0 | 271200 | 0 | 50419.6718 | 181.2832 | 0
626 | 1 | 0 | 0 | 0.1062 | 4.3435 | 0 | 0 | 0 | 0 | 4.3435 | 0 | 271200 | 0 | 50419.6718 | 185.0482 | 0
627 | 1 | 0 | 0 | 0.13802 | 5.6449 | 0 | 0 | 0 | 0 | 5.6449 | 0 | 271200 | 0 | 50419.6718 | 189.9412 | 0
628 | 1 | 0 | 0 | 0.12721 | 5.2029 | 0 | 0 | 0 | 0 | 5.2029 | 0 | 271200 | 0 | 50419.6718 | 194.4511 | 0
629 | 1 | 0 | 0 | 0.1459 | 5.9673 | 0 | 0 | 0 | 0 | 5.9673 | 0 | 271200 | 0 | 50419.6718 | 199.6235 | 0
630 | 1 | 0 | 0 | 0.19482 | 7.9683 | 0 | 0 | 0 | 0 | 7.9683 | 0 | 271200 | 0 | 50419.6718 | 206.5304 | 0
631 | 1 | 0 | 0 | 0.14562 | 5.956 | 0 | 0 | 0 | 0 | 5.956 | 0 | 271200 | 0 | 50419.6718 | 211.6931 | 0
632 | 1 | 1 | 0.064478 | 0.10022 | 22.7203 | 200 | 22.7203 | 177.2797 | 200 | 0 | 0 | 271000 | 200 | 50619.6718 | 34.4133 | 0
633 | 1 | 1 | 0.33801 | 0.09579 | 101.5348 | 200 | 101.5348 | 34.4133 | 135.9482 | 0 | 0 | 270800 | 135.9482 | 50755.62 | 0 | 0
634 | 1 | 0 | 0.64985 | 0.089637 | 191.3428 | 0 | 0 | 0 | 0 | 180 | 11.3428 | 270800 | 11.3428 | 50766.9628 | 156.024 | 0
635 | 1 | 0 | 0.92585 | 0.084644 | 270.8477 | 0 | 0 | 0 | 0 | 180 | 90.8477 | 270800 | 90.8477 | 50857.8105 | 312.048 | 0
636 | 1 | 0 | 1 | 0.09891 | 292.8454 | 0 | 0 | 0 | 0 | 180 | 112.8454 | 270800 | 112.8454 | 50970.656 | 468.072 | 0
637 | 1 | 0 | 1 | 0.10208 | 292.975 | 0 | 0 | 0 | 0 | 49.3055 | 200 | 270800 | 200 | 51170.656 | 510.81 | 43.6695
638 | 1 | 0 | 1 | 0.096954 | 292.7654 | 0 | 0 | 0 | 0 | 0 | 200 | 270800 | 200 | 51370.656 | 510.81 | 92.7654
639 | 1 | 0 | 0.92585 | 0.10465 | 271.6662 | 0 | 0 | 0 | 0 | 0 | 200 | 270800 | 200 | 51570.656 | 510.81 | 71.6662
640 | 1 | 0 | 0.64985 | 0.11155 | 192.239 | 0 | 0 | 0 | 0 | 0 | 192.239 | 270800 | 192.239 | 51762.8949 | 510.81 | 0
641 | 1 | 0 | 0.33801 | 0.083956 | 101.0508 | 0 | 0 | 0 | 0 | 0 | 101.0508 | 270800 | 101.0508 | 51863.9457 | 510.81 | 0
642 | 1 | 0 | 0.064478 | 0.11124 | 23.1711 | 0 | 0 | 0 | 0 | 0 | 23.1711 | 270800 | 23.1711 | 51887.1168 | 510.81 | 0
643 | 1 | 0 | 0 | 0.1072 | 4.3844 | 0 | 0 | 0 | 0 | 0 | 4.3844 | 270800 | 4.3844 | 51891.5011 | 510.81 | 0
644 | 1 | 1 | 0 | 0.07766 | 3.1763 | 200 | 3.1763 | 180 | 183.1763 | 0 | 0 | 270600 | 183.1763 | 52074.6774 | 330.81 | 0
645 | 1 | 1 | 0 | 0.089281 | 3.6516 | 200 | 3.6516 | 180 | 183.6516 | 0 | 0 | 270400 | 183.6516 | 52258.329 | 150.81 | 0
646 | 1 | 0 | 0 | 0.095244 | 3.8955 | 0 | 0 | 0 | 0 | 3.8955 | 0 | 270400 | 0 | 52258.329 | 154.1866 | 0
647 | 1 | 0 | 0 | 0.06816 | 2.7877 | 0 | 0 | 0 | 0 | 2.7877 | 0 | 270400 | 0 | 52258.329 | 156.603 | 0
648 | 1 | 0 | 0 | 0.076806 | 3.1414 | 0 | 0 | 0 | 0 | 3.1414 | 0 | 270400 | 0 | 52258.329 | 159.326 | 0
649 | 1 | 0 | 0 | 0.057739 | 2.3615 | 0 | 0 | 0 | 0 | 2.3615 | 0 | 270400 | 0 | 52258.329 | 161.3729 | 0
650 | 1 | 0 | 0 | 0.053212 | 2.1764 | 0 | 0 | 0 | 0 | 2.1764 | 0 | 270400 | 0 | 52258.329 | 163.2594 | 0
651 | 1 | 0 | 0 | 0.073323 | 2.9989 | 0 | 0 | 0 | 0 | 2.9989 | 0 | 270400 | 0 | 52258.329 | 165.8589 | 0
652 | 1 | 0 | 0 | 0.087236 | 3.568 | 0 | 0 | 0 | 0 | 3.568 | 0 | 270400 | 0 | 52258.329 | 168.9516 | 0
653 | 1 | 0 | 0 | 0.12937 | 5.291 | 0 | 0 | 0 | 0 | 5.291 | 0 | 270400 | 0 | 52258.329 | 173.5378 | 0
654 | 1 | 0 | 0 | 0.11659 | 4.7685 | 0 | 0 | 0 | 0 | 4.7685 | 0 | 270400 | 0 | 52258.329 | 177.6712 | 0
655 | 1 | 0 | 0 | 0.091646 | 3.7483 | 0 | 0 | 0 | 0 | 3.7483 | 0 | 270400 | 0 | 52258.329 | 180.9202 | 0
656 | 1 | 1 | 0.05973 | 0.12205 | 22.2417 | 200 | 22.2417 | 177.7583 | 200 | 0 | 0 | 270200 | 200 | 52458.329 | 3.1619 | 0
657 | 1 | 1 | 0.31312 | 0.12942 | 95.7223 | 200 | 95.7223 | 3.1619 | 98.8842 | 0 | 0 | 270000 | 98.8842 | 52557.2132 | 0 | 0
658 | 1 | 0 | 0.602 | 0.13056 | 179.1971 | 0 | 0 | 0 | 0 | 179.1971 | 0 | 270000 | 0 | 52557.2132 | 155.328 | 0
659 | 1 | 0 | 0.85768 | 0.19536 | 255.6872 | 0 | 0 | 0 | 0 | 180 | 75.6872 | 270000 | 75.6872 | 52632.9004 | 311.352 | 0
660 | 1 | 0 | 1 | 0.17779 | 296.0716 | 0 | 0 | 0 | 0 | 180 | 116.0716 | 270000 | 116.0716 | 52748.972 | 467.376 | 0
661 | 1 | 0 | 1 | 0.17292 | 295.8724 | 0 | 0 | 0 | 0 | 50.1084 | 200 | 270000 | 200 | 52948.972 | 510.81 | 45.7639
662 | 1 | 0 | 1 | 0.15678 | 295.2122 | 0 | 0 | 0 | 0 | 0 | 200 | 270000 | 200 | 53148.972 | 510.81 | 95.2122
663 | 1 | 0 | 0.85768 | 0.17362 | 254.7983 | 0 | 0 | 0 | 0 | 0 | 200 | 270000 | 200 | 53348.972 | 510.81 | 54.7983
664 | 1 | 0 | 0.602 | 0.16746 | 180.7063 | 0 | 0 | 0 | 0 | 0 | 180.7063 | 270000 | 180.7063 | 53529.6783 | 510.81 | 0
665 | 1 | 0 | 0.31312 | 0.14917 | 96.5302 | 0 | 0 | 0 | 0 | 0 | 96.5302 | 270000 | 96.5302 | 53626.2085 | 510.81 | 0
666 | 1 | 0 | 0.05973 | 0.15974 | 23.7834 | 0 | 0 | 0 | 0 | 0 | 23.7834 | 270000 | 23.7834 | 53649.992 | 510.81 | 0
667 | 1 | 0 | 0 | 0.23667 | 9.68 | 0 | 0 | 0 | 0 | 0 | 9.68 | 270000 | 9.68 | 53659.672 | 510.81 | 0
668 | 1 | 1 | 0 | 0.15385 | 6.2924 | 200 | 6.2924 | 180 | 186.2924 | 0 | 0 | 269800 | 186.2924 | 53845.9644 | 330.81 | 0
669 | 1 | 1 | 0 | 0.13523 | 5.531 | 200 | 5.531 | 180 | 185.531 | 0 | 0 | 269600 | 185.531 | 54031.4954 | 150.81 | 0
670 | 1 | 0 | 0 | 0.12254 | 5.0117 | 0 | 0 | 0 | 0 | 5.0117 | 0 | 269600 | 0 | 54031.4954 | 155.1541 | 0
671 | 1 | 0 | 0 | 0.072461 | 2.9637 | 0 | 0 | 0 | 0 | 2.9637 | 0 | 269600 | 0 | 54031.4954 | 157.723 | 0
672 | 1 | 0 | 0 | 0.11133 | 4.5533 | 0 | 0 | 0 | 0 | 4.5533 | 0 | 269600 | 0 | 54031.4954 | 161.6698 | 0
673 | 1 | 0 | 0 | 0.11386 | 4.657 | 0 | 0 | 0 | 0 | 4.657 | 0 | 269600 | 0 | 54031.4954 | 165.7066 | 0
674 | 1 | 0 | 0 | 0.12718 | 5.2016 | 0 | 0 | 0 | 0 | 5.2016 | 0 | 269600 | 0 | 54031.4954 | 170.2153 | 0
675 | 1 | 0 | 0 | 0.16676 | 6.8206 | 0 | 0 | 0 | 0 | 6.8206 | 0 | 269600 | 0 | 54031.4954 | 176.1274 | 0
676 | 1 | 0 | 0 | 0.17387 | 7.1114 | 0 | 0 | 0 | 0 | 7.1114 | 0 | 269600 | 0 | 54031.4954 | 182.2915 | 0
677 | 1 | 0 | 0 | 0.25121 | 10.2744 | 0 | 0 | 0 | 0 | 10.2744 | 0 | 269600 | 0 | 54031.4954 | 191.1973 | 0
678 | 1 | 0 | 0 | 0.20423 | 8.3529 | 0 | 0 | 0 | 0 | 8.3529 | 0 | 269600 | 0 | 54031.4954 | 198.4377 | 0
679 | 1 | 0 | 0 | 0.23009 | 9.4107 | 0 | 0 | 0 | 0 | 9.4107 | 0 | 269600 | 0 | 54031.4954 | 206.5949 | 0
680 | 1 | 1 | 0.062363 | 0.33428 | 31.6824 | 200 | 31.6824 | 168.3176 | 200 | 0 | 0 | 269400 | 200 | 54231.4954 | 38.2772 | 0
681 | 1 | 1 | 0.32693 | 0.3271 | 107.7945 | 200 | 107.7945 | 38.2772 | 146.0717 | 0 | 0 | 269200 | 146.0717 | 54377.5671 | 0 | 0
682 | 1 | 0 | 0.62854 | 0.25566 | 191.9787 | 0 | 0 | 0 | 0 | 180 | 11.9787 | 269200 | 11.9787 | 54389.5458 | 156.024 | 0
683 | 1 | 0 | 0.89549 | 0.31147 | 271.3565 | 0 | 0 | 0 | 0 | 180 | 91.3565 | 269200 | 91.3565 | 54480.9023 | 312.048 | 0
684 | 1 | 0 | 1 | 0.28284 | 300.368 | 0 | 0 | 0 | 0 | 180 | 120.368 | 269200 | 120.368 | 54601.2702 | 468.072 | 0
685 | 1 | 0 | 1 | 0.22047 | 297.8173 | 0 | 0 | 0 | 0 | 49.3055 | 200 | 269200 | 200 | 54801.2702 | 510.81 | 48.5118
686 | 1 | 0 | 1 | 0.22386 | 297.9558 | 0 | 0 | 0 | 0 | 0 | 200 | 269200 | 200 | 55001.2702 | 510.81 | 97.9558
687 | 1 | 0 | 0.89549 | 0.37275 | 273.8628 | 0 | 0 | 0 | 0 | 0 | 200 | 269200 | 200 | 55201.2702 | 510.81 | 73.8628
688 | 1 | 0 | 0.62854 | 0.59899 | 206.0209 | 0 | 0 | 0 | 0 | 0 | 200 | 269200 | 200 | 55401.2702 | 510.81 | 6.0209
689 | 1 | 0 | 0.32693 | 0.62133 | 119.8285 | 0 | 0 | 0 | 0 | 0 | 119.8285 | 269200 | 119.8285 | 55521.0987 | 510.81 | 0
690 | 1 | 0 | 0.062363 | 0.96329 | 57.409 | 0 | 0 | 0 | 0 | 0 | 57.409 | 269200 | 57.409 | 55578.5078 | 510.81 | 0
691 | 1 | 0 | 0 | 0.43224 | 17.6786 | 0 | 0 | 0 | 0 | 0 | 17.6786 | 269200 | 17.6786 | 55596.1863 | 510.81 | 0
692 | 1 | 1 | 0 | 0.3614 | 14.7811 | 200 | 14.7811 | 180 | 194.7811 | 0 | 0 | 269000 | 194.7811 | 55790.9674 | 330.81 | 0
693 | 1 | 1 | 0 | 0.4506 | 18.4297 | 200 | 18.4297 | 180 | 198.4297 | 0 | 0 | 268800 | 198.4297 | 55989.3971 | 150.81 | 0
694 | 1 | 0 | 0 | 0.45665 | 18.6768 | 0 | 0 | 0 | 0 | 18.6768 | 0 | 268800 | 0 | 55989.3971 | 166.999 | 0
695 | 1 | 0 | 0 | 0.43221 | 17.6775 | 0 | 0 | 0 | 0 | 17.6775 | 0 | 268800 | 0 | 55989.3971 | 182.3219 | 0
696 | 1 | 0 | 0 | 0.40458 | 16.5471 | 0 | 0 | 0 | 0 | 16.5471 | 0 | 268800 | 0 | 55989.3971 | 196.6649 | 0
697 | 1 | 0 | 0 | 0.2983 | 12.2006 | 0 | 0 | 0 | 0 | 12.2006 | 0 | 268800 | 0 | 55989.3971 | 207.2403 | 0
698 | 1 | 0 | 0 | 0.2196 | 8.9818 | 0 | 0 | 0 | 0 | 8.9818 | 0 | 268800 | 0 | 55989.3971 | 215.0258 | 0
699 | 1 | 0 | 0 | 0.32487 | 13.2873 | 0 | 0 | 0 | 0 | 13.2873 | 0 | 268800 | 0 | 55989.3971 | 226.5433 | 0
700 | 1 | 0 | 0 | 0.29948 | 12.2487 | 0 | 0 | 0 | 0 | 12.2487 | 0 | 268800 | 0 | 55989.3971 | 237.1604 | 0
701 | 1 | 0 | 0 | 0.31636 | 12.9391 | 0 | 0 | 0 | 0 | 12.9391 | 0 | 268800 | 0 | 55989.3971 | 248.376 | 0
702 | 1 | 0 | 0 | 0.20456 | 8.3665 | 0 | 0 | 0 | 0 | 8.3665 | 0 | 268800 | 0 | 55989.3971 | 255.6281 | 0
703 | 1 | 0 | 0 | 0.24004 | 9.8178 | 0 | 0 | 0 | 0 | 9.8178 | 0 | 268800 | 0 | 55989.3971 | 264.1382 | 0
704 | 1 | 1 | 0.065221 | 0.23413 | 28.4119 | 200 | 28.4119 | 171.5881 | 200 | 0 | 0 | 268600 | 200 | 56189.3971 | 92.5501 | 0
705 | 1 | 1 | 0.34191 | 0.22545 | 107.9636 | 200 | 107.9636 | 92.0364 | 200 | 0 | 0 | 268400 | 200 | 56389.3971 | 0.51371 | 0
706 | 1 | 0 | 0.65734 | 0.31522 | 202.7333 | 0 | 0 | 0 | 0 | 180 | 22.7333 | 268400 | 22.7333 | 56412.1303 | 156.5377 | 0
707 | 1 | 0 | 0.93653 | 0.45406 | 289.04 | 0 | 0 | 0 | 0 | 180 | 109.04 | 268400 | 109.04 | 56521.1703 | 312.5617 | 0
708 | 1 | 0 | 1 | 0.51303 | 309.7831 | 0 | 0 | 0 | 0 | 180 | 129.7831 | 268400 | 129.7831 | 56650.9534 | 468.5857 | 0
709 | 1 | 0 | 1 | 0.4951 | 309.0495 | 0 | 0 | 0 | 0 | 48.7128 | 200 | 268400 | 200 | 56850.9534 | 510.81 | 60.3367
710 | 1 | 0 | 1 | 0.27737 | 300.1443 | 0 | 0 | 0 | 0 | 0 | 200 | 268400 | 200 | 57050.9534 | 510.81 | 100.1443
711 | 1 | 0 | 0.93653 | 0.38904 | 286.3806 | 0 | 0 | 0 | 0 | 0 | 200 | 268400 | 200 | 57250.9534 | 510.81 | 86.3806
712 | 1 | 0 | 0.65734 | 0.69904 | 218.4317 | 0 | 0 | 0 | 0 | 0 | 200 | 268400 | 200 | 57450.9534 | 510.81 | 18.4317
713 | 1 | 0 | 0.34191 | 0.69283 | 127.0797 | 0 | 0 | 0 | 0 | 0 | 127.0797 | 268400 | 127.0797 | 57578.0331 | 510.81 | 0
714 | 1 | 0 | 0.065221 | 0.66405 | 45.9955 | 0 | 0 | 0 | 0 | 0 | 45.9955 | 268400 | 45.9955 | 57624.0286 | 510.81 | 0
715 | 1 | 0 | 0 | 0.65357 | 26.7309 | 0 | 0 | 0 | 0 | 0 | 26.7309 | 268400 | 26.7309 | 57650.7594 | 510.81 | 0
716 | 1 | 1 | 0 | 0.66808 | 27.3246 | 200 | 27.3246 | 172.6754 | 200 | 0 | 0 | 268200 | 200 | 57850.7594 | 338.1346 | 0
717 | 1 | 1 | 0 | 0.68797 | 28.1379 | 200 | 28.1379 | 171.8621 | 200 | 0 | 0 | 268000 | 200 | 58050.7594 | 166.2724 | 0
718 | 1 | 0 | 0 | 0.83296 | 34.0682 | 0 | 0 | 0 | 0 | 34.0682 | 0 | 268000 | 0 | 58050.7594 | 195.8027 | 0
719 | 1 | 0 | 0 | 0.73847 | 30.2035 | 0 | 0 | 0 | 0 | 30.2035 | 0 | 268000 | 0 | 58050.7594 | 221.9831 | 0
720 | 1 | 0 | 0 | 0.46659 | 19.0835 | 0 | 0 | 0 | 0 | 19.0835 | 0 | 268000 | 0 | 58050.7594 | 238.5246 | 0
721 | 1 | 0 | 0 | 0.5836 | 23.8692 | 0 | 0 | 0 | 0 | 23.8692 | 0 | 268000 | 0 | 58050.7594 | 259.2145 | 0
722 | 1 | 0 | 0 | 0.32635 | 13.3478 | 0 | 0 | 0 | 0 | 13.3478 | 0 | 268000 | 0 | 58050.7594 | 270.7843 | 0
723 | 1 | 0 | 0 | 0.26461 | 10.8226 | 0 | 0 | 0 | 0 | 10.8226 | 0 | 268000 | 0 | 58050.7594 | 280.1653 | 0
724 | 1 | 0 | 0 | 0.36761 | 15.0352 | 0 | 0 | 0 | 0 | 15.0352 | 0 | 268000 | 0 | 58050.7594 | 293.1978 | 0
725 | 1 | 0 | 0 | 0.20954 | 8.5701 | 0 | 0 | 0 | 0 | 8.5701 | 0 | 268000 | 0 | 58050.7594 | 300.6264 | 0
726 | 1 | 0 | 0 | 0.16385 | 6.7014 | 0 | 0 | 0 | 0 | 6.7014 | 0 | 268000 | 0 | 58050.7594 | 306.4352 | 0
727 | 1 | 0 | 0 | 0.1528 | 6.2496 | 0 | 0 | 0 | 0 | 6.2496 | 0 | 268000 | 0 | 58050.7594 | 311.8524 | 0
728 | 1 | 1 | 0.073678 | 0.13934 | 26.9773 | 200 | 26.9773 | 173.0227 | 200 | 0 | 0 | 267800 | 200 | 58250.7594 | 138.8297 | 0
729 | 1 | 1 | 0.38624 | 0.1367 | 117.1375 | 200 | 117.1375 | 82.8625 | 200 | 0 | 0 | 267600 | 200 | 58450.7594 | 55.9672 | 0
730 | 1 | 0 | 0.74258 | 0.12791 | 219.6886 | 0 | 0 | 0 | 0 | 180 | 39.6886 | 267600 | 39.6886 | 58490.4481 | 211.9912 | 0
731 | 1 | 0 | 1 | 0.12547 | 293.9316 | 0 | 0 | 0 | 0 | 180 | 113.9316 | 267600 | 113.9316 | 58604.3796 | 368.0152 | 0
732 | 1 | 0 | 1 | 0.12705 | 293.9963 | 0 | 0 | 0 | 0 | 164.7379 | 129.2585 | 267600 | 129.2585 | 58733.6381 | 510.81 | 0
733 | 1 | 0 | 1 | 0.12114 | 293.7547 | 0 | 0 | 0 | 0 | 0 | 200 | 267600 | 200 | 58933.6381 | 510.81 | 93.7547
734 | 1 | 0 | 1 | 0.15749 | 295.2412 | 0 | 0 | 0 | 0 | 0 | 200 | 267600 | 200 | 59133.6381 | 510.81 | 95.2412
735 | 1 | 0 | 1 | 0.18107 | 296.2057 | 0 | 0 | 0 | 0 | 0 | 200 | 267600 | 200 | 59333.6381 | 510.81 | 96.2057
736 | 1 | 0 | 0.74258 | 0.18049 | 221.8389 | 0 | 0 | 0 | 0 | 0 | 200 | 267600 | 200 | 59533.6381 | 510.81 | 21.8389
737 | 1 | 0 | 0.38624 | 0.12436 | 116.6329 | 0 | 0 | 0 | 0 | 0 | 116.6329 | 267600 | 116.6329 | 59650.271 | 510.81 | 0
738 | 1 | 0 | 0.073678 | 0.10977 | 25.7679 | 0 | 0 | 0 | 0 | 0 | 25.7679 | 267600 | 25.7679 | 59676.0389 | 510.81 | 0
739 | 1 | 0 | 0 | 0.099774 | 4.0808 | 0 | 0 | 0 | 0 | 0 | 4.0808 | 267600 | 4.0808 | 59680.1197 | 510.81 | 0
740 | 1 | 1 | 0 | 0.11112 | 4.5446 | 200 | 4.5446 | 180 | 184.5446 | 0 | 0 | 267400 | 184.5446 | 59864.6643 | 330.81 | 0
741 | 1 | 1 | 0 | 0.10784 | 4.4106 | 200 | 4.4106 | 180 | 184.4106 | 0 | 0 | 267200 | 184.4106 | 60049.0749 | 150.81 | 0
742 | 1 | 0 | 0 | 0.092034 | 3.7642 | 0 | 0 | 0 | 0 | 3.7642 | 0 | 267200 | 0 | 60049.0749 | 154.0728 | 0
743 | 1 | 0 | 0 | 0.12437 | 5.0869 | 0 | 0 | 0 | 0 | 5.0869 | 0 | 267200 | 0 | 60049.0749 | 158.4821 | 0
744 | 1 | 0 | 0 | 0.08377 | 3.4262 | 0 | 0 | 0 | 0 | 3.4262 | 0 | 267200 | 0 | 60049.0749 | 161.4519 | 0
745 | 2 | 0 | 0 | 0.12216 | 4.9964 | 0 | 0 | 0 | 0 | 4.9964 | 0 | 267200 | 0 | 60049.0749 | 165.7828 | 0
746 | 2 | 0 | 0 | 0.14484 | 5.9238 | 0 | 0 | 0 | 0 | 5.9238 | 0 | 267200 | 0 | 60049.0749 | 170.9176 | 0
747 | 2 | 0 | 0 | 0.11342 | 4.6389 | 0 | 0 | 0 | 0 | 4.6389 | 0 | 267200 | 0 | 60049.0749 | 174.9386 | 0
748 | 2 | 0 | 0 | 0.1432 | 5.8567 | 0 | 0 | 0 | 0 | 5.8567 | 0 | 267200 | 0 | 60049.0749 | 180.0152 | 0
749 | 2 | 0 | 0 | 0.12882 | 5.2689 | 0 | 0 | 0 | 0 | 5.2689 | 0 | 267200 | 0 | 60049.0749 | 184.5823 | 0
750 | 2 | 0 | 0 | 0.12436 | 5.0863 | 0 | 0 | 0 | 0 | 5.0863 | 0 | 267200 | 0 | 60049.0749 | 188.9911 | 0
751 | 2 | 0 | 0 | 0.083123 | 3.3997 | 0 | 0 | 0 | 0 | 3.3997 | 0 | 267200 | 0 | 60049.0749 | 191.938 | 0
752 | 2 | 1 | 0.12018 | 0.082983 | 38.1014 | 200 | 38.1014 | 161.8986 | 200 | 0 | 0 | 267000 | 200 | 60249.0749 | 30.0394 | 0
753 | 2 | 1 | 0.40596 | 0.080053 | 120.5151 | 200 | 120.5151 | 30.0394 | 150.5545 | 0 | 0 | 266800 | 150.5545 | 60399.6294 | 0 | 0
754 | 2 | 0 | 0.71275 | 0.1792 | 213.1709 | 0 | 0 | 0 | 0 | 180 | 33.1709 | 266800 | 33.1709 | 60432.8003 | 156.024 | 0
755 | 2 | 0 | 0.97805 | 0.16123 | 289.0558 | 0 | 0 | 0 | 0 | 180 | 109.0558 | 266800 | 109.0558 | 60541.856 | 312.048 | 0
756 | 2 | 0 | 1 | 0.15419 | 295.1065 | 0 | 0 | 0 | 0 | 180 | 115.1065 | 266800 | 115.1065 | 60656.9625 | 468.072 | 0
757 | 2 | 0 | 1 | 0.14053 | 294.5476 | 0 | 0 | 0 | 0 | 49.3055 | 200 | 266800 | 200 | 60856.9625 | 510.81 | 45.2421
758 | 2 | 0 | 1 | 0.12345 | 293.8491 | 0 | 0 | 0 | 0 | 0 | 200 | 266800 | 200 | 61056.9625 | 510.81 | 93.8491
759 | 2 | 0 | 0.97805 | 0.14597 | 288.4317 | 0 | 0 | 0 | 0 | 0 | 200 | 266800 | 200 | 61256.9625 | 510.81 | 88.4317
760 | 2 | 0 | 0.71275 | 0.1665 | 212.6516 | 0 | 0 | 0 | 0 | 0 | 200 | 266800 | 200 | 61456.9625 | 510.81 | 12.6516
761 | 2 | 0 | 0.40596 | 0.1579 | 123.6993 | 0 | 0 | 0 | 0 | 0 | 123.6993 | 266800 | 123.6993 | 61580.6618 | 510.81 | 0
762 | 2 | 0 | 0.12018 | 0.1806 | 42.094 | 0 | 0 | 0 | 0 | 0 | 42.094 | 266800 | 42.094 | 61622.7558 | 510.81 | 0
763 | 2 | 0 | 0 | 0.19544 | 7.9933 | 0 | 0 | 0 | 0 | 0 | 7.9933 | 266800 | 7.9933 | 61630.7491 | 510.81 | 0
764 | 2 | 1 | 0 | 0.23635 | 9.6666 | 200 | 9.6666 | 180 | 189.6666 | 0 | 0 | 266600 | 189.6666 | 61820.4158 | 330.81 | 0
765 | 2 | 1 | 0 | 0.27064 | 11.0692 | 200 | 11.0692 | 180 | 191.0692 | 0 | 0 | 266400 | 191.0692 | 62011.4849 | 150.81 | 0
766 | 2 | 0 | 0 | 0.21073 | 8.619 | 0 | 0 | 0 | 0 | 8.619 | 0 | 266400 | 0 | 62011.4849 | 158.281 | 0
767 | 2 | 0 | 0 | 0.23698 | 9.6924 | 0 | 0 | 0 | 0 | 9.6924 | 0 | 266400 | 0 | 62011.4849 | 166.6823 | 0
768 | 2 | 0 | 0 | 0.10884 | 4.4518 | 0 | 0 | 0 | 0 | 4.4518 | 0 | 266400 | 0 | 62011.4849 | 170.5411 | 0
769 | 2 | 0 | 0 | 0.10917 | 4.4649 | 0 | 0 | 0 | 0 | 4.4649 | 0 | 266400 | 0 | 62011.4849 | 174.4113 | 0
770 | 2 | 0 | 0 | 0.17378 | 7.1074 | 0 | 0 | 0 | 0 | 7.1074 | 0 | 266400 | 0 | 62011.4849 | 180.5721 | 0
771 | 2 | 0 | 0 | 0.19392 | 7.9315 | 0 | 0 | 0 | 0 | 7.9315 | 0 | 266400 | 0 | 62011.4849 | 187.447 | 0
772 | 2 | 0 | 0 | 0.25042 | 10.2423 | 0 | 0 | 0 | 0 | 10.2423 | 0 | 266400 | 0 | 62011.4849 | 196.3251 | 0
773 | 2 | 0 | 0 | 0.29464 | 12.0507 | 0 | 0 | 0 | 0 | 12.0507 | 0 | 266400 | 0 | 62011.4849 | 206.7706 | 0
774 | 2 | 0 | 0 | 0.15758 | 6.445 | 0 | 0 | 0 | 0 | 6.445 | 0 | 266400 | 0 | 62011.4849 | 212.3571 | 0
775 | 2 | 0 | 0 | 0.12283 | 5.0235 | 0 | 0 | 0 | 0 | 5.0235 | 0 | 266400 | 0 | 62011.4849 | 216.7116 | 0
776 | 2 | 1 | 0.1596 | 0.19471 | 54.0571 | 200 | 54.0571 | 145.9429 | 200 | 0 | 0 | 266200 | 200 | 62211.4849 | 70.7687 | 0
777 | 2 | 1 | 0.53914 | 0.20403 | 164.0471 | 200 | 164.0471 | 35.9529 | 200 | 0 | 0 | 266000 | 200 | 62411.4849 | 34.8158 | 0
778 | 2 | 0 | 0.94657 | 0.23896 | 283.1419 | 0 | 0 | 0 | 0 | 180 | 103.1419 | 266000 | 103.1419 | 62514.6268 | 190.8398 | 0
779 | 2 | 0 | 1 | 0.24695 | 298.9001 | 0 | 0 | 0 | 0 | 180 | 118.9001 | 266000 | 118.9001 | 62633.5269 | 346.8638 | 0
780 | 2 | 0 | 1 | 0.19361 | 296.7185 | 0 | 0 | 0 | 0 | 180 | 116.7185 | 266000 | 116.7185 | 62750.2454 | 502.8878 | 0
781 | 2 | 0 | 1 | 0.2516 | 299.0904 | 0 | 0 | 0 | 0 | 9.1396 | 200 | 266000 | 200 | 62950.2454 | 510.81 | 89.9508
782 | 2 | 0 | 1 | 0.21853 | 297.7377 | 0 | 0 | 0 | 0 | 0 | 200 | 266000 | 200 | 63150.2454 | 510.81 | 97.7377
783 | 2 | 0 | 1 | 0.17453 | 295.9382 | 0 | 0 | 0 | 0 | 0 | 200 | 266000 | 200 | 63350.2454 | 510.81 | 95.9382
784 | 2 | 0 | 0.94657 | 0.1782 | 280.6566 | 0 | 0 | 0 | 0 | 0 | 200 | 266000 | 200 | 63550.2454 | 510.81 | 80.6566
785 | 2 | 0 | 0.53914 | 0.19916 | 163.848 | 0 | 0 | 0 | 0 | 0 | 163.848 | 266000 | 163.848 | 63714.0934 | 510.81 | 0
786 | 2 | 0 | 0.1596 | 0.26346 | 56.8688 | 0 | 0 | 0 | 0 | 0 | 56.8688 | 266000 | 56.8688 | 63770.9623 | 510.81 | 0
787 | 2 | 0 | 0 | 0.17739 | 7.2553 | 0 | 0 | 0 | 0 | 0 | 7.2553 | 266000 | 7.2553 | 63778.2175 | 510.81 | 0
788 | 2 | 1 | 0 | 0.14461 | 5.9148 | 200 | 5.9148 | 180 | 185.9148 | 0 | 0 | 265800 | 185.9148 | 63964.1323 | 330.81 | 0
789 | 2 | 1 | 0 | 0.17631 | 7.2112 | 200 | 7.2112 | 180 | 187.2112 | 0 | 0 | 265600 | 187.2112 | 64151.3435 | 150.81 | 0
790 | 2 | 0 | 0 | 0.16101 | 6.5853 | 0 | 0 | 0 | 0 | 6.5853 | 0 | 265600 | 0 | 64151.3435 | 156.5181 | 0
791 | 2 | 0 | 0 | 0.12044 | 4.926 | 0 | 0 | 0 | 0 | 4.926 | 0 | 265600 | 0 | 64151.3435 | 160.788 | 0
792 | 2 | 0 | 0 | 0.13498 | 5.5209 | 0 | 0 | 0 | 0 | 5.5209 | 0 | 265600 | 0 | 64151.3435 | 165.5735 | 0
793 | 2 | 0 | 0 | 0.15066 | 6.1618 | 0 | 0 | 0 | 0 | 6.1618 | 0 | 265600 | 0 | 64151.3435 | 170.9146 | 0
794 | 2 | 0 | 0 | 0.19994 | 8.1773 | 0 | 0 | 0 | 0 | 8.1773 | 0 | 265600 | 0 | 64151.3435 | 178.0027 | 0
795 | 2 | 0 | 0 | 0.20885 | 8.5418 | 0 | 0 | 0 | 0 | 8.5418 | 0 | 265600 | 0 | 64151.3435 | 185.4067 | 0
796 | 2 | 0 | 0 | 0.22211 | 9.0843 | 0 | 0 | 0 | 0 | 9.0843 | 0 | 265600 | 0 | 64151.3435 | 193.281 | 0
797 | 2 | 0 | 0 | 0.21694 | 8.873 | 0 | 0 | 0 | 0 | 8.873 | 0 | 265600 | 0 | 64151.3435 | 200.9721 | 0
798 | 2 | 0 | 0 | 0.20295 | 8.3007 | 0 | 0 | 0 | 0 | 8.3007 | 0 | 265600 | 0 | 64151.3435 | 208.1671 | 0
799 | 2 | 0 | 0 | 0.17462 | 7.1419 | 0 | 0 | 0 | 0 | 7.1419 | 0 | 265600 | 0 | 64151.3435 | 214.3577 | 0
800 | 2 | 1 | 0.11848 | 0.099631 | 38.2922 | 200 | 38.2922 | 161.7078 | 200 | 0 | 0 | 265400 | 200 | 64351.3435 | 52.6499 | 0
801 | 2 | 1 | 0.40022 | 0.12595 | 120.7363 | 200 | 120.7363 | 52.6499 | 173.3862 | 0 | 0 | 265200 | 173.3862 | 64524.7297 | 0 | 0
802 | 2 | 0 | 0.70268 | 0.17374 | 210.0398 | 0 | 0 | 0 | 0 | 180 | 30.0398 | 265200 | 30.0398 | 64554.7695 | 156.024 | 0
803 | 2 | 0 | 0.96424 | 0.28184 | 289.9988 | 0 | 0 | 0 | 0 | 180 | 109.9988 | 265200 | 109.9988 | 64664.7683 | 312.048 | 0
804 | 2 | 0 | 1 | 0.28343 | 300.3923 | 0 | 0 | 0 | 0 | 180 | 120.3923 | 265200 | 120.3923 | 64785.1606 | 468.072 | 0
805 | 2 | 0 | 1 | 0.22949 | 298.1862 | 0 | 0 | 0 | 0 | 49.3055 | 200 | 265200 | 200 | 64985.1606 | 510.81 | 48.8807
806 | 2 | 0 | 1 | 0.16114 | 295.3905 | 0 | 0 | 0 | 0 | 0 | 200 | 265200 | 200 | 65185.1606 | 510.81 | 95.3905
807 | 2 | 0 | 0.96424 | 0.20561 | 286.881 | 0 | 0 | 0 | 0 | 0 | 200 | 265200 | 200 | 65385.1606 | 510.81 | 86.881
808 | 2 | 0 | 0.70268 | 0.19465 | 210.895 | 0 | 0 | 0 | 0 | 0 | 200 | 265200 | 200 | 65585.1606 | 510.81 | 10.895
809 | 2 | 0 | 0.40022 | 0.27529 | 126.8443 | 0 | 0 | 0 | 0 | 0 | 126.8443 | 265200 | 126.8443 | 65712.005 | 510.81 | 0
810 | 2 | 0 | 0.11848 | 0.23895 | 43.9902 | 0 | 0 | 0 | 0 | 0 | 43.9902 | 265200 | 43.9902 | 65755.9952 | 510.81 | 0
811 | 2 | 0 | 0 | 0.23681 | 9.6854 | 0 | 0 | 0 | 0 | 0 | 9.6854 | 265200 | 9.6854 | 65765.6806 | 510.81 | 0
812 | 2 | 1 | 0 | 0.16221 | 6.6344 | 200 | 6.6344 | 180 | 186.6344 | 0 | 0 | 265000 | 186.6344 | 65952.315 | 330.81 | 0
813 | 2 | 1 | 0 | 0.18733 | 7.6619 | 200 | 7.6619 | 180 | 187.6619 | 0 | 0 | 264800 | 187.6619 | 66139.9769 | 150.81 | 0
814 | 2 | 0 | 0 | 0.18909 | 7.7336 | 0 | 0 | 0 | 0 | 7.7336 | 0 | 264800 | 0 | 66139.9769 | 157.5135 | 0
815 | 2 | 0 | 0 | 0.086325 | 3.5307 | 0 | 0 | 0 | 0 | 3.5307 | 0 | 264800 | 0 | 66139.9769 | 160.5739 | 0
816 | 2 | 0 | 0 | 0.10587 | 4.3302 | 0 | 0 | 0 | 0 | 4.3302 | 0 | 264800 | 0 | 66139.9769 | 164.3273 | 0
817 | 2 | 0 | 0 | 0.096006 | 3.9266 | 0 | 0 | 0 | 0 | 3.9266 | 0 | 264800 | 0 | 66139.9769 | 167.7309 | 0
818 | 2 | 0 | 0 | 0.11332 | 4.6349 | 0 | 0 | 0 | 0 | 4.6349 | 0 | 264800 | 0 | 66139.9769 | 171.7484 | 0
819 | 2 | 0 | 0 | 0.10711 | 4.3807 | 0 | 0 | 0 | 0 | 4.3807 | 0 | 264800 | 0 | 66139.9769 | 175.5456 | 0
820 | 2 | 0 | 0 | 0.11039 | 4.5151 | 0 | 0 | 0 | 0 | 4.5151 | 0 | 264800 | 0 | 66139.9769 | 179.4593 | 0
821 | 2 | 0 | 0 | 0.13046 | 5.3358 | 0 | 0 | 0 | 0 | 5.3358 | 0 | 264800 | 0 | 66139.9769 | 184.0843 | 0
822 | 2 | 0 | 0 | 0.13161 | 5.3828 | 0 | 0 | 0 | 0 | 5.3828 | 0 | 264800 | 0 | 66139.9769 | 188.7502 | 0
823 | 2 | 0 | 0 | 0.17084 | 6.9876 | 0 | 0 | 0 | 0 | 6.9876 | 0 | 264800 | 0 | 66139.9769 | 194.807 | 0
824 | 2 | 1 | 0.13637 | 0.2215 | 48.4432 | 200 | 48.4432 | 151.5568 | 200 | 0 | 0 | 264600 | 200 | 66339.9769 | 43.2502 | 0
825 | 2 | 1 | 0.46066 | 0.1956 | 141.038 | 200 | 141.038 | 43.2502 | 184.2882 | 0 | 0 | 264400 | 184.2882 | 66524.2651 | 0 | 0
826 | 2 | 0 | 0.80878 | 0.21304 | 242.2903 | 0 | 0 | 0 | 0 | 180 | 62.2903 | 264400 | 62.2903 | 66586.5554 | 156.024 | 0
827 | 2 | 0 | 1 | 0.13089 | 294.1533 | 0 | 0 | 0 | 0 | 180 | 114.1533 | 264400 | 114.1533 | 66700.7086 | 312.048 | 0
828 | 2 | 0 | 1 | 0.19751 | 296.8781 | 0 | 0 | 0 | 0 | 180 | 116.8781 | 264400 | 116.8781 | 66817.5868 | 468.072 | 0
829 | 2 | 0 | 1 | 0.14009 | 294.5295 | 0 | 0 | 0 | 0 | 49.3055 | 200 | 264400 | 200 | 67017.5868 | 510.81 | 45.224
830 | 2 | 0 | 1 | 0.15231 | 295.0293 | 0 | 0 | 0 | 0 | 0 | 200 | 264400 | 200 | 67217.5868 | 510.81 | 95.0293
831 | 2 | 0 | 1 | 0.17195 | 295.8328 | 0 | 0 | 0 | 0 | 0 | 200 | 264400 | 200 | 67417.5868 | 510.81 | 95.8328
832 | 2 | 0 | 0.80878 | 0.1646 | 240.3089 | 0 | 0 | 0 | 0 | 0 | 200 | 264400 | 200 | 67617.5868 | 510.81 | 40.3089
833 | 2 | 0 | 0.46066 | 0.24415 | 143.0236 | 0 | 0 | 0 | 0 | 0 | 143.0236 | 264400 | 143.0236 | 67760.6104 | 510.81 | 0
834 | 2 | 0 | 0.13637 | 0.18841 | 47.0898 | 0 | 0 | 0 | 0 | 0 | 47.0898 | 264400 | 47.0898 | 67807.7002 | 510.81 | 0
835 | 2 | 0 | 0 | 0.12001 | 4.9086 | 0 | 0 | 0 | 0 | 0 | 4.9086 | 264400 | 4.9086 | 67812.6087 | 510.81 | 0
836 | 2 | 1 | 0 | 0.12535 | 5.1269 | 200 | 5.1269 | 180 | 185.1269 | 0 | 0 | 264200 | 185.1269 | 67997.7356 | 330.81 | 0
837 | 2 | 1 | 0 | 0.23281 | 9.5219 | 200 | 9.5219 | 180 | 189.5219 | 0 | 0 | 264000 | 189.5219 | 68187.2575 | 150.81 | 0
838 | 2 | 0 | 0 | 0.21916 | 8.9637 | 0 | 0 | 0 | 0 | 8.9637 | 0 | 264000 | 0 | 68187.2575 | 158.5797 | 0
839 | 2 | 0 | 0 | 0.26282 | 10.7493 | 0 | 0 | 0 | 0 | 10.7493 | 0 | 264000 | 0 | 68187.2575 | 167.8972 | 0
840 | 2 | 0 | 0 | 0.27763 | 11.3549 | 0 | 0 | 0 | 0 | 11.3549 | 0 | 264000 | 0 | 68187.2575 | 177.7396 | 0
841 | 2 | 0 | 0 | 0.35964 | 14.7093 | 0 | 0 | 0 | 0 | 14.7093 | 0 | 264000 | 0 | 68187.2575 | 190.4897 | 0
842 | 2 | 0 | 0 | 0.298 | 12.1882 | 0 | 0 | 0 | 0 | 12.1882 | 0 | 264000 | 0 | 68187.2575 | 201.0544 | 0
843 | 2 | 0 | 0 | 0.35522 | 14.5284 | 0 | 0 | 0 | 0 | 14.5284 | 0 | 264000 | 0 | 68187.2575 | 213.6477 | 0
844 | 2 | 0 | 0 | 0.37958 | 15.5247 | 0 | 0 | 0 | 0 | 15.5247 | 0 | 264000 | 0 | 68187.2575 | 227.1045 | 0
845 | 2 | 0 | 0 | 0.40196 | 16.4402 | 0 | 0 | 0 | 0 | 16.4402 | 0 | 264000 | 0 | 68187.2575 | 241.3549 | 0
846 | 2 | 0 | 0 | 0.4048 | 16.5562 | 0 | 0 | 0 | 0 | 16.5562 | 0 | 264000 | 0 | 68187.2575 | 255.7057 | 0
847 | 2 | 0 | 0 | 0.43042 | 17.6041 | 0 | 0 | 0 | 0 | 17.6041 | 0 | 264000 | 0 | 68187.2575 | 270.9649 | 0
848 | 2 | 1 | 0.13971 | 0.35015 | 54.6695 | 200 | 54.6695 | 145.3305 | 200 | 0 | 0 | 263800 | 200 | 68387.2575 | 125.6344 | 0
849 | 2 | 1 | 0.47193 | 0.26352 | 147.0729 | 200 | 147.0729 | 52.9271 | 200 | 0 | 0 | 263600 | 200 | 68587.2575 | 72.7073 | 0
850 | 2 | 0 | 0.82858 | 0.30748 | 251.8704 | 0 | 0 | 0 | 0 | 180 | 71.8704 | 263600 | 71.8704 | 68659.1279 | 228.7313 | 0
851 | 2 | 0 | 1 | 0.45263 | 307.3126 | 0 | 0 | 0 | 0 | 180 | 127.3126 | 263600 | 127.3126 | 68786.4405 | 384.7553 | 0
852 | 2 | 0 | 1 | 0.31325 | 301.6119 | 0 | 0 | 0 | 0 | 145.4253 | 156.1865 | 263600 | 156.1865 | 68942.6271 | 510.81 | 0
853 | 2 | 0 | 1 | 0.21338 | 297.5272 | 0 | 0 | 0 | 0 | 0 | 200 | 263600 | 200 | 69142.6271 | 510.81 | 97.5272
854 | 2 | 0 | 1 | 0.15619 | 295.188 | 0 | 0 | 0 | 0 | 0 | 200 | 263600 | 200 | 69342.6271 | 510.81 | 95.188
855 | 2 | 0 | 1 | 0.18973 | 296.5598 | 0 | 0 | 0 | 0 | 0 | 200 | 263600 | 200 | 69542.6271 | 510.81 | 96.5598
856 | 2 | 0 | 0.82858 | 0.31833 | 252.3141 | 0 | 0 | 0 | 0 | 0 | 200 | 263600 | 200 | 69742.6271 | 510.81 | 52.3141
857 | 2 | 0 | 0.47193 | 0.39125 | 152.2967 | 0 | 0 | 0 | 0 | 0 | 152.2967 | 263600 | 152.2967 | 69894.9238 | 510.81 | 0
858 | 2 | 0 | 0.13971 | 0.51494 | 61.4092 | 0 | 0 | 0 | 0 | 0 | 61.4092 | 263600 | 61.4092 | 69956.333 | 510.81 | 0
859 | 2 | 0 | 0 | 0.30064 | 12.2963 | 0 | 0 | 0 | 0 | 0 | 12.2963 | 263600 | 12.2963 | 69968.6292 | 510.81 | 0
860 | 2 | 1 | 0 | 0.35424 | 14.4884 | 200 | 14.4884 | 180 | 194.4884 | 0 | 0 | 263400 | 194.4884 | 70163.1176 | 330.81 | 0
861 | 2 | 1 | 0 | 0.34311 | 14.0331 | 200 | 14.0331 | 180 | 194.0331 | 0 | 0 | 263200 | 194.0331 | 70357.1507 | 150.81 | 0
862 | 2 | 0 | 0 | 0.38895 | 15.9082 | 0 | 0 | 0 | 0 | 15.9082 | 0 | 263200 | 0 | 70357.1507 | 164.5992 | 0
863 | 2 | 0 | 0 | 0.44073 | 18.0259 | 0 | 0 | 0 | 0 | 18.0259 | 0 | 263200 | 0 | 70357.1507 | 180.2241 | 0
864 | 2 | 0 | 0 | 0.4726 | 19.3293 | 0 | 0 | 0 | 0 | 19.3293 | 0 | 263200 | 0 | 70357.1507 | 196.9788 | 0
865 | 2 | 0 | 0 | 0.56684 | 23.1839 | 0 | 0 | 0 | 0 | 23.1839 | 0 | 263200 | 0 | 70357.1507 | 217.0746 | 0
866 | 2 | 0 | 0 | 0.42173 | 17.2486 | 0 | 0 | 0 | 0 | 17.2486 | 0 | 263200 | 0 | 70357.1507 | 232.0256 | 0
867 | 2 | 0 | 0 | 0.32353 | 13.2325 | 0 | 0 | 0 | 0 | 13.2325 | 0 | 263200 | 0 | 70357.1507 | 243.4955 | 0
868 | 2 | 0 | 0 | 0.20874 | 8.5373 | 0 | 0 | 0 | 0 | 8.5373 | 0 | 263200 | 0 | 70357.1507 | 250.8956 | 0
869 | 2 | 0 | 0 | 0.17534 | 7.1713 | 0 | 0 | 0 | 0 | 7.1713 | 0 | 263200 | 0 | 70357.1507 | 257.1117 | 0
870 | 2 | 0 | 0 | 0.26333 | 10.7702 | 0 | 0 | 0 | 0 | 10.7702 | 0 | 263200 | 0 | 70357.1507 | 266.4474 | 0
871 | 2 | 0 | 0 | 0.34081 | 13.9393 | 0 | 0 | 0 | 0 | 13.9393 | 0 | 263200 | 0 | 70357.1507 | 278.5299 | 0
872 | 2 | 1 | 0.13961 | 0.47449 | 59.7265 | 200 | 59.7265 | 140.2735 | 200 | 0 | 0 | 263000 | 200 | 70557.1507 | 138.2565 | 0
873 | 2 | 1 | 0.4716 | 0.43753 | 154.0947 | 200 | 154.0947 | 45.9053 | 200 | 0 | 0 | 262800 | 200 | 70757.1507 | 92.3512 | 0
874 | 2 | 0 | 0.828 | 0.36623 | 254.1059 | 0 | 0 | 0 | 0 | 180 | 74.1059 | 262800 | 74.1059 | 70831.2566 | 248.3752 | 0
875 | 2 | 0 | 1 | 0.35195 | 303.1946 | 0 | 0 | 0 | 0 | 180 | 123.1946 | 262800 | 123.1946 | 70954.4513 | 404.3992 | 0
876 | 2 | 0 | 1 | 0.35929 | 303.4952 | 0 | 0 | 0 | 0 | 122.7629 | 180.7323 | 262800 | 180.7323 | 71135.1836 | 510.81 | 0
877 | 2 | 0 | 1 | 0.35485 | 303.3132 | 0 | 0 | 0 | 0 | 0 | 200 | 262800 | 200 | 71335.1836 | 510.81 | 103.3132
878 | 2 | 0 | 1 | 0.33773 | 302.6133 | 0 | 0 | 0 | 0 | 0 | 200 | 262800 | 200 | 71535.1836 | 510.81 | 102.6133
879 | 2 | 0 | 1 | 0.36565 | 303.7549 | 0 | 0 | 0 | 0 | 0 | 200 | 262800 | 200 | 71735.1836 | 510.81 | 103.7549
880 | 2 | 0 | 0.828 | 0.39576 | 255.3135 | 0 | 0 | 0 | 0 | 0 | 200 | 262800 | 200 | 71935.1836 | 510.81 | 55.3135
881 | 2 | 0 | 0.4716 | 0.37027 | 151.3434 | 0 | 0 | 0 | 0 | 0 | 151.3434 | 262800 | 151.3434 | 72086.527 | 510.81 | 0
882 | 2 | 0 | 0.13961 | 0.35958 | 55.0269 | 0 | 0 | 0 | 0 | 0 | 55.0269 | 262800 | 55.0269 | 72141.5539 | 510.81 | 0
883 | 2 | 0 | 0 | 0.40701 | 16.6466 | 0 | 0 | 0 | 0 | 0 | 16.6466 | 262800 | 16.6466 | 72158.2005 | 510.81 | 0
884 | 2 | 1 | 0 | 0.25953 | 10.6148 | 200 | 10.6148 | 180 | 190.6148 | 0 | 0 | 262600 | 190.6148 | 72348.8153 | 330.81 | 0
885 | 2 | 1 | 0 | 0.25279 | 10.3392 | 200 | 10.3392 | 180 | 190.3392 | 0 | 0 | 262400 | 190.3392 | 72539.1546 | 150.81 | 0
886 | 2 | 0 | 0 | 0.33402 | 13.6615 | 0 | 0 | 0 | 0 | 13.6615 | 0 | 262400 | 0 | 72539.1546 | 162.6518 | 0
887 | 2 | 0 | 0 | 0.30243 | 12.3693 | 0 | 0 | 0 | 0 | 12.3693 | 0 | 262400 | 0 | 72539.1546 | 173.3735 | 0
888 | 2 | 0 | 0 | 0.39251 | 16.0537 | 0 | 0 | 0 | 0 | 16.0537 | 0 | 262400 | 0 | 72539.1546 | 187.2889 | 0
889 | 2 | 0 | 0 | 0.41514 | 16.9794 | 0 | 0 | 0 | 0 | 16.9794 | 0 | 262400 | 0 | 72539.1546 | 202.0067 | 0
890 | 2 | 0 | 0 | 0.6763 | 27.6608 | 0 | 0 | 0 | 0 | 27.6608 | 0 | 262400 | 0 | 72539.1546 | 225.983 | 0
891 | 2 | 0 | 0 | 0.49054 | 20.063 | 0 | 0 | 0 | 0 | 20.063 | 0 | 262400 | 0 | 72539.1546 | 243.3736 | 0
892 | 2 | 0 | 0 | 0.46776 | 19.1312 | 0 | 0 | 0 | 0 | 19.1312 | 0 | 262400 | 0 | 72539.1546 | 259.9566 | 0
893 | 2 | 0 | 0 | 0.50121 | 20.4996 | 0 | 0 | 0 | 0 | 20.4996 | 0 | 262400 | 0 | 72539.1546 | 277.7256 | 0
894 | 2 | 0 | 0 | 0.49909 | 20.4126 | 0 | 0 | 0 | 0 | 20.4126 | 0 | 262400 | 0 | 72539.1546 | 295.4192 | 0
895 | 2 | 0 | 0 | 0.66277 | 27.1075 | 0 | 0 | 0 | 0 | 27.1075 | 0 | 262400 | 0 | 72539.1546 | 318.916 | 0
896 | 2 | 1 | 0.13867 | 0.67163 | 67.5181 | 200 | 67.5181 | 132.4819 | 200 | 0 | 0 | 262200 | 200 | 72739.1546 | 186.434 | 0
897 | 2 | 1 | 0.46842 | 0.60436 | 159.9994 | 200 | 159.9994 | 40.0006 | 200 | 0 | 0 | 262000 | 200 | 72939.1546 | 146.4334 | 0
898 | 2 | 0 | 0.82242 | 0.86946 | 273.0758 | 0 | 0 | 0 | 0 | 180 | 93.0758 | 262000 | 93.0758 | 73032.2303 | 302.4574 | 0
899 | 2 | 0 | 1 | 0.57459 | 312.3008 | 0 | 0 | 0 | 0 | 180 | 132.3008 | 262000 | 132.3008 | 73164.5311 | 458.4814 | 0
900 | 2 | 0 | 1 | 0.47934 | 308.4049 | 0 | 0 | 0 | 0 | 60.3698 | 200 | 262000 | 200 | 73364.5311 | 510.81 | 48.0351
901 | 2 | 0 | 1 | 0.31116 | 301.5266 | 0 | 0 | 0 | 0 | 0 | 200 | 262000 | 200 | 73564.5311 | 510.81 | 101.5266
902 | 2 | 0 | 1 | 0.2826 | 300.3583 | 0 | 0 | 0 | 0 | 0 | 200 | 262000 | 200 | 73764.5311 | 510.81 | 100.3583
903 | 2 | 0 | 1 | 0.28161 | 300.3178 | 0 | 0 | 0 | 0 | 0 | 200 | 262000 | 200 | 73964.5311 | 510.81 | 100.3178
904 | 2 | 0 | 0.82242 | 0.22493 | 246.7147 | 0 | 0 | 0 | 0 | 0 | 200 | 262000 | 200 | 74164.5311 | 510.81 | 46.7147
905 | 2 | 0 | 0.46842 | 0.39293 | 151.3522 | 0 | 0 | 0 | 0 | 0 | 151.3522 | 262000 | 151.3522 | 74315.8833 | 510.81 | 0
906 | 2 | 0 | 0.13867 | 0.24722 | 50.1595 | 0 | 0 | 0 | 0 | 0 | 50.1595 | 262000 | 50.1595 | 74366.0428 | 510.81 | 0
907 | 2 | 0 | 0 | 0.29236 | 11.9576 | 0 | 0 | 0 | 0 | 0 | 11.9576 | 262000 | 11.9576 | 74378.0004 | 510.81 | 0
908 | 2 | 1 | 0 | 0.3917 | 16.0205 | 200 | 16.0205 | 180 | 196.0205 | 0 | 0 | 261800 | 196.0205 | 74574.0209 | 330.81 | 0
909 | 2 | 1 | 0 | 0.30064 | 12.2963 | 200 | 12.2963 | 180 | 192.2963 | 0 | 0 | 261600 | 192.2963 | 74766.3172 | 150.81 | 0
910 | 2 | 0 | 0 | 0.446 | 18.2413 | 0 | 0 | 0 | 0 | 18.2413 | 0 | 261600 | 0 | 74766.3172 | 166.6216 | 0
911 | 2 | 0 | 0 | 0.41408 | 16.9358 | 0 | 0 | 0 | 0 | 16.9358 | 0 | 261600 | 0 | 74766.3172 | 181.3015 | 0
912 | 2 | 0 | 0 | 0.293 | 11.9838 | 0 | 0 | 0 | 0 | 11.9838 | 0 | 261600 | 0 | 74766.3172 | 191.6891 | 0
913 | 2 | 0 | 0 | 0.27229 | 11.1367 | 0 | 0 | 0 | 0 | 11.1367 | 0 | 261600 | 0 | 74766.3172 | 201.3424 | 0
914 | 2 | 0 | 0 | 0.32236 | 13.1847 | 0 | 0 | 0 | 0 | 13.1847 | 0 | 261600 | 0 | 74766.3172 | 212.7709 | 0
915 | 2 | 0 | 0 | 0.2814 | 11.5091 | 0 | 0 | 0 | 0 | 11.5091 | 0 | 261600 | 0 | 74766.3172 | 222.747 | 0
916 | 2 | 0 | 0 | 0.33382 | 13.6533 | 0 | 0 | 0 | 0 | 13.6533 | 0 | 261600 | 0 | 74766.3172 | 234.5816 | 0
917 | 2 | 0 | 0 | 0.42013 | 17.1835 | 0 | 0 | 0 | 0 | 17.1835 | 0 | 261600 | 0 | 74766.3172 | 249.4763 | 0
918 | 2 | 0 | 0 | 0.41472 | 16.9621 | 0 | 0 | 0 | 0 | 16.9621 | 0 | 261600 | 0 | 74766.3172 | 264.179 | 0
919 | 2 | 0 | 0 | 0.38087 | 15.5777 | 0 | 0 | 0 | 0 | 15.5777 | 0 | 261600 | 0 | 74766.3172 | 277.6818 | 0
920 | 2 | 1 | 0.13956 | 0.28023 | 51.7672 | 200 | 51.7672 | 148.2328 | 200 | 0 | 0 | 261400 | 200 | 74966.3172 | 129.449 | 0
921 | 2 | 1 | 0.47144 | 0.25911 | 146.7495 | 200 | 146.7495 | 53.2505 | 200 | 0 | 0 | 261200 | 200 | 75166.3172 | 76.1984 | 0
922 | 2 | 0 | 0.82771 | 0.21481 | 247.8294 | 0 | 0 | 0 | 0 | 180 | 67.8294 | 261200 | 67.8294 | 75234.1467 | 232.2224 | 0
923 | 2 | 0 | 1 | 0.2441 | 298.7836 | 0 | 0 | 0 | 0 | 180 | 118.7836 | 261200 | 118.7836 | 75352.9302 | 388.2464 | 0
924 | 2 | 0 | 1 | 0.18276 | 296.275 | 0 | 0 | 0 | 0 | 141.3978 | 154.8773 | 261200 | 154.8773 | 75507.8075 | 510.81 | 0
925 | 2 | 0 | 1 | 0.20427 | 297.1547 | 0 | 0 | 0 | 0 | 0 | 200 | 261200 | 200 | 75707.8075 | 510.81 | 97.1547
926 | 2 | 0 | 1 | 0.23093 | 298.245 | 0 | 0 | 0 | 0 | 0 | 200 | 261200 | 200 | 75907.8075 | 510.81 | 98.245
927 | 2 | 0 | 1 | 0.16102 | 295.3856 | 0 | 0 | 0 | 0 | 0 | 200 | 261200 | 200 | 76107.8075 | 510.81 | 95.3856
928 | 2 | 0 | 0.82771 | 0.14892 | 245.1346 | 0 | 0 | 0 | 0 | 0 | 200 | 261200 | 200 | 76307.8075 | 510.81 | 45.1346
929 | 2 | 0 | 0.47144 | 0.11126 | 140.7024 | 0 | 0 | 0 | 0 | 0 | 140.7024 | 261200 | 140.7024 | 76448.5099 | 510.81 | 0
930 | 2 | 0 | 0.13956 | 0.13965 | 46.0174 | 0 | 0 | 0 | 0 | 0 | 46.0174 | 261200 | 46.0174 | 76494.5273 | 510.81 | 0
931 | 2 | 0 | 0 | 0.13067 | 5.3445 | 0 | 0 | 0 | 0 | 0 | 5.3445 | 261200 | 5.3445 | 76499.8718 | 510.81 | 0
932 | 2 | 1 | 0 | 0.16771 | 6.8593 | 200 | 6.8593 | 180 | 186.8593 | 0 | 0 | 261000 | 186.8593 | 76686.7311 | 330.81 | 0
933 | 2 | 1 | 0 | 0.17318 | 7.0831 | 200 | 7.0831 | 180 | 187.0831 | 0 | 0 | 260800 | 187.0831 | 76873.8142 | 150.81 | 0
934 | 2 | 0 | 0 | 0.13784 | 5.6375 | 0 | 0 | 0 | 0 | 5.6375 | 0 | 260800 | 0 | 76873.8142 | 155.6966 | 0
935 | 2 | 0 | 0 | 0.094527 | 3.8662 | 0 | 0 | 0 | 0 | 3.8662 | 0 | 260800 | 0 | 76873.8142 | 159.0478 | 0
936 | 2 | 0 | 0 | 0.11281 | 4.6141 | 0 | 0 | 0 | 0 | 4.6141 | 0 | 260800 | 0 | 76873.8142 | 163.0473 | 0
937 | 2 | 0 | 0 | 0.11683 | 4.7785 | 0 | 0 | 0 | 0 | 4.7785 | 0 | 260800 | 0 | 76873.8142 | 167.1893 | 0
938 | 2 | 0 | 0 | 0.090819 | 3.7145 | 0 | 0 | 0 | 0 | 3.7145 | 0 | 260800 | 0 | 76873.8142 | 170.409 | 0
939 | 2 | 0 | 0 | 0.092093 | 3.7666 | 0 | 0 | 0 | 0 | 3.7666 | 0 | 260800 | 0 | 76873.8142 | 173.6739 | 0
940 | 2 | 0 | 0 | 0.16129 | 6.5969 | 0 | 0 | 0 | 0 | 6.5969 | 0 | 260800 | 0 | 76873.8142 | 179.3921 | 0
941 | 2 | 0 | 0 | 0.16677 | 6.8208 | 0 | 0 | 0 | 0 | 6.8208 | 0 | 260800 | 0 | 76873.8142 | 185.3044 | 0
942 | 2 | 0 | 0 | 0.25844 | 10.5704 | 0 | 0 | 0 | 0 | 10.5704 | 0 | 260800 | 0 | 76873.8142 | 194.4668 | 0
943 | 2 | 0 | 0 | 0.23517 | 9.6185 | 0 | 0 | 0 | 0 | 9.6185 | 0 | 260800 | 0 | 76873.8142 | 202.8041 | 0
944 | 2 | 1 | 0.13835 | 0.29627 | 52.0733 | 200 | 52.0733 | 147.9267 | 200 | 0 | 0 | 260600 | 200 | 77073.8142 | 54.8774 | 0
945 | 2 | 1 | 0.46735 | 0.25882 | 145.5556 | 200 | 145.5556 | 54.4444 | 200 | 0 | 0 | 260400 | 200 | 77273.8142 | 0.43297 | 0
946 | 2 | 0 | 0.82053 | 0.23671 | 246.6494 | 0 | 0 | 0 | 0 | 180 | 66.6494 | 260400 | 66.6494 | 77340.4636 | 156.457 | 0
947 | 2 | 0 | 1 | 0.21723 | 297.6847 | 0 | 0 | 0 | 0 | 180 | 117.6847 | 260400 | 117.6847 | 77458.1483 | 312.481 | 0
948 | 2 | 0 | 1 | 0.17908 | 296.1246 | 0 | 0 | 0 | 0 | 180 | 116.1246 | 260400 | 116.1246 | 77574.2728 | 468.505 | 0
949 | 2 | 0 | 1 | 0.21638 | 297.6499 | 0 | 0 | 0 | 0 | 48.806 | 200 | 260400 | 200 | 77774.2728 | 510.81 | 48.8439
950 | 2 | 0 | 1 | 0.19397 | 296.7335 | 0 | 0 | 0 | 0 | 0 | 200 | 260400 | 200 | 77974.2728 | 510.81 | 96.7335
951 | 2 | 0 | 1 | 0.16097 | 295.3838 | 0 | 0 | 0 | 0 | 0 | 200 | 260400 | 200 | 78174.2728 | 510.81 | 95.3838
952 | 2 | 0 | 0.82053 | 0.149 | 243.0622 | 0 | 0 | 0 | 0 | 0 | 200 | 260400 | 200 | 78374.2728 | 510.81 | 43.0622
953 | 2 | 0 | 0.46735 | 0.20043 | 143.1674 | 0 | 0 | 0 | 0 | 0 | 143.1674 | 260400 | 143.1674 | 78517.4402 | 510.81 | 0
954 | 2 | 0 | 0.13835 | 0.2218 | 49.0275 | 0 | 0 | 0 | 0 | 0 | 49.0275 | 260400 | 49.0275 | 78566.4677 | 510.81 | 0
955 | 2 | 0 | 0 | 0.15529 | 6.3513 | 0 | 0 | 0 | 0 | 0 | 6.3513 | 260400 | 6.3513 | 78572.819 | 510.81 | 0
956 | 2 | 1 | 0 | 0.16996 | 6.9515 | 200 | 6.9515 | 180 | 186.9515 | 0 | 0 | 260200 | 186.9515 | 78759.7705 | 330.81 | 0
957 | 2 | 1 | 0 | 0.15746 | 6.4403 | 200 | 6.4403 | 180 | 186.4403 | 0 | 0 | 260000 | 186.4403 | 78946.2108 | 150.81 | 0
958 | 2 | 0 | 0 | 0.10328 | 4.2242 | 0 | 0 | 0 | 0 | 4.2242 | 0 | 260000 | 0 | 78946.2108 | 154.4715 | 0
959 | 2 | 0 | 0 | 0.14693 | 6.0095 | 0 | 0 | 0 | 0 | 6.0095 | 0 | 260000 | 0 | 78946.2108 | 159.6805 | 0
960 | 2 | 0 | 0 | 0.15251 | 6.2377 | 0 | 0 | 0 | 0 | 6.2377 | 0 | 260000 | 0 | 78946.2108 | 165.0874 | 0
961 | 2 | 0 | 0 | 0.10193 | 4.1687 | 0 | 0 | 0 | 0 | 4.1687 | 0 | 260000 | 0 | 78946.2108 | 168.7008 | 0
962 | 2 | 0 | 0 | 0.16893 | 6.9094 | 0 | 0 | 0 | 0 | 6.9094 | 0 | 260000 | 0 | 78946.2108 | 174.6899 | 0
963 | 2 | 0 | 0 | 0.27892 | 11.408 | 0 | 0 | 0 | 0 | 11.408 | 0 | 260000 | 0 | 78946.2108 | 184.5783 | 0
964 | 2 | 0 | 0 | 0.31246 | 12.7797 | 0 | 0 | 0 | 0 | 12.7797 | 0 | 260000 | 0 | 78946.2108 | 195.6557 | 0
965 | 2 | 0 | 0 | 0.26102 | 10.6756 | 0 | 0 | 0 | 0 | 10.6756 | 0 | 260000 | 0 | 78946.2108 | 204.9093 | 0
966 | 2 | 0 | 0 | 0.19076 | 7.8021 | 0 | 0 | 0 | 0 | 7.8021 | 0 | 260000 | 0 | 78946.2108 | 211.6721 | 0
967 | 2 | 0 | 0 | 0.1528 | 6.2494 | 0 | 0 | 0 | 0 | 6.2494 | 0 | 260000 | 0 | 78946.2108 | 217.0892 | 0
968 | 2 | 1 | 0.15555 | 0.13634 | 50.4991 | 200 | 50.4991 | 149.5009 | 200 | 0 | 0 | 259800 | 200 | 79146.2108 | 67.5882 | 0
969 | 2 | 1 | 0.52544 | 0.0987 | 155.7836 | 200 | 155.7836 | 44.2164 | 200 | 0 | 0 | 259600 | 200 | 79346.2108 | 23.3718 | 0
970 | 2 | 0 | 0.92252 | 0.10759 | 270.824 | 0 | 0 | 0 | 0 | 180 | 90.824 | 259600 | 90.824 | 79437.0349 | 179.3958 | 0
971 | 2 | 0 | 1 | 0.11483 | 293.4966 | 0 | 0 | 0 | 0 | 180 | 113.4966 | 259600 | 113.4966 | 79550.5315 | 335.4198 | 0
972 | 2 | 0 | 1 | 0.15975 | 295.3336 | 0 | 0 | 0 | 0 | 180 | 115.3336 | 259600 | 115.3336 | 79665.8651 | 491.4438 | 0
973 | 2 | 0 | 1 | 0.12486 | 293.9066 | 0 | 0 | 0 | 0 | 22.3421 | 200 | 259600 | 200 | 79865.8651 | 510.81 | 71.5645
974 | 2 | 0 | 1 | 0.12927 | 294.0873 | 0 | 0 | 0 | 0 | 0 | 200 | 259600 | 200 | 80065.8651 | 510.81 | 94.0873
975 | 2 | 0 | 1 | 0.10122 | 292.9399 | 0 | 0 | 0 | 0 | 0 | 200 | 259600 | 200 | 80265.8651 | 510.81 | 92.9399
976 | 2 | 0 | 0.92252 | 0.14852 | 272.4984 | 0 | 0 | 0 | 0 | 0 | 200 | 259600 | 200 | 80465.8651 | 510.81 | 72.4984
977 | 2 | 0 | 0.52544 | 0.12391 | 156.8149 | 0 | 0 | 0 | 0 | 0 | 156.8149 | 259600 | 156.8149 | 80622.68 | 510.81 | 0
978 | 2 | 0 | 0.15555 | 0.12211 | 49.9167 | 0 | 0 | 0 | 0 | 0 | 49.9167 | 259600 | 49.9167 | 80672.5967 | 510.81 | 0
979 | 2 | 0 | 0 | 0.21074 | 8.6193 | 0 | 0 | 0 | 0 | 0 | 8.6193 | 259600 | 8.6193 | 80681.2161 | 510.81 | 0
980 | 2 | 1 | 0 | 0.31125 | 12.7302 | 200 | 12.7302 | 180 | 192.7302 | 0 | 0 | 259400 | 192.7302 | 80873.9463 | 330.81 | 0
981 | 2 | 1 | 0 | 0.38092 | 15.5796 | 200 | 15.5796 | 180 | 195.5796 | 0 | 0 | 259200 | 195.5796 | 81069.5259 | 150.81 | 0
982 | 2 | 0 | 0 | 0.40991 | 16.7652 | 0 | 0 | 0 | 0 | 16.7652 | 0 | 259200 | 0 | 81069.5259 | 165.3421 | 0
983 | 2 | 0 | 0 | 0.52984 | 21.6706 | 0 | 0 | 0 | 0 | 21.6706 | 0 | 259200 | 0 | 81069.5259 | 184.1261 | 0
984 | 2 | 0 | 0 | 0.55792 | 22.8189 | 0 | 0 | 0 | 0 | 22.8189 | 0 | 259200 | 0 | 81069.5259 | 203.9055 | 0
985 | 2 | 0 | 0 | 0.79417 | 32.4816 | 0 | 0 | 0 | 0 | 32.4816 | 0 | 259200 | 0 | 81069.5259 | 232.0606 | 0
986 | 2 | 0 | 0 | 0.83292 | 34.0663 | 0 | 0 | 0 | 0 | 34.0663 | 0 | 259200 | 0 | 81069.5259 | 261.5893 | 0
987 | 2 | 0 | 0 | 0.69002 | 28.2217 | 0 | 0 | 0 | 0 | 28.2217 | 0 | 259200 | 0 | 81069.5259 | 286.0519 | 0
988 | 2 | 0 | 0 | 0.64441 | 26.3564 | 0 | 0 | 0 | 0 | 26.3564 | 0 | 259200 | 0 | 81069.5259 | 308.8976 | 0
989 | 2 | 0 | 0 | 0.76766 | 31.3974 | 0 | 0 | 0 | 0 | 31.3974 | 0 | 259200 | 0 | 81069.5259 | 336.1129 | 0
990 | 2 | 0 | 0 | 0.92854 | 37.9773 | 0 | 0 | 0 | 0 | 37.9773 | 0 | 259200 | 0 | 81069.5259 | 369.0316 | 0
991 | 2 | 0 | 0 | 0.63634 | 26.0263 | 0 | 0 | 0 | 0 | 26.0263 | 0 | 259200 | 0 | 81069.5259 | 391.5912 | 0
992 | 2 | 1 | 0.10295 | 0.44108 | 47.7718 | 200 | 47.7718 | 152.2282 | 200 | 0 | 0 | 259000 | 200 | 81269.5259 | 239.363 | 0
993 | 2 | 1 | 0.34776 | 0.39442 | 116.5649 | 200 | 116.5649 | 83.4351 | 200 | 0 | 0 | 258800 | 200 | 81469.5259 | 155.9279 | 0
994 | 2 | 0 | 0.61057 | 0.44546 | 194.5511 | 0 | 0 | 0 | 0 | 180 | 14.5511 | 258800 | 14.5511 | 81484.077 | 311.9519 | 0
995 | 2 | 0 | 0.83784 | 0.42419 | 259.3165 | 0 | 0 | 0 | 0 | 180 | 79.3165 | 258800 | 79.3165 | 81563.3935 | 467.9759 | 0
996 | 2 | 0 | 0.99068 | 0.65463 | 312.8818 | 0 | 0 | 0 | 0 | 49.4163 | 200 | 258800 | 200 | 81763.3935 | 510.81 | 63.4655
997 | 2 | 0 | 1 | 0.38714 | 304.6338 | 0 | 0 | 0 | 0 | 0 | 200 | 258800 | 200 | 81963.3935 | 510.81 | 104.6338
998 | 2 | 0 | 0.99068 | 0.26256 | 296.8464 | 0 | 0 | 0 | 0 | 0 | 200 | 258800 | 200 | 82163.3935 | 510.81 | 96.8464
999 | 2 | 0 | 0.83784 | 0.25943 | 252.5781 | 0 | 0 | 0 | 0 | 0 | 200 | 258800 | 200 | 82363.3935 | 510.81 | 52.5781
1000 | 2 | 0 | 0.61057 | 0.29062 | 188.218 | 0 | 0 | 0 | 0 | 0 | 188.218 | 258800 | 188.218 | 82551.6115 | 510.81 | 0
1001 | 2 | 0 | 0.34776 | 0.24155 | 110.3126 | 0 | 0 | 0 | 0 | 0 | 110.3126 | 258800 | 110.3126 | 82661.924 | 510.81 | 0
1002 | 2 | 0 | 0.10295 | 0.23413 | 39.3076 | 0 | 0 | 0 | 0 | 0 | 39.3076 | 258800 | 39.3076 | 82701.2317 | 510.81 | 0
1003 | 2 | 0 | 0 | 0.15165 | 6.2026 | 0 | 0 | 0 | 0 | 0 | 6.2026 | 258800 | 6.2026 | 82707.4342 | 510.81 | 0
1004 | 2 | 1 | 0 | 0.10565 | 4.3213 | 200 | 4.3213 | 180 | 184.3213 | 0 | 0 | 258600 | 184.3213 | 82891.7555 | 330.81 | 0
1005 | 2 | 1 | 0 | 0.11704 | 4.7871 | 200 | 4.7871 | 180 | 184.7871 | 0 | 0 | 258400 | 184.7871 | 83076.5426 | 150.81 | 0
1006 | 2 | 0 | 0 | 0.076147 | 3.1144 | 0 | 0 | 0 | 0 | 3.1144 | 0 | 258400 | 0 | 83076.5426 | 153.5096 | 0
1007 | 2 | 0 | 0 | 0.072663 | 2.9719 | 0 | 0 | 0 | 0 | 2.9719 | 0 | 258400 | 0 | 83076.5426 | 156.0856 | 0
1008 | 2 | 0 | 0 | 0.082019 | 3.3546 | 0 | 0 | 0 | 0 | 3.3546 | 0 | 258400 | 0 | 83076.5426 | 158.9934 | 0
1009 | 2 | 0 | 0 | 0.099124 | 4.0542 | 0 | 0 | 0 | 0 | 4.0542 | 0 | 258400 | 0 | 83076.5426 | 162.5075 | 0
1010 | 2 | 0 | 0 | 0.10648 | 4.3552 | 0 | 0 | 0 | 0 | 4.3552 | 0 | 258400 | 0 | 83076.5426 | 166.2826 | 0
1011 | 2 | 0 | 0 | 0.07709 | 3.153 | 0 | 0 | 0 | 0 | 3.153 | 0 | 258400 | 0 | 83076.5426 | 169.0156 | 0
1012 | 2 | 0 | 0 | 0.068287 | 2.7929 | 0 | 0 | 0 | 0 | 2.7929 | 0 | 258400 | 0 | 83076.5426 | 171.4365 | 0
1013 | 2 | 0 | 0 | 0.083624 | 3.4202 | 0 | 0 | 0 | 0 | 3.4202 | 0 | 258400 | 0 | 83076.5426 | 174.4012 | 0
1014 | 2 | 0 | 0 | 0.091493 | 3.7421 | 0 | 0 | 0 | 0 | 3.7421 | 0 | 258400 | 0 | 83076.5426 | 177.6448 | 0
1015 | 2 | 0 | 0 | 0.048946 | 2.0019 | 0 | 0 | 0 | 0 | 2.0019 | 0 | 258400 | 0 | 83076.5426 | 179.38 | 0
1016 | 2 | 1 | 0.124 | 0.039901 | 37.4434 | 200 | 37.4434 | 162.5566 | 200 | 0 | 0 | 258200 | 200 | 83276.5426 | 16.8235 | 0
1017 | 2 | 1 | 0.41887 | 0.040576 | 122.6298 | 200 | 122.6298 | 16.8235 | 139.4533 | 0 | 0 | 258000 | 139.4533 | 83415.9959 | 0 | 0
1018 | 2 | 0 | 0.73542 | 0.041706 | 214.0948 | 0 | 0 | 0 | 0 | 180 | 34.0948 | 258000 | 34.0948 | 83450.0907 | 156.024 | 0
1019 | 2 | 0 | 1 | 0.03391 | 290.1869 | 0 | 0 | 0 | 0 | 180 | 110.1869 | 258000 | 110.1869 | 83560.2776 | 312.048 | 0
1020 | 2 | 0 | 1 | 0.055178 | 291.0568 | 0 | 0 | 0 | 0 | 180 | 111.0568 | 258000 | 111.0568 | 83671.3343 | 468.072 | 0
1021 | 2 | 0 | 1 | 0.070497 | 291.6833 | 0 | 0 | 0 | 0 | 49.3055 | 200 | 258000 | 200 | 83871.3343 | 510.81 | 42.3778
1022 | 2 | 0 | 1 | 0.066962 | 291.5387 | 0 | 0 | 0 | 0 | 0 | 200 | 258000 | 200 | 84071.3343 | 510.81 | 91.5387
1023 | 2 | 0 | 1 | 0.10387 | 293.0482 | 0 | 0 | 0 | 0 | 0 | 200 | 258000 | 200 | 84271.3343 | 510.81 | 93.0482
1024 | 2 | 0 | 0.73542 | 0.13924 | 218.0838 | 0 | 0 | 0 | 0 | 0 | 200 | 258000 | 200 | 84471.3343 | 510.81 | 18.0838
1025 | 2 | 0 | 0.41887 | 0.10307 | 125.1856 | 0 | 0 | 0 | 0 | 0 | 125.1856 | 258000 | 125.1856 | 84596.52 | 510.81 | 0
1026 | 2 | 0 | 0.124 | 0.14301 | 41.6607 | 0 | 0 | 0 | 0 | 0 | 41.6607 | 258000 | 41.6607 | 84638.1807 | 510.81 | 0
1027 | 2 | 0 | 0 | 0.094168 | 3.8515 | 0 | 0 | 0 | 0 | 0 | 3.8515 | 258000 | 3.8515 | 84642.0321 | 510.81 | 0
1028 | 2 | 1 | 0 | 0.090505 | 3.7017 | 200 | 3.7017 | 180 | 183.7017 | 0 | 0 | 257800 | 183.7017 | 84825.7338 | 330.81 | 0
1029 | 2 | 1 | 0 | 0.0737 | 3.0143 | 200 | 3.0143 | 180 | 183.0143 | 0 | 0 | 257600 | 183.0143 | 85008.7481 | 150.81 | 0
1030 | 2 | 0 | 0 | 0.070869 | 2.8985 | 0 | 0 | 0 | 0 | 2.8985 | 0 | 257600 | 0 | 85008.7481 | 153.3225 | 0
1031 | 2 | 0 | 0 | 0.083392 | 3.4107 | 0 | 0 | 0 | 0 | 3.4107 | 0 | 257600 | 0 | 85008.7481 | 156.2789 | 0
1032 | 2 | 0 | 0 | 0.10907 | 4.461 | 0 | 0 | 0 | 0 | 4.461 | 0 | 257600 | 0 | 85008.7481 | 160.1457 | 0
1033 | 2 | 0 | 0 | 0.095599 | 3.91 | 0 | 0 | 0 | 0 | 3.91 | 0 | 257600 | 0 | 85008.7481 | 163.5349 | 0
1034 | 2 | 0 | 0 | 0.090398 | 3.6973 | 0 | 0 | 0 | 0 | 3.6973 | 0 | 257600 | 0 | 85008.7481 | 166.7397 | 0
1035 | 2 | 0 | 0 | 0.1309 | 5.3539 | 0 | 0 | 0 | 0 | 5.3539 | 0 | 257600 | 0 | 85008.7481 | 171.3805 | 0
1036 | 2 | 0 | 0 | 0.11654 | 4.7665 | 0 | 0 | 0 | 0 | 4.7665 | 0 | 257600 | 0 | 85008.7481 | 175.5121 | 0
1037 | 2 | 0 | 0 | 0.16526 | 6.759 | 0 | 0 | 0 | 0 | 6.759 | 0 | 257600 | 0 | 85008.7481 | 181.3708 | 0
1038 | 2 | 0 | 0 | 0.18326 | 7.4954 | 0 | 0 | 0 | 0 | 7.4954 | 0 | 257600 | 0 | 85008.7481 | 187.8677 | 0
1039 | 2 | 0 | 0 | 0.23511 | 9.6162 | 0 | 0 | 0 | 0 | 9.6162 | 0 | 257600 | 0 | 85008.7481 | 196.2031 | 0
1040 | 2 | 1 | 0.14618 | 0.237 | 51.9109 | 200 | 51.9109 | 148.0891 | 200 | 0 | 0 | 257400 | 200 | 85208.7481 | 48.114 | 0
1041 | 2 | 1 | 0.4938 | 0.17821 | 149.8985 | 200 | 149.8985 | 48.114 | 198.0125 | 0 | 0 | 257200 | 198.0125 | 85406.7606 | 0 | 0
1042 | 2 | 0 | 0.86697 | 0.21004 | 258.9727 | 0 | 0 | 0 | 0 | 180 | 78.9727 | 257200 | 78.9727 | 85485.7333 | 156.024 | 0
1043 | 2 | 0 | 1 | 0.23865 | 298.5606 | 0 | 0 | 0 | 0 | 180 | 118.5606 | 257200 | 118.5606 | 85604.2939 | 312.048 | 0
1044 | 2 | 0 | 1 | 0.26046 | 299.453 | 0 | 0 | 0 | 0 | 180 | 119.453 | 257200 | 119.453 | 85723.7469 | 468.072 | 0
1045 | 2 | 0 | 1 | 0.25007 | 299.0279 | 0 | 0 | 0 | 0 | 49.3055 | 200 | 257200 | 200 | 85923.7469 | 510.81 | 49.7224
1046 | 2 | 0 | 1 | 0.32178 | 301.9607 | 0 | 0 | 0 | 0 | 0 | 200 | 257200 | 200 | 86123.7469 | 510.81 | 101.9607
1047 | 2 | 0 | 1 | 0.30647 | 301.3348 | 0 | 0 | 0 | 0 | 0 | 200 | 257200 | 200 | 86323.7469 | 510.81 | 101.3348
1048 | 2 | 0 | 0.86697 | 0.34166 | 264.356 | 0 | 0 | 0 | 0 | 0 | 200 | 257200 | 200 | 86523.7469 | 510.81 | 64.356
1049 | 2 | 0 | 0.4938 | 0.22745 | 151.9125 | 0 | 0 | 0 | 0 | 0 | 151.9125 | 257200 | 151.9125 | 86675.6594 | 510.81 | 0
1050 | 2 | 0 | 0.14618 | 0.207 | 50.6838 | 0 | 0 | 0 | 0 | 0 | 50.6838 | 257200 | 50.6838 | 86726.3432 | 510.81 | 0
1051 | 2 | 0 | 0 | 0.24614 | 10.0672 | 0 | 0 | 0 | 0 | 0 | 10.0672 | 257200 | 10.0672 | 86736.4104 | 510.81 | 0
1052 | 2 | 1 | 0 | 0.18546 | 7.5853 | 200 | 7.5853 | 180 | 187.5853 | 0 | 0 | 257000 | 187.5853 | 86923.9957 | 330.81 | 0
1053 | 2 | 1 | 0 | 0.20369 | 8.3308 | 200 | 8.3308 | 180 | 188.3308 | 0 | 0 | 256800 | 188.3308 | 87112.3265 | 150.81 | 0
1054 | 2 | 0 | 0 | 0.23991 | 9.8124 | 0 | 0 | 0 | 0 | 9.8124 | 0 | 256800 | 0 | 87112.3265 | 159.3154 | 0
1055 | 2 | 0 | 0 | 0.1958 | 8.0084 | 0 | 0 | 0 | 0 | 8.0084 | 0 | 256800 | 0 | 87112.3265 | 166.2571 | 0
1056 | 2 | 0 | 0 | 0.12884 | 5.2697 | 0 | 0 | 0 | 0 | 5.2697 | 0 | 256800 | 0 | 87112.3265 | 170.8248 | 0
1057 | 2 | 0 | 0 | 0.13334 | 5.4538 | 0 | 0 | 0 | 0 | 5.4538 | 0 | 256800 | 0 | 87112.3265 | 175.5522 | 0
1058 | 2 | 0 | 0 | 0.17229 | 7.0465 | 0 | 0 | 0 | 0 | 7.0465 | 0 | 256800 | 0 | 87112.3265 | 181.6601 | 0
1059 | 2 | 0 | 0 | 0.19198 | 7.852 | 0 | 0 | 0 | 0 | 7.852 | 0 | 256800 | 0 | 87112.3265 | 188.4662 | 0
1060 | 2 | 0 | 0 | 0.23705 | 9.6952 | 0 | 0 | 0 | 0 | 9.6952 | 0 | 256800 | 0 | 87112.3265 | 196.8701 | 0
1061 | 2 | 0 | 0 | 0.34011 | 13.9104 | 0 | 0 | 0 | 0 | 13.9104 | 0 | 256800 | 0 | 87112.3265 | 208.9276 | 0
1062 | 2 | 0 | 0 | 0.46321 | 18.9455 | 0 | 0 | 0 | 0 | 18.9455 | 0 | 256800 | 0 | 87112.3265 | 225.3495 | 0
1063 | 2 | 0 | 0 | 0.72526 | 29.6631 | 0 | 0 | 0 | 0 | 29.6631 | 0 | 256800 | 0 | 87112.3265 | 251.0615 | 0
1064 | 2 | 1 | 0.14294 | 0.51803 | 62.4675 | 200 | 62.4675 | 137.5325 | 200 | 0 | 0 | 256600 | 200 | 87312.3265 | 113.529 | 0
1065 | 2 | 1 | 0.48283 | 0.58156 | 163.228 | 200 | 163.228 | 36.772 | 200 | 0 | 0 | 256400 | 200 | 87512.3265 | 76.757 | 0
1066 | 2 | 0 | 0.84771 | 0.8177 | 278.2639 | 0 | 0 | 0 | 0 | 180 | 98.2639 | 256400 | 98.2639 | 87610.5904 | 232.781 | 0
1067 | 2 | 0 | 1 | 0.74291 | 319.185 | 0 | 0 | 0 | 0 | 180 | 139.185 | 256400 | 139.185 | 87749.7754 | 388.805 | 0
1068 | 2 | 0 | 1 | 0.76276 | 319.9968 | 0 | 0 | 0 | 0 | 140.7533 | 179.2434 | 256400 | 179.2434 | 87929.0188 | 510.81 | 0
1069 | 2 | 0 | 1 | 0.70059 | 317.454 | 0 | 0 | 0 | 0 | 0 | 200 | 256400 | 200 | 88129.0188 | 510.81 | 117.454
1070 | 2 | 0 | 1 | 0.38241 | 304.4406 | 0 | 0 | 0 | 0 | 0 | 200 | 256400 | 200 | 88329.0188 | 510.81 | 104.4406
1071 | 2 | 0 | 1 | 0.44456 | 306.9826 | 0 | 0 | 0 | 0 | 0 | 200 | 256400 | 200 | 88529.0188 | 510.81 | 106.9826
1072 | 2 | 0 | 0.84771 | 0.32526 | 258.1234 | 0 | 0 | 0 | 0 | 0 | 200 | 256400 | 200 | 88729.0188 | 510.81 | 58.1234
1073 | 2 | 0 | 0.48283 | 0.43403 | 157.194 | 0 | 0 | 0 | 0 | 0 | 157.194 | 256400 | 157.194 | 88886.2128 | 510.81 | 0
1074 | 2 | 0 | 0.14294 | 0.45411 | 59.8532 | 0 | 0 | 0 | 0 | 0 | 59.8532 | 256400 | 59.8532 | 88946.066 | 510.81 | 0
1075 | 2 | 0 | 0 | 0.60798 | 24.8663 | 0 | 0 | 0 | 0 | 0 | 24.8663 | 256400 | 24.8663 | 88970.9323 | 510.81 | 0
1076 | 2 | 1 | 0 | 0.75145 | 30.7343 | 200 | 30.7343 | 169.2657 | 200 | 0 | 0 | 256200 | 200 | 89170.9323 | 341.5443 | 0
1077 | 2 | 1 | 0 | 0.39798 | 16.2772 | 200 | 16.2772 | 180 | 196.2772 | 0 | 0 | 256000 | 196.2772 | 89367.2095 | 161.5443 | 0
1078 | 2 | 0 | 0 | 0.37304 | 15.2574 | 0 | 0 | 0 | 0 | 15.2574 | 0 | 256000 | 0 | 89367.2095 | 174.7694 | 0
1079 | 2 | 0 | 0 | 0.36638 | 14.9849 | 0 | 0 | 0 | 0 | 14.9849 | 0 | 256000 | 0 | 89367.2095 | 187.7583 | 0
1080 | 2 | 0 | 0 | 0.32556 | 13.3153 | 0 | 0 | 0 | 0 | 13.3153 | 0 | 256000 | 0 | 89367.2095 | 199.3 | 0
1081 | 2 | 0 | 0 | 0.27627 | 11.2996 | 0 | 0 | 0 | 0 | 11.2996 | 0 | 256000 | 0 | 89367.2095 | 209.0945 | 0
1082 | 2 | 0 | 0 | 0.25711 | 10.516 | 0 | 0 | 0 | 0 | 10.516 | 0 | 256000 | 0 | 89367.2095 | 218.2098 | 0
1083 | 2 | 0 | 0 | 0.17369 | 7.1037 | 0 | 0 | 0 | 0 | 7.1037 | 0 | 256000 | 0 | 89367.2095 | 224.3673 | 0
1084 | 2 | 0 | 0 | 0.13947 | 5.7041 | 0 | 0 | 0 | 0 | 5.7041 | 0 | 256000 | 0 | 89367.2095 | 229.3116 | 0
1085 | 2 | 0 | 0 | 0.10577 | 4.3259 | 0 | 0 | 0 | 0 | 4.3259 | 0 | 256000 | 0 | 89367.2095 | 233.0613 | 0
1086 | 2 | 0 | 0 | 0.1701 | 6.9572 | 0 | 0 | 0 | 0 | 6.9572 | 0 | 256000 | 0 | 89367.2095 | 239.0918 | 0
1087 | 2 | 0 | 0 | 0.22618 | 9.2507 | 0 | 0 | 0 | 0 | 9.2507 | 0 | 256000 | 0 | 89367.2095 | 247.1103 | 0
1088 | 2 | 1 | 0.14792 | 0.18174 | 50.1532 | 200 | 50.1532 | 149.8468 | 200 | 0 | 0 | 255800 | 200 | 89567.2095 | 97.2635 | 0
1089 | 2 | 1 | 0.49968 | 0.26844 | 155.2858 | 200 | 155.2858 | 44.7142 | 200 | 0 | 0 | 255600 | 200 | 89767.2095 | 52.5493 | 0
1090 | 2 | 0 | 0.87729 | 0.36027 | 268.0959 | 0 | 0 | 0 | 0 | 180 | 88.0959 | 255600 | 88.0959 | 89855.3054 | 208.5733 | 0
1091 | 2 | 0 | 1 | 0.44778 | 307.1143 | 0 | 0 | 0 | 0 | 180 | 127.1143 | 255600 | 127.1143 | 89982.4197 | 364.5973 | 0
1092 | 2 | 0 | 1 | 0.29565 | 300.892 | 0 | 0 | 0 | 0 | 168.681 | 132.211 | 255600 | 132.211 | 90114.6307 | 510.81 | 0
1093 | 2 | 0 | 1 | 0.34353 | 302.8505 | 0 | 0 | 0 | 0 | 0 | 200 | 255600 | 200 | 90314.6307 | 510.81 | 102.8505
1094 | 2 | 0 | 1 | 0.3836 | 304.4892 | 0 | 0 | 0 | 0 | 0 | 200 | 255600 | 200 | 90514.6307 | 510.81 | 104.4892
1095 | 2 | 0 | 1 | 0.34824 | 303.0429 | 0 | 0 | 0 | 0 | 0 | 200 | 255600 | 200 | 90714.6307 | 510.81 | 103.0429
1096 | 2 | 0 | 0.87729 | 0.47542 | 272.8057 | 0 | 0 | 0 | 0 | 0 | 200 | 255600 | 200 | 90914.6307 | 510.81 | 72.8057
1097 | 2 | 0 | 0.49968 | 0.52365 | 165.724 | 0 | 0 | 0 | 0 | 0 | 165.724 | 255600 | 165.724 | 91080.3547 | 510.81 | 0
1098 | 2 | 0 | 0.14792 | 0.51456 | 63.7653 | 0 | 0 | 0 | 0 | 0 | 63.7653 | 255600 | 63.7653 | 91144.12 | 510.81 | 0
1099 | 2 | 0 | 0 | 0.49331 | 20.1763 | 0 | 0 | 0 | 0 | 0 | 20.1763 | 255600 | 20.1763 | 91164.2963 | 510.81 | 0
1100 | 2 | 1 | 0 | 0.37609 | 15.382 | 200 | 15.382 | 180 | 195.382 | 0 | 0 | 255400 | 195.382 | 91359.6784 | 330.81 | 0
1101 | 2 | 1 | 0 | 0.38243 | 15.6412 | 200 | 15.6412 | 180 | 195.6412 | 0 | 0 | 255200 | 195.6412 | 91555.3196 | 150.81 | 0
1102 | 2 | 0 | 0 | 0.29476 | 12.0556 | 0 | 0 | 0 | 0 | 12.0556 | 0 | 255200 | 0 | 91555.3196 | 161.2598 | 0
1103 | 2 | 0 | 0 | 0.24824 | 10.1532 | 0 | 0 | 0 | 0 | 10.1532 | 0 | 255200 | 0 | 91555.3196 | 170.0606 | 0
1104 | 2 | 0 | 0 | 0.24962 | 10.2093 | 0 | 0 | 0 | 0 | 10.2093 | 0 | 255200 | 0 | 91555.3196 | 178.9101 | 0
1105 | 2 | 0 | 0 | 0.18362 | 7.5102 | 0 | 0 | 0 | 0 | 7.5102 | 0 | 255200 | 0 | 91555.3196 | 185.4199 | 0
1106 | 2 | 0 | 0 | 0.2603 | 10.6464 | 0 | 0 | 0 | 0 | 10.6464 | 0 | 255200 | 0 | 91555.3196 | 194.6482 | 0
1107 | 2 | 0 | 0 | 0.24955 | 10.2067 | 0 | 0 | 0 | 0 | 10.2067 | 0 | 255200 | 0 | 91555.3196 | 203.4954 | 0
1108 | 2 | 0 | 0 | 0.15806 | 6.4646 | 0 | 0 | 0 | 0 | 6.4646 | 0 | 255200 | 0 | 91555.3196 | 209.0989 | 0
1109 | 2 | 0 | 0 | 0.21509 | 8.7971 | 0 | 0 | 0 | 0 | 8.7971 | 0 | 255200 | 0 | 91555.3196 | 216.7242 | 0
1110 | 2 | 0 | 0 | 0.32129 | 13.1408 | 0 | 0 | 0 | 0 | 13.1408 | 0 | 255200 | 0 | 91555.3196 | 228.1147 | 0
1111 | 2 | 0 | 0 | 0.3361 | 13.7464 | 0 | 0 | 0 | 0 | 13.7464 | 0 | 255200 | 0 | 91555.3196 | 240.03 | 0
1112 | 2 | 1 | 0.11111 | 0.18141 | 39.5078 | 200 | 39.5078 | 160.4922 | 200 | 0 | 0 | 255000 | 200 | 91755.3196 | 79.5378 | 0
1113 | 2 | 1 | 0.37532 | 0.10869 | 112.8377 | 200 | 112.8377 | 79.5378 | 192.3755 | 0 | 0 | 254800 | 192.3755 | 91947.695 | 0 | 0
1114 | 2 | 0 | 0.65895 | 0.1624 | 196.9486 | 0 | 0 | 0 | 0 | 180 | 16.9486 | 254800 | 16.9486 | 91964.6436 | 156.024 | 0
1115 | 2 | 0 | 0.90424 | 0.18641 | 268.7676 | 0 | 0 | 0 | 0 | 180 | 88.7676 | 254800 | 88.7676 | 92053.4112 | 312.048 | 0
1116 | 2 | 0 | 1 | 0.17082 | 295.7867 | 0 | 0 | 0 | 0 | 180 | 115.7867 | 254800 | 115.7867 | 92169.1979 | 468.072 | 0
1117 | 2 | 0 | 1 | 0.18801 | 296.4895 | 0 | 0 | 0 | 0 | 49.3055 | 200 | 254800 | 200 | 92369.1979 | 510.81 | 47.184
1118 | 2 | 0 | 1 | 0.17155 | 295.8163 | 0 | 0 | 0 | 0 | 0 | 200 | 254800 | 200 | 92569.1979 | 510.81 | 95.8163
1119 | 2 | 0 | 0.90424 | 0.11926 | 266.021 | 0 | 0 | 0 | 0 | 0 | 200 | 254800 | 200 | 92769.1979 | 510.81 | 66.021
1120 | 2 | 0 | 0.65895 | 0.11111 | 194.8508 | 0 | 0 | 0 | 0 | 0 | 194.8508 | 254800 | 194.8508 | 92964.0487 | 510.81 | 0
1121 | 2 | 0 | 0.37532 | 0.099626 | 112.4671 | 0 | 0 | 0 | 0 | 0 | 112.4671 | 254800 | 112.4671 | 93076.5158 | 510.81 | 0
1122 | 2 | 0 | 0.11111 | 0.1319 | 37.4828 | 0 | 0 | 0 | 0 | 0 | 37.4828 | 254800 | 37.4828 | 93113.9986 | 510.81 | 0
1123 | 2 | 0 | 0 | 0.1879 | 7.6853 | 0 | 0 | 0 | 0 | 0 | 7.6853 | 254800 | 7.6853 | 93121.6839 | 510.81 | 0
1124 | 2 | 1 | 0 | 0.2561 | 10.4746 | 200 | 10.4746 | 180 | 190.4746 | 0 | 0 | 254600 | 190.4746 | 93312.1585 | 330.81 | 0
1125 | 2 | 1 | 0 | 0.3514 | 14.3721 | 200 | 14.3721 | 180 | 194.3721 | 0 | 0 | 254400 | 194.3721 | 93506.5305 | 150.81 | 0
1126 | 2 | 0 | 0 | 0.4415 | 18.0575 | 0 | 0 | 0 | 0 | 18.0575 | 0 | 254400 | 0 | 93506.5305 | 166.4623 | 0
1127 | 2 | 0 | 0 | 0.27931 | 11.4239 | 0 | 0 | 0 | 0 | 11.4239 | 0 | 254400 | 0 | 93506.5305 | 176.3645 | 0
1128 | 2 | 0 | 0 | 0.45262 | 18.5121 | 0 | 0 | 0 | 0 | 18.5121 | 0 | 254400 | 0 | 93506.5305 | 192.4108 | 0
1129 | 2 | 0 | 0 | 0.38144 | 15.6011 | 0 | 0 | 0 | 0 | 15.6011 | 0 | 254400 | 0 | 93506.5305 | 205.9338 | 0
1130 | 2 | 0 | 0 | 0.36456 | 14.9104 | 0 | 0 | 0 | 0 | 14.9104 | 0 | 254400 | 0 | 93506.5305 | 218.8581 | 0
1131 | 2 | 0 | 0 | 0.41717 | 17.0624 | 0 | 0 | 0 | 0 | 17.0624 | 0 | 254400 | 0 | 93506.5305 | 233.6478 | 0
1132 | 2 | 0 | 0 | 0.63537 | 25.9866 | 0 | 0 | 0 | 0 | 25.9866 | 0 | 254400 | 0 | 93506.5305 | 256.173 | 0
1133 | 2 | 0 | 0 | 0.66546 | 27.2174 | 0 | 0 | 0 | 0 | 27.2174 | 0 | 254400 | 0 | 93506.5305 | 279.765 | 0
1134 | 2 | 0 | 0 | 0.99314 | 40.6196 | 0 | 0 | 0 | 0 | 40.6196 | 0 | 254400 | 0 | 93506.5305 | 314.9741 | 0
1135 | 2 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 254400 | 0 | 93506.5305 | 350.4262 | 0
1136 | 2 | 1 | 0.12347 | 0.71849 | 65.0437 | 200 | 65.0437 | 134.9563 | 200 | 0 | 0 | 254200 | 200 | 93706.5305 | 215.47 | 0
1137 | 2 | 1 | 0.41707 | 0.63684 | 146.4964 | 200 | 146.4964 | 53.5036 | 200 | 0 | 0 | 254000 | 200 | 93906.5305 | 161.9664 | 0
1138 | 2 | 0 | 0.73225 | 0.44903 | 229.8402 | 0 | 0 | 0 | 0 | 180 | 49.8402 | 254000 | 49.8402 | 93956.3707 | 317.9904 | 0
1139 | 2 | 0 | 1 | 0.37311 | 304.0602 | 0 | 0 | 0 | 0 | 180 | 124.0602 | 254000 | 124.0602 | 94080.4309 | 474.0144 | 0
1140 | 2 | 0 | 1 | 0.36161 | 303.5897 | 0 | 0 | 0 | 0 | 42.4499 | 200 | 254000 | 200 | 94280.4309 | 510.81 | 61.1398
1141 | 2 | 0 | 1 | 0.3195 | 301.8677 | 0 | 0 | 0 | 0 | 0 | 200 | 254000 | 200 | 94480.4309 | 510.81 | 101.8677
1142 | 2 | 0 | 1 | 0.4264 | 306.2396 | 0 | 0 | 0 | 0 | 0 | 200 | 254000 | 200 | 94680.4309 | 510.81 | 106.2396
1143 | 2 | 0 | 1 | 0.61441 | 313.9294 | 0 | 0 | 0 | 0 | 0 | 200 | 254000 | 200 | 94880.4309 | 510.81 | 113.9294
1144 | 2 | 0 | 0.73225 | 0.56748 | 234.6844 | 0 | 0 | 0 | 0 | 0 | 200 | 254000 | 200 | 95080.4309 | 510.81 | 34.6844
1145 | 2 | 0 | 0.41707 | 0.59881 | 144.9408 | 0 | 0 | 0 | 0 | 0 | 144.9408 | 254000 | 144.9408 | 95225.3717 | 510.81 | 0
1146 | 2 | 0 | 0.12347 | 0.52179 | 56.9986 | 0 | 0 | 0 | 0 | 0 | 56.9986 | 254000 | 56.9986 | 95282.3703 | 510.81 | 0
1147 | 2 | 0 | 0 | 0.44076 | 18.0269 | 0 | 0 | 0 | 0 | 0 | 18.0269 | 254000 | 18.0269 | 95300.3972 | 510.81 | 0
1148 | 2 | 1 | 0 | 0.34486 | 14.1049 | 200 | 14.1049 | 180 | 194.1049 | 0 | 0 | 253800 | 194.1049 | 95494.502 | 330.81 | 0
1149 | 2 | 1 | 0 | 0.28366 | 11.6017 | 200 | 11.6017 | 180 | 191.6017 | 0 | 0 | 253600 | 191.6017 | 95686.1037 | 150.81 | 0
1150 | 2 | 0 | 0 | 0.30692 | 12.5529 | 0 | 0 | 0 | 0 | 12.5529 | 0 | 253600 | 0 | 95686.1037 | 161.6909 | 0
1151 | 2 | 0 | 0 | 0.2695 | 11.0227 | 0 | 0 | 0 | 0 | 11.0227 | 0 | 253600 | 0 | 95686.1037 | 171.2453 | 0
1152 | 2 | 0 | 0 | 0.22408 | 9.1648 | 0 | 0 | 0 | 0 | 9.1648 | 0 | 253600 | 0 | 95686.1037 | 179.1894 | 0
1153 | 2 | 0 | 0 | 0.17764 | 7.2656 | 0 | 0 | 0 | 0 | 7.2656 | 0 | 253600 | 0 | 95686.1037 | 185.4872 | 0
1154 | 2 | 0 | 0 | 0.1307 | 5.3455 | 0 | 0 | 0 | 0 | 5.3455 | 0 | 253600 | 0 | 95686.1037 | 190.1207 | 0
1155 | 2 | 0 | 0 | 0.12377 | 5.0622 | 0 | 0 | 0 | 0 | 5.0622 | 0 | 253600 | 0 | 95686.1037 | 194.5086 | 0
1156 | 2 | 0 | 0 | 0.127 | 5.1945 | 0 | 0 | 0 | 0 | 5.1945 | 0 | 253600 | 0 | 95686.1037 | 199.0112 | 0
1157 | 2 | 0 | 0 | 0.12696 | 5.1928 | 0 | 0 | 0 | 0 | 5.1928 | 0 | 253600 | 0 | 95686.1037 | 203.5123 | 0
1158 | 2 | 0 | 0 | 0.17339 | 7.0915 | 0 | 0 | 0 | 0 | 7.0915 | 0 | 253600 | 0 | 95686.1037 | 209.6593 | 0
1159 | 2 | 0 | 0 | 0.19325 | 7.9037 | 0 | 0 | 0 | 0 | 7.9037 | 0 | 253600 | 0 | 95686.1037 | 216.5102 | 0
1160 | 2 | 1 | 0.14106 | 0.31293 | 53.5373 | 200 | 53.5373 | 146.4627 | 200 | 0 | 0 | 253400 | 200 | 95886.1037 | 70.0475 | 0
1161 | 2 | 1 | 0.4765 | 0.17636 | 144.8265 | 200 | 144.8265 | 55.1735 | 200 | 0 | 0 | 253200 | 200 | 96086.1037 | 14.874 | 0
1162 | 2 | 0 | 0.8366 | 0.14118 | 247.3837 | 0 | 0 | 0 | 0 | 180 | 67.3837 | 253200 | 67.3837 | 96153.4874 | 170.898 | 0
1163 | 2 | 0 | 1 | 0.12718 | 294.0017 | 0 | 0 | 0 | 0 | 180 | 114.0017 | 253200 | 114.0017 | 96267.4892 | 326.922 | 0
1164 | 2 | 0 | 1 | 0.10087 | 292.9256 | 0 | 0 | 0 | 0 | 180 | 112.9256 | 253200 | 112.9256 | 96380.4147 | 482.946 | 0
1165 | 2 | 0 | 1 | 0.16645 | 295.6079 | 0 | 0 | 0 | 0 | 32.1459 | 200 | 253200 | 200 | 96580.4147 | 510.81 | 63.462
1166 | 2 | 0 | 1 | 0.20084 | 297.0145 | 0 | 0 | 0 | 0 | 0 | 200 | 253200 | 200 | 96780.4147 | 510.81 | 97.0145
1167 | 2 | 0 | 1 | 0.14938 | 294.9094 | 0 | 0 | 0 | 0 | 0 | 200 | 253200 | 200 | 96980.4147 | 510.81 | 94.9094
1168 | 2 | 0 | 0.8366 | 0.11804 | 246.4375 | 0 | 0 | 0 | 0 | 0 | 200 | 253200 | 200 | 97180.4147 | 510.81 | 46.4375
1169 | 2 | 0 | 0.4765 | 0.083659 | 141.0351 | 0 | 0 | 0 | 0 | 0 | 141.0351 | 253200 | 141.0351 | 97321.4499 | 510.81 | 0
1170 | 2 | 0 | 0.14106 | 0.051248 | 42.8345 | 0 | 0 | 0 | 0 | 0 | 42.8345 | 253200 | 42.8345 | 97364.2843 | 510.81 | 0
1171 | 2 | 0 | 0 | 0.037056 | 1.5156 | 0 | 0 | 0 | 0 | 0 | 1.5156 | 253200 | 1.5156 | 97365.7999 | 510.81 | 0
1172 | 2 | 1 | 0 | 0.031983 | 1.3081 | 200 | 1.3081 | 180 | 181.3081 | 0 | 0 | 253000 | 181.3081 | 97547.108 | 330.81 | 0
1173 | 2 | 1 | 0 | 0.028438 | 1.1631 | 200 | 1.1631 | 180 | 181.1631 | 0 | 0 | 252800 | 181.1631 | 97728.2712 | 150.81 | 0
1174 | 2 | 0 | 0 | 0.027034 | 1.1057 | 0 | 0 | 0 | 0 | 1.1057 | 0 | 252800 | 0 | 97728.2712 | 151.7684 | 0
1175 | 2 | 0 | 0 | 0.032446 | 1.327 | 0 | 0 | 0 | 0 | 1.327 | 0 | 252800 | 0 | 97728.2712 | 152.9187 | 0
1176 | 2 | 0 | 0 | 0.054826 | 2.2424 | 0 | 0 | 0 | 0 | 2.2424 | 0 | 252800 | 0 | 97728.2712 | 154.8624 | 0
1177 | 2 | 0 | 0 | 0.077477 | 3.1688 | 0 | 0 | 0 | 0 | 3.1688 | 0 | 252800 | 0 | 97728.2712 | 157.6091 | 0
1178 | 2 | 0 | 0 | 0.084314 | 3.4484 | 0 | 0 | 0 | 0 | 3.4484 | 0 | 252800 | 0 | 97728.2712 | 160.5982 | 0
1179 | 2 | 0 | 0 | 0.083375 | 3.41 | 0 | 0 | 0 | 0 | 3.41 | 0 | 252800 | 0 | 97728.2712 | 163.554 | 0
1180 | 2 | 0 | 0 | 0.12283 | 5.0238 | 0 | 0 | 0 | 0 | 5.0238 | 0 | 252800 | 0 | 97728.2712 | 167.9087 | 0
1181 | 2 | 0 | 0 | 0.2078 | 8.4991 | 0 | 0 | 0 | 0 | 8.4991 | 0 | 252800 | 0 | 97728.2712 | 175.2758 | 0
1182 | 2 | 0 | 0 | 0.21017 | 8.5959 | 0 | 0 | 0 | 0 | 8.5959 | 0 | 252800 | 0 | 97728.2712 | 182.7267 | 0
1183 | 2 | 0 | 0 | 0.23339 | 9.5458 | 0 | 0 | 0 | 0 | 9.5458 | 0 | 252800 | 0 | 97728.2712 | 191.001 | 0
1184 | 2 | 1 | 0.13185 | 0.18509 | 45.6473 | 200 | 45.6473 | 154.3527 | 200 | 0 | 0 | 252600 | 200 | 97928.2712 | 36.6483 | 0
1185 | 2 | 1 | 0.44537 | 0.25975 | 139.2475 | 200 | 139.2475 | 36.6483 | 175.8958 | 0 | 0 | 252400 | 175.8958 | 98104.1669 | 0 | 0
1186 | 2 | 0 | 0.78195 | 0.19031 | 233.6103 | 0 | 0 | 0 | 0 | 180 | 53.6103 | 252400 | 53.6103 | 98157.7772 | 156.024 | 0
1187 | 2 | 0 | 1 | 0.17375 | 295.9063 | 0 | 0 | 0 | 0 | 180 | 115.9063 | 252400 | 115.9063 | 98273.6836 | 312.048 | 0
1188 | 2 | 0 | 1 | 0.12749 | 294.0142 | 0 | 0 | 0 | 0 | 180 | 114.0142 | 252400 | 114.0142 | 98387.6978 | 468.072 | 0
1189 | 2 | 0 | 1 | 0.16951 | 295.7331 | 0 | 0 | 0 | 0 | 49.3055 | 200 | 252400 | 200 | 98587.6978 | 510.81 | 46.4276
1190 | 2 | 0 | 1 | 0.21318 | 297.5191 | 0 | 0 | 0 | 0 | 0 | 200 | 252400 | 200 | 98787.6978 | 510.81 | 97.5191
1191 | 2 | 0 | 1 | 0.14808 | 294.8567 | 0 | 0 | 0 | 0 | 0 | 200 | 252400 | 200 | 98987.6978 | 510.81 | 94.8567
1192 | 2 | 0 | 0.78195 | 0.17475 | 232.9741 | 0 | 0 | 0 | 0 | 0 | 200 | 252400 | 200 | 99187.6978 | 510.81 | 32.9741
1193 | 2 | 0 | 0.44537 | 0.19848 | 136.7414 | 0 | 0 | 0 | 0 | 0 | 136.7414 | 252400 | 136.7414 | 99324.4392 | 510.81 | 0
1194 | 2 | 0 | 0.13185 | 0.18394 | 45.6005 | 0 | 0 | 0 | 0 | 0 | 45.6005 | 252400 | 45.6005 | 99370.0396 | 510.81 | 0
1195 | 2 | 0 | 0 | 0.25783 | 10.5451 | 0 | 0 | 0 | 0 | 0 | 10.5451 | 252400 | 10.5451 | 99380.5847 | 510.81 | 0
1196 | 2 | 1 | 0 | 0.2076 | 8.4909 | 200 | 8.4909 | 180 | 188.4909 | 0 | 0 | 252200 | 188.4909 | 99569.0756 | 330.81 | 0
1197 | 2 | 1 | 0 | 0.19861 | 8.1231 | 200 | 8.1231 | 180 | 188.1231 | 0 | 0 | 252000 | 188.1231 | 99757.1987 | 150.81 | 0
1198 | 2 | 0 | 0 | 0.24158 | 9.8807 | 0 | 0 | 0 | 0 | 9.8807 | 0 | 252000 | 0 | 99757.1987 | 159.3746 | 0
1199 | 2 | 0 | 0 | 0.22748 | 9.3037 | 0 | 0 | 0 | 0 | 9.3037 | 0 | 252000 | 0 | 99757.1987 | 167.4391 | 0
1200 | 2 | 0 | 0 | 0.26217 | 10.7226 | 0 | 0 | 0 | 0 | 10.7226 | 0 | 252000 | 0 | 99757.1987 | 176.7334 | 0
1201 | 2 | 0 | 0 | 0.19911 | 8.1434 | 0 | 0 | 0 | 0 | 8.1434 | 0 | 252000 | 0 | 99757.1987 | 183.7921 | 0
1202 | 2 | 0 | 0 | 0.24665 | 10.0879 | 0 | 0 | 0 | 0 | 10.0879 | 0 | 252000 | 0 | 99757.1987 | 192.5364 | 0
1203 | 2 | 0 | 0 | 0.32429 | 13.2636 | 0 | 0 | 0 | 0 | 13.2636 | 0 | 252000 | 0 | 99757.1987 | 204.0333 | 0
1204 | 2 | 0 | 0 | 0.24242 | 9.9148 | 0 | 0 | 0 | 0 | 9.9148 | 0 | 252000 | 0 | 99757.1987 | 212.6274 | 0
1205 | 2 | 0 | 0 | 0.19822 | 8.1071 | 0 | 0 | 0 | 0 | 8.1071 | 0 | 252000 | 0 | 99757.1987 | 219.6546 | 0
1206 | 2 | 0 | 0 | 0.16058 | 6.5677 | 0 | 0 | 0 | 0 | 6.5677 | 0 | 252000 | 0 | 99757.1987 | 225.3475 | 0
1207 | 2 | 0 | 0 | 0.15081 | 6.1683 | 0 | 0 | 0 | 0 | 6.1683 | 0 | 252000 | 0 | 99757.1987 | 230.6942 | 0
1208 | 2 | 1 | 0.13766 | 0.20488 | 48.1353 | 200 | 48.1353 | 151.8647 | 200 | 0 | 0 | 251800 | 200 | 99957.1987 | 78.8295 | 0
1209 | 2 | 1 | 0.46501 | 0.20303 | 142.5982 | 200 | 142.5982 | 57.4018 | 200 | 0 | 0 | 251600 | 200 | 100157.1987 | 21.4276 | 0
1210 | 2 | 0 | 0.81642 | 0.24253 | 245.7019 | 0 | 0 | 0 | 0 | 180 | 65.7019 | 251600 | 65.7019 | 100222.9007 | 177.4516 | 0
1211 | 2 | 0 | 1 | 0.30407 | 301.2367 | 0 | 0 | 0 | 0 | 180 | 121.2367 | 251600 | 121.2367 | 100344.1373 | 333.4756 | 0
1212 | 2 | 0 | 1 | 0.30784 | 301.3908 | 0 | 0 | 0 | 0 | 180 | 121.3908 | 251600 | 121.3908 | 100465.5282 | 489.4996 | 0
1213 | 2 | 0 | 1 | 0.28442 | 300.4329 | 0 | 0 | 0 | 0 | 24.5851 | 200 | 251600 | 200 | 100665.5282 | 510.81 | 75.8478
1214 | 2 | 0 | 1 | 0.44746 | 307.101 | 0 | 0 | 0 | 0 | 0 | 200 | 251600 | 200 | 100865.5282 | 510.81 | 107.101
1215 | 2 | 0 | 1 | 0.47641 | 308.2854 | 0 | 0 | 0 | 0 | 0 | 200 | 251600 | 200 | 101065.5282 | 510.81 | 108.2854
1216 | 2 | 0 | 0.81642 | 0.59116 | 259.9609 | 0 | 0 | 0 | 0 | 0 | 200 | 251600 | 200 | 101265.5282 | 510.81 | 59.9609
1217 | 2 | 0 | 0.46501 | 0.55323 | 156.9215 | 0 | 0 | 0 | 0 | 0 | 156.9215 | 251600 | 156.9215 | 101422.4497 | 510.81 | 0
1218 | 2 | 0 | 0.13766 | 0.56195 | 62.7396 | 0 | 0 | 0 | 0 | 0 | 62.7396 | 251600 | 62.7396 | 101485.1892 | 510.81 | 0
1219 | 2 | 0 | 0 | 0.37353 | 15.2774 | 0 | 0 | 0 | 0 | 0 | 15.2774 | 251600 | 15.2774 | 101500.4667 | 510.81 | 0
1220 | 2 | 1 | 0 | 0.44633 | 18.2549 | 200 | 18.2549 | 180 | 198.2549 | 0 | 0 | 251400 | 198.2549 | 101698.7216 | 330.81 | 0
1221 | 2 | 1 | 0 | 0.3689 | 15.088 | 200 | 15.088 | 180 | 195.088 | 0 | 0 | 251200 | 195.088 | 101893.8096 | 150.81 | 0
1222 | 2 | 0 | 0 | 0.37306 | 15.258 | 0 | 0 | 0 | 0 | 15.258 | 0 | 251200 | 0 | 101893.8096 | 164.0356 | 0
1223 | 2 | 0 | 0 | 0.42717 | 17.4713 | 0 | 0 | 0 | 0 | 17.4713 | 0 | 251200 | 0 | 101893.8096 | 179.1797 | 0
1224 | 2 | 0 | 0 | 0.31987 | 13.0826 | 0 | 0 | 0 | 0 | 13.0826 | 0 | 251200 | 0 | 101893.8096 | 190.5197 | 0
1225 | 2 | 0 | 0 | 0.29867 | 12.2156 | 0 | 0 | 0 | 0 | 12.2156 | 0 | 251200 | 0 | 101893.8096 | 201.1082 | 0
1226 | 2 | 0 | 0 | 0.28318 | 11.5821 | 0 | 0 | 0 | 0 | 11.5821 | 0 | 251200 | 0 | 101893.8096 | 211.1476 | 0
1227 | 2 | 0 | 0 | 0.29158 | 11.9256 | 0 | 0 | 0 | 0 | 11.9256 | 0 | 251200 | 0 | 101893.8096 | 221.4847 | 0
1228 | 2 | 0 | 0 | 0.30696 | 12.5548 | 0 | 0 | 0 | 0 | 12.5548 | 0 | 251200 | 0 | 101893.8096 | 232.3672 | 0
1229 | 2 | 0 | 0 | 0.20905 | 8.5503 | 0 | 0 | 0 | 0 | 8.5503 | 0 | 251200 | 0 | 101893.8096 | 239.7786 | 0
1230 | 2 | 0 | 0 | 0.12666 | 5.1806 | 0 | 0 | 0 | 0 | 5.1806 | 0 | 251200 | 0 | 101893.8096 | 244.2691 | 0
1231 | 2 | 0 | 0 | 0.11736 | 4.8 | 0 | 0 | 0 | 0 | 4.8 | 0 | 251200 | 0 | 101893.8096 | 248.4297 | 0
1232 | 2 | 1 | 0.11824 | 0.2132 | 42.8662 | 200 | 42.8662 | 157.1338 | 200 | 0 | 0 | 251000 | 200 | 102093.8096 | 91.2959 | 0
1233 | 2 | 1 | 0.39939 | 0.21386 | 124.092 | 200 | 124.092 | 75.908 | 200 | 0 | 0 | 250800 | 200 | 102293.8096 | 15.3879 | 0
1234 | 2 | 0 | 0.70122 | 0.18579 | 210.1116 | 0 | 0 | 0 | 0 | 180 | 30.1116 | 250800 | 30.1116 | 102323.9211 | 171.4119 | 0
1235 | 2 | 0 | 0.96223 | 0.077877 | 281.0786 | 0 | 0 | 0 | 0 | 180 | 101.0786 | 250800 | 101.0786 | 102424.9998 | 327.4359 | 0
1236 | 2 | 0 | 1 | 0.087981 | 292.3984 | 0 | 0 | 0 | 0 | 180 | 112.3984 | 250800 | 112.3984 | 102537.3982 | 483.4599 | 0
1237 | 2 | 0 | 1 | 0.10647 | 293.1546 | 0 | 0 | 0 | 0 | 31.5529 | 200 | 250800 | 200 | 102737.3982 | 510.81 | 61.6017
1238 | 2 | 0 | 1 | 0.1126 | 293.4052 | 0 | 0 | 0 | 0 | 0 | 200 | 250800 | 200 | 102937.3982 | 510.81 | 93.4052
1239 | 2 | 0 | 0.96223 | 0.10493 | 282.1852 | 0 | 0 | 0 | 0 | 0 | 200 | 250800 | 200 | 103137.3982 | 510.81 | 82.1852
1240 | 2 | 0 | 0.70122 | 0.10583 | 206.8415 | 0 | 0 | 0 | 0 | 0 | 200 | 250800 | 200 | 103337.3982 | 510.81 | 6.8415
1241 | 2 | 0 | 0.39939 | 0.12468 | 120.4444 | 0 | 0 | 0 | 0 | 0 | 120.4444 | 250800 | 120.4444 | 103457.8425 | 510.81 | 0
1242 | 2 | 0 | 0.11824 | 0.093106 | 37.9543 | 0 | 0 | 0 | 0 | 0 | 37.9543 | 250800 | 37.9543 | 103495.7969 | 510.81 | 0
1243 | 2 | 0 | 0 | 0.099935 | 4.0873 | 0 | 0 | 0 | 0 | 0 | 4.0873 | 250800 | 4.0873 | 103499.8842 | 510.81 | 0
1244 | 2 | 1 | 0 | 0.12841 | 5.2519 | 200 | 5.2519 | 180 | 185.2519 | 0 | 0 | 250600 | 185.2519 | 103685.1361 | 330.81 | 0
1245 | 2 | 1 | 0 | 0.14217 | 5.8148 | 200 | 5.8148 | 180 | 185.8148 | 0 | 0 | 250400 | 185.8148 | 103870.9508 | 150.81 | 0
1246 | 2 | 0 | 0 | 0.16307 | 6.6694 | 0 | 0 | 0 | 0 | 6.6694 | 0 | 250400 | 0 | 103870.9508 | 156.5911 | 0
1247 | 2 | 0 | 0 | 0.15444 | 6.3166 | 0 | 0 | 0 | 0 | 6.3166 | 0 | 250400 | 0 | 103870.9508 | 162.0663 | 0
1248 | 2 | 0 | 0 | 0.15387 | 6.2932 | 0 | 0 | 0 | 0 | 6.2932 | 0 | 250400 | 0 | 103870.9508 | 167.5212 | 0
1249 | 2 | 0 | 0 | 0.14238 | 5.8233 | 0 | 0 | 0 | 0 | 5.8233 | 0 | 250400 | 0 | 103870.9508 | 172.5688 | 0
1250 | 2 | 0 | 0 | 0.12351 | 5.0517 | 0 | 0 | 0 | 0 | 5.0517 | 0 | 250400 | 0 | 103870.9508 | 176.9476 | 0
1251 | 2 | 0 | 0 | 0.14364 | 5.8747 | 0 | 0 | 0 | 0 | 5.8747 | 0 | 250400 | 0 | 103870.9508 | 182.0398 | 0
1252 | 2 | 0 | 0 | 0.17214 | 7.0403 | 0 | 0 | 0 | 0 | 7.0403 | 0 | 250400 | 0 | 103870.9508 | 188.1424 | 0
1253 | 2 | 0 | 0 | 0.13998 | 5.7253 | 0 | 0 | 0 | 0 | 5.7253 | 0 | 250400 | 0 | 103870.9508 | 193.1051 | 0
1254 | 2 | 0 | 0 | 0.13522 | 5.5305 | 0 | 0 | 0 | 0 | 5.5305 | 0 | 250400 | 0 | 103870.9508 | 197.8989 | 0
1255 | 2 | 0 | 0 | 0.11969 | 4.8953 | 0 | 0 | 0 | 0 | 4.8953 | 0 | 250400 | 0 | 103870.9508 | 202.1421 | 0
1256 | 2 | 1 | 0.099927 | 0.10873 | 33.3061 | 200 | 33.3061 | 166.6939 | 200 | 0 | 0 | 250200 | 200 | 104070.9508 | 35.4482 | 0
1257 | 2 | 1 | 0.33755 | 0.12513 | 102.6023 | 200 | 102.6023 | 35.4482 | 138.0505 | 0 | 0 | 250000 | 138.0505 | 104209.0013 | 0 | 0
1258 | 2 | 0 | 0.59264 | 0.16237 | 177.7955 | 0 | 0 | 0 | 0 | 177.7955 | 0 | 250000 | 0 | 104209.0013 | 154.1131 | 0
1259 | 2 | 0 | 0.81324 | 0.16592 | 241.6496 | 0 | 0 | 0 | 0 | 180 | 61.6496 | 250000 | 61.6496 | 104270.651 | 310.1371 | 0
1260 | 2 | 0 | 0.96159 | 0.17462 | 284.8497 | 0 | 0 | 0 | 0 | 180 | 104.8497 | 250000 | 104.8497 | 104375.5007 | 466.1611 | 0
1261 | 2 | 0 | 1 | 0.15573 | 295.1693 | 0 | 0 | 0 | 0 | 51.51 | 200 | 250000 | 200 | 104575.5007 | 510.81 | 43.6593
1262 | 2 | 0 | 0.96159 | 0.11849 | 282.5539 | 0 | 0 | 0 | 0 | 0 | 200 | 250000 | 200 | 104775.5007 | 510.81 | 82.5539
1263 | 2 | 0 | 0.81324 | 0.17048 | 241.8361 | 0 | 0 | 0 | 0 | 0 | 200 | 250000 | 200 | 104975.5007 | 510.81 | 41.8361
1264 | 2 | 0 | 0.59264 | 0.17559 | 178.3364 | 0 | 0 | 0 | 0 | 0 | 178.3364 | 250000 | 178.3364 | 105153.8371 | 510.81 | 0
1265 | 2 | 0 | 0.33755 | 0.12442 | 102.5733 | 0 | 0 | 0 | 0 | 0 | 102.5733 | 250000 | 102.5733 | 105256.4104 | 510.81 | 0
1266 | 2 | 0 | 0.099927 | 0.10992 | 33.3546 | 0 | 0 | 0 | 0 | 0 | 33.3546 | 250000 | 33.3546 | 105289.765 | 510.81 | 0
1267 | 2 | 0 | 0 | 0.17844 | 7.2983 | 0 | 0 | 0 | 0 | 0 | 7.2983 | 250000 | 7.2983 | 105297.0633 | 510.81 | 0
1268 | 2 | 1 | 0 | 0.18956 | 7.7532 | 200 | 7.7532 | 180 | 187.7532 | 0 | 0 | 249800 | 187.7532 | 105484.8164 | 330.81 | 0
1269 | 2 | 1 | 0 | 0.37074 | 15.1631 | 200 | 15.1631 | 180 | 195.1631 | 0 | 0 | 249600 | 195.1631 | 105679.9796 | 150.81 | 0
1270 | 2 | 0 | 0 | 0.38615 | 15.7936 | 0 | 0 | 0 | 0 | 15.7936 | 0 | 249600 | 0 | 105679.9796 | 164.4999 | 0
1271 | 2 | 0 | 0 | 0.37478 | 15.3284 | 0 | 0 | 0 | 0 | 15.3284 | 0 | 249600 | 0 | 105679.9796 | 177.7865 | 0
1272 | 2 | 0 | 0 | 0.33126 | 13.5484 | 0 | 0 | 0 | 0 | 13.5484 | 0 | 249600 | 0 | 105679.9796 | 189.5302 | 0
1273 | 2 | 0 | 0 | 0.24361 | 9.9635 | 0 | 0 | 0 | 0 | 9.9635 | 0 | 249600 | 0 | 105679.9796 | 198.1666 | 0
1274 | 2 | 0 | 0 | 0.28696 | 11.7367 | 0 | 0 | 0 | 0 | 11.7367 | 0 | 249600 | 0 | 105679.9796 | 208.34 | 0
1275 | 2 | 0 | 0 | 0.38689 | 15.8239 | 0 | 0 | 0 | 0 | 15.8239 | 0 | 249600 | 0 | 105679.9796 | 222.0561 | 0
1276 | 2 | 0 | 0 | 0.43878 | 17.946 | 0 | 0 | 0 | 0 | 17.946 | 0 | 249600 | 0 | 105679.9796 | 237.6117 | 0
1277 | 2 | 0 | 0 | 0.36237 | 14.8211 | 0 | 0 | 0 | 0 | 14.8211 | 0 | 249600 | 0 | 105679.9796 | 250.4586 | 0
1278 | 2 | 0 | 0 | 0.49102 | 20.0826 | 0 | 0 | 0 | 0 | 20.0826 | 0 | 249600 | 0 | 105679.9796 | 267.8661 | 0
1279 | 2 | 0 | 0 | 0.49765 | 20.3537 | 0 | 0 | 0 | 0 | 20.3537 | 0 | 249600 | 0 | 105679.9796 | 285.5087 | 0
1280 | 2 | 1 | 0.14006 | 0.60199 | 65.0706 | 200 | 65.0706 | 134.9294 | 200 | 0 | 0 | 249400 | 200 | 105879.9796 | 150.5793 | 0
1281 | 2 | 1 | 0.47312 | 0.38849 | 152.5265 | 200 | 152.5265 | 47.4735 | 200 | 0 | 0 | 249200 | 200 | 106079.9796 | 103.1058 | 0
1282 | 2 | 0 | 0.83066 | 0.37979 | 255.4291 | 0 | 0 | 0 | 0 | 180 | 75.4291 | 249200 | 75.4291 | 106155.4087 | 259.1298 | 0
1283 | 2 | 0 | 1 | 0.31106 | 301.5225 | 0 | 0 | 0 | 0 | 180 | 121.5225 | 249200 | 121.5225 | 106276.9312 | 415.1538 | 0
1284 | 2 | 0 | 1 | 0.40437 | 305.3388 | 0 | 0 | 0 | 0 | 110.3555 | 194.9833 | 249200 | 194.9833 | 106471.9144 | 510.81 | 0
1285 | 2 | 0 | 1 | 0.44269 | 306.9059 | 0 | 0 | 0 | 0 | 0 | 200 | 249200 | 200 | 106671.9144 | 510.81 | 106.9059
1286 | 2 | 0 | 1 | 0.82494 | 322.54 | 0 | 0 | 0 | 0 | 0 | 200 | 249200 | 200 | 106871.9144 | 510.81 | 122.54
1287 | 2 | 0 | 1 | 0.97557 | 328.7006 | 0 | 0 | 0 | 0 | 0 | 200 | 249200 | 200 | 107071.9144 | 510.81 | 128.7006
1288 | 2 | 0 | 0.83066 | 1 | 280.7958 | 0 | 0 | 0 | 0 | 0 | 200 | 249200 | 200 | 107271.9144 | 510.81 | 80.7958
1289 | 2 | 0 | 0.47312 | 0.65149 | 163.2832 | 0 | 0 | 0 | 0 | 0 | 163.2832 | 249200 | 163.2832 | 107435.1976 | 510.81 | 0
1290 | 2 | 0 | 0.14006 | 0.51837 | 61.6507 | 0 | 0 | 0 | 0 | 0 | 61.6507 | 249200 | 61.6507 | 107496.8483 | 510.81 | 0
1291 | 2 | 0 | 0 | 0.52523 | 21.4819 | 0 | 0 | 0 | 0 | 0 | 21.4819 | 249200 | 21.4819 | 107518.3302 | 510.81 | 0
1292 | 2 | 1 | 0 | 0.43982 | 17.9888 | 200 | 17.9888 | 180 | 197.9888 | 0 | 0 | 249000 | 197.9888 | 107716.319 | 330.81 | 0
1293 | 2 | 1 | 0 | 0.3478 | 14.2251 | 200 | 14.2251 | 180 | 194.2251 | 0 | 0 | 248800 | 194.2251 | 107910.5441 | 150.81 | 0
1294 | 2 | 0 | 0 | 0.28356 | 11.5974 | 0 | 0 | 0 | 0 | 11.5974 | 0 | 248800 | 0 | 107910.5441 | 160.8626 | 0
1295 | 2 | 0 | 0 | 0.21796 | 8.9146 | 0 | 0 | 0 | 0 | 8.9146 | 0 | 248800 | 0 | 107910.5441 | 168.5898 | 0
1296 | 2 | 0 | 0 | 0.11445 | 4.6812 | 0 | 0 | 0 | 0 | 4.6812 | 0 | 248800 | 0 | 107910.5441 | 172.6475 | 0
1297 | 2 | 0 | 0 | 0.098004 | 4.0084 | 0 | 0 | 0 | 0 | 4.0084 | 0 | 248800 | 0 | 107910.5441 | 176.1219 | 0
1298 | 2 | 0 | 0 | 0.18776 | 7.6792 | 0 | 0 | 0 | 0 | 7.6792 | 0 | 248800 | 0 | 107910.5441 | 182.7783 | 0
1299 | 2 | 0 | 0 | 0.2249 | 9.1985 | 0 | 0 | 0 | 0 | 9.1985 | 0 | 248800 | 0 | 107910.5441 | 190.7516 | 0
1300 | 2 | 0 | 0 | 0.16191 | 6.6222 | 0 | 0 | 0 | 0 | 6.6222 | 0 | 248800 | 0 | 107910.5441 | 196.4917 | 0
1301 | 2 | 0 | 0 | 0.19904 | 8.1408 | 0 | 0 | 0 | 0 | 8.1408 | 0 | 248800 | 0 | 107910.5441 | 203.5481 | 0
1302 | 2 | 0 | 0 | 0.22671 | 9.2726 | 0 | 0 | 0 | 0 | 9.2726 | 0 | 248800 | 0 | 107910.5441 | 211.5856 | 0
1303 | 2 | 0 | 0 | 0.30758 | 12.5799 | 0 | 0 | 0 | 0 | 12.5799 | 0 | 248800 | 0 | 107910.5441 | 222.4899 | 0
1304 | 2 | 1 | 0.14446 | 0.37478 | 57.0496 | 200 | 57.0496 | 142.9504 | 200 | 0 | 0 | 248600 | 200 | 108110.5441 | 79.5395 | 0
1305 | 2 | 1 | 0.48799 | 0.31882 | 153.9714 | 200 | 153.9714 | 46.0286 | 200 | 0 | 0 | 248400 | 200 | 108310.5441 | 33.5109 | 0
1306 | 2 | 0 | 0.85677 | 0.2446 | 257.4401 | 0 | 0 | 0 | 0 | 180 | 77.4401 | 248400 | 77.4401 | 108387.9842 | 189.5349 | 0
1307 | 2 | 0 | 1 | 0.33132 | 302.3512 | 0 | 0 | 0 | 0 | 180 | 122.3512 | 248400 | 122.3512 | 108510.3354 | 345.5589 | 0
1308 | 2 | 0 | 1 | 0.22951 | 298.187 | 0 | 0 | 0 | 0 | 180 | 118.187 | 248400 | 118.187 | 108628.5224 | 501.5829 | 0
1309 | 2 | 0 | 1 | 0.27611 | 300.0928 | 0 | 0 | 0 | 0 | 10.6451 | 200 | 248400 | 200 | 108828.5224 | 510.81 | 89.4477
1310 | 2 | 0 | 1 | 0.26357 | 299.58 | 0 | 0 | 0 | 0 | 0 | 200 | 248400 | 200 | 109028.5224 | 510.81 | 99.58
1311 | 2 | 0 | 1 | 0.25375 | 299.1782 | 0 | 0 | 0 | 0 | 0 | 200 | 248400 | 200 | 109228.5224 | 510.81 | 99.1782
1312 | 2 | 0 | 0.85677 | 0.32682 | 260.8027 | 0 | 0 | 0 | 0 | 0 | 200 | 248400 | 200 | 109428.5224 | 510.81 | 60.8027
1313 | 2 | 0 | 0.48799 | 0.2311 | 150.3839 | 0 | 0 | 0 | 0 | 0 | 150.3839 | 248400 | 150.3839 | 109578.9063 | 510.81 | 0
1314 | 2 | 0 | 0.14446 | 0.25211 | 52.0321 | 0 | 0 | 0 | 0 | 0 | 52.0321 | 248400 | 52.0321 | 109630.9384 | 510.81 | 0
1315 | 2 | 0 | 0 | 0.25668 | 10.4983 | 0 | 0 | 0 | 0 | 0 | 10.4983 | 248400 | 10.4983 | 109641.4367 | 510.81 | 0
1316 | 2 | 1 | 0 | 0.33069 | 13.5251 | 200 | 13.5251 | 180 | 193.5251 | 0 | 0 | 248200 | 193.5251 | 109834.9618 | 330.81 | 0
1317 | 2 | 1 | 0 | 0.30469 | 12.4618 | 200 | 12.4618 | 180 | 192.4618 | 0 | 0 | 248000 | 192.4618 | 110027.4236 | 150.81 | 0
1318 | 2 | 0 | 0 | 0.3884 | 15.8856 | 0 | 0 | 0 | 0 | 15.8856 | 0 | 248000 | 0 | 110027.4236 | 164.5797 | 0
1319 | 2 | 0 | 0 | 0.41276 | 16.882 | 0 | 0 | 0 | 0 | 16.882 | 0 | 248000 | 0 | 110027.4236 | 179.213 | 0
1320 | 2 | 0 | 0 | 0.38573 | 15.7762 | 0 | 0 | 0 | 0 | 15.7762 | 0 | 248000 | 0 | 110027.4236 | 192.8878 | 0
1321 | 2 | 0 | 0 | 0.34887 | 14.2687 | 0 | 0 | 0 | 0 | 14.2687 | 0 | 248000 | 0 | 110027.4236 | 205.256 | 0
1322 | 2 | 0 | 0 | 0.16779 | 6.8625 | 0 | 0 | 0 | 0 | 6.8625 | 0 | 248000 | 0 | 110027.4236 | 211.2044 | 0
1323 | 2 | 0 | 0 | 0.18872 | 7.7185 | 0 | 0 | 0 | 0 | 7.7185 | 0 | 248000 | 0 | 110027.4236 | 217.8948 | 0
1324 | 2 | 0 | 0 | 0.16161 | 6.61 | 0 | 0 | 0 | 0 | 6.61 | 0 | 248000 | 0 | 110027.4236 | 223.6244 | 0
1325 | 2 | 0 | 0 | 0.20252 | 8.2831 | 0 | 0 | 0 | 0 | 8.2831 | 0 | 248000 | 0 | 110027.4236 | 230.8042 | 0
1326 | 2 | 0 | 0 | 0.28488 | 11.6516 | 0 | 0 | 0 | 0 | 11.6516 | 0 | 248000 | 0 | 110027.4236 | 240.9038 | 0
1327 | 2 | 0 | 0 | 0.22361 | 9.1457 | 0 | 0 | 0 | 0 | 9.1457 | 0 | 248000 | 0 | 110027.4236 | 248.8313 | 0
1328 | 2 | 1 | 0.11809 | 0.17369 | 41.2093 | 200 | 41.2093 | 158.7907 | 200 | 0 | 0 | 247800 | 200 | 110227.4236 | 90.0405 | 0
1329 | 2 | 1 | 0.39891 | 0.17331 | 122.2948 | 200 | 122.2948 | 77.7052 | 200 | 0 | 0 | 247600 | 200 | 110427.4236 | 12.3353 | 0
1330 | 2 | 0 | 0.70038 | 0.17973 | 209.6204 | 0 | 0 | 0 | 0 | 180 | 29.6204 | 247600 | 29.6204 | 110457.044 | 168.3593 | 0
1331 | 2 | 0 | 0.96108 | 0.27385 | 288.7601 | 0 | 0 | 0 | 0 | 180 | 108.7601 | 247600 | 108.7601 | 110565.8041 | 324.3833 | 0
1332 | 2 | 0 | 1 | 0.19816 | 296.9047 | 0 | 0 | 0 | 0 | 180 | 116.9047 | 247600 | 116.9047 | 110682.7088 | 480.4073 | 0
1333 | 2 | 0 | 1 | 0.18 | 296.1618 | 0 | 0 | 0 | 0 | 35.0746 | 200 | 247600 | 200 | 110882.7088 | 510.81 | 61.0872
1334 | 2 | 0 | 1 | 0.17539 | 295.9735 | 0 | 0 | 0 | 0 | 0 | 200 | 247600 | 200 | 111082.7088 | 510.81 | 95.9735
1335 | 2 | 0 | 0.96108 | 0.24852 | 287.724 | 0 | 0 | 0 | 0 | 0 | 200 | 247600 | 200 | 111282.7088 | 510.81 | 87.724
1336 | 2 | 0 | 0.70038 | 0.23977 | 212.0762 | 0 | 0 | 0 | 0 | 0 | 200 | 247600 | 200 | 111482.7088 | 510.81 | 12.0762
1337 | 2 | 0 | 0.39891 | 0.28962 | 127.0519 | 0 | 0 | 0 | 0 | 0 | 127.0519 | 247600 | 127.0519 | 111609.7607 | 510.81 | 0
1338 | 2 | 0 | 0.11809 | 0.24248 | 44.0226 | 0 | 0 | 0 | 0 | 0 | 44.0226 | 247600 | 44.0226 | 111653.7833 | 510.81 | 0
1339 | 2 | 0 | 0 | 0.17649 | 7.2183 | 0 | 0 | 0 | 0 | 0 | 7.2183 | 247600 | 7.2183 | 111661.0016 | 510.81 | 0
1340 | 2 | 1 | 0 | 0.17581 | 7.1905 | 200 | 7.1905 | 180 | 187.1905 | 0 | 0 | 247400 | 187.1905 | 111848.1922 | 330.81 | 0
1341 | 2 | 1 | 0 | 0.18105 | 7.4051 | 200 | 7.4051 | 180 | 187.4051 | 0 | 0 | 247200 | 187.4051 | 112035.5973 | 150.81 | 0
1342 | 2 | 0 | 0 | 0.18226 | 7.4546 | 0 | 0 | 0 | 0 | 7.4546 | 0 | 247200 | 0 | 112035.5973 | 157.2716 | 0
1343 | 2 | 0 | 0 | 0.15976 | 6.5344 | 0 | 0 | 0 | 0 | 6.5344 | 0 | 247200 | 0 | 112035.5973 | 162.9356 | 0
1344 | 2 | 0 | 0 | 0.18195 | 7.4416 | 0 | 0 | 0 | 0 | 7.4416 | 0 | 247200 | 0 | 112035.5973 | 169.386 | 0
1345 | 2 | 0 | 0 | 0.18594 | 7.6048 | 0 | 0 | 0 | 0 | 7.6048 | 0 | 247200 | 0 | 112035.5973 | 175.9778 | 0
1346 | 2 | 0 | 0 | 0.14585 | 5.9651 | 0 | 0 | 0 | 0 | 5.9651 | 0 | 247200 | 0 | 112035.5973 | 181.1484 | 0
1347 | 2 | 0 | 0 | 0.16402 | 6.7086 | 0 | 0 | 0 | 0 | 6.7086 | 0 | 247200 | 0 | 112035.5973 | 186.9634 | 0
1348 | 2 | 0 | 0 | 0.16983 | 6.946 | 0 | 0 | 0 | 0 | 6.946 | 0 | 247200 | 0 | 112035.5973 | 192.9841 | 0
1349 | 2 | 0 | 0 | 0.24296 | 9.9371 | 0 | 0 | 0 | 0 | 9.9371 | 0 | 247200 | 0 | 112035.5973 | 201.5976 | 0
1350 | 2 | 0 | 0 | 0.19399 | 7.9342 | 0 | 0 | 0 | 0 | 7.9342 | 0 | 247200 | 0 | 112035.5973 | 208.4749 | 0
1351 | 2 | 0 | 0 | 0.16353 | 6.6885 | 0 | 0 | 0 | 0 | 6.6885 | 0 | 247200 | 0 | 112035.5973 | 214.2725 | 0
1352 | 2 | 1 | 0.11719 | 0.34748 | 48.0553 | 200 | 48.0553 | 151.9447 | 200 | 0 | 0 | 247000 | 200 | 112235.5973 | 62.3279 | 0
1353 | 2 | 1 | 0.39585 | 0.29785 | 126.5035 | 200 | 126.5035 | 62.3279 | 188.8314 | 0 | 0 | 246800 | 188.8314 | 112424.4286 | 0 | 0
1354 | 2 | 0 | 0.695 | 0.2655 | 211.5748 | 0 | 0 | 0 | 0 | 180 | 31.5748 | 246800 | 31.5748 | 112456.0034 | 156.024 | 0
1355 | 2 | 0 | 0.9537 | 0.23184 | 284.9095 | 0 | 0 | 0 | 0 | 180 | 104.9095 | 246800 | 104.9095 | 112560.9129 | 312.048 | 0
1356 | 2 | 0 | 1 | 0.23313 | 298.3351 | 0 | 0 | 0 | 0 | 180 | 118.3351 | 246800 | 118.3351 | 112679.248 | 468.072 | 0
1357 | 2 | 0 | 1 | 0.26642 | 299.6965 | 0 | 0 | 0 | 0 | 49.3055 | 200 | 246800 | 200 | 112879.248 | 510.81 | 50.391
1358 | 2 | 0 | 1 | 0.25749 | 299.3313 | 0 | 0 | 0 | 0 | 0 | 200 | 246800 | 200 | 113079.248 | 510.81 | 99.3313
1359 | 2 | 0 | 0.9537 | 0.31968 | 288.5024 | 0 | 0 | 0 | 0 | 0 | 200 | 246800 | 200 | 113279.248 | 510.81 | 88.5024
1360 | 2 | 0 | 0.695 | 0.42583 | 218.1323 | 0 | 0 | 0 | 0 | 0 | 200 | 246800 | 200 | 113479.248 | 510.81 | 18.1323
1361 | 2 | 0 | 0.39585 | 0.37479 | 129.6506 | 0 | 0 | 0 | 0 | 0 | 129.6506 | 246800 | 129.6506 | 113608.8986 | 510.81 | 0
1362 | 2 | 0 | 0.11719 | 0.36176 | 48.6391 | 0 | 0 | 0 | 0 | 0 | 48.6391 | 246800 | 48.6391 | 113657.5377 | 510.81 | 0
1363 | 2 | 0 | 0 | 0.38542 | 15.7636 | 0 | 0 | 0 | 0 | 0 | 15.7636 | 246800 | 15.7636 | 113673.3013 | 510.81 | 0
1364 | 2 | 1 | 0 | 0.28569 | 11.6848 | 200 | 11.6848 | 180 | 191.6848 | 0 | 0 | 246600 | 191.6848 | 113864.9861 | 330.81 | 0
1365 | 2 | 1 | 0 | 0.16527 | 6.7594 | 200 | 6.7594 | 180 | 186.7594 | 0 | 0 | 246400 | 186.7594 | 114051.7456 | 150.81 | 0
1366 | 2 | 0 | 0 | 0.13833 | 5.6577 | 0 | 0 | 0 | 0 | 5.6577 | 0 | 246400 | 0 | 114051.7456 | 155.7141 | 0
1367 | 2 | 0 | 0 | 0.10822 | 4.4263 | 0 | 0 | 0 | 0 | 4.4263 | 0 | 246400 | 0 | 114051.7456 | 159.5508 | 0
1368 | 2 | 0 | 0 | 0.10149 | 4.1509 | 0 | 0 | 0 | 0 | 4.1509 | 0 | 246400 | 0 | 114051.7456 | 163.1489 | 0
1369 | 2 | 0 | 0 | 0.072129 | 2.9501 | 0 | 0 | 0 | 0 | 2.9501 | 0 | 246400 | 0 | 114051.7456 | 165.706 | 0
1370 | 2 | 0 | 0 | 0.082752 | 3.3846 | 0 | 0 | 0 | 0 | 3.3846 | 0 | 246400 | 0 | 114051.7456 | 168.6397 | 0
1371 | 2 | 0 | 0 | 0.11409 | 4.6662 | 0 | 0 | 0 | 0 | 4.6662 | 0 | 246400 | 0 | 114051.7456 | 172.6844 | 0
1372 | 2 | 0 | 0 | 0.094529 | 3.8662 | 0 | 0 | 0 | 0 | 3.8662 | 0 | 246400 | 0 | 114051.7456 | 176.0356 | 0
1373 | 2 | 0 | 0 | 0.075192 | 3.0754 | 0 | 0 | 0 | 0 | 3.0754 | 0 | 246400 | 0 | 114051.7456 | 178.7014 | 0
1374 | 2 | 0 | 0 | 0.073693 | 3.014 | 0 | 0 | 0 | 0 | 3.014 | 0 | 246400 | 0 | 114051.7456 | 181.3139 | 0
1375 | 2 | 0 | 0 | 0.068342 | 2.7952 | 0 | 0 | 0 | 0 | 2.7952 | 0 | 246400 | 0 | 114051.7456 | 183.7368 | 0
1376 | 2 | 1 | 0.13979 | 0.089842 | 44.0459 | 200 | 44.0459 | 155.9541 | 200 | 0 | 0 | 246200 | 200 | 114251.7456 | 27.7827 | 0
1377 | 2 | 1 | 0.4722 | 0.15345 | 142.6489 | 200 | 142.6489 | 27.7827 | 170.4316 | 0 | 0 | 246000 | 170.4316 | 114422.1772 | 0 | 0
1378 | 2 | 0 | 0.82906 | 0.15855 | 245.9164 | 0 | 0 | 0 | 0 | 180 | 65.9164 | 246000 | 65.9164 | 114488.0936 | 156.024 | 0
1379 | 2 | 0 | 1 | 0.1259 | 293.9494 | 0 | 0 | 0 | 0 | 180 | 113.9494 | 246000 | 113.9494 | 114602.0429 | 312.048 | 0
1380 | 2 | 0 | 1 | 0.18479 | 296.3578 | 0 | 0 | 0 | 0 | 180 | 116.3578 | 246000 | 116.3578 | 114718.4008 | 468.072 | 0
1381 | 2 | 0 | 1 | 0.16097 | 295.3838 | 0 | 0 | 0 | 0 | 49.3055 | 200 | 246000 | 200 | 114918.4008 | 510.81 | 46.0783
1382 | 2 | 0 | 1 | 0.16815 | 295.6775 | 0 | 0 | 0 | 0 | 0 | 200 | 246000 | 200 | 115118.4008 | 510.81 | 95.6775
1383 | 2 | 0 | 1 | 0.14749 | 294.8323 | 0 | 0 | 0 | 0 | 0 | 200 | 246000 | 200 | 115318.4008 | 510.81 | 94.8323
1384 | 2 | 0 | 0.82906 | 0.16109 | 246.0204 | 0 | 0 | 0 | 0 | 0 | 200 | 246000 | 200 | 115518.4008 | 510.81 | 46.0204
1385 | 2 | 0 | 0.4722 | 0.13331 | 141.8252 | 0 | 0 | 0 | 0 | 0 | 141.8252 | 246000 | 141.8252 | 115660.226 | 510.81 | 0
1386 | 2 | 0 | 0.13979 | 0.092686 | 44.1622 | 0 | 0 | 0 | 0 | 0 | 44.1622 | 246000 | 44.1622 | 115704.3882 | 510.81 | 0
1387 | 2 | 0 | 0 | 0.094948 | 3.8834 | 0 | 0 | 0 | 0 | 0 | 3.8834 | 246000 | 3.8834 | 115708.2716 | 510.81 | 0
1388 | 2 | 1 | 0 | 0.076568 | 3.1316 | 200 | 3.1316 | 180 | 183.1316 | 0 | 0 | 245800 | 183.1316 | 115891.4032 | 330.81 | 0
1389 | 2 | 1 | 0 | 0.11791 | 4.8224 | 200 | 4.8224 | 180 | 184.8224 | 0 | 0 | 245600 | 184.8224 | 116076.2256 | 150.81 | 0
1390 | 2 | 0 | 0 | 0.092702 | 3.7915 | 0 | 0 | 0 | 0 | 3.7915 | 0 | 245600 | 0 | 116076.2256 | 154.0965 | 0
1391 | 2 | 0 | 0 | 0.076501 | 3.1289 | 0 | 0 | 0 | 0 | 3.1289 | 0 | 245600 | 0 | 116076.2256 | 156.8086 | 0
1392 | 2 | 0 | 0 | 0.087459 | 3.5771 | 0 | 0 | 0 | 0 | 3.5771 | 0 | 245600 | 0 | 116076.2256 | 159.9092 | 0
1393 | 2 | 0 | 0 | 0.08143 | 3.3305 | 0 | 0 | 0 | 0 | 3.3305 | 0 | 245600 | 0 | 116076.2256 | 162.7961 | 0
1394 | 2 | 0 | 0 | 0.065699 | 2.6871 | 0 | 0 | 0 | 0 | 2.6871 | 0 | 245600 | 0 | 116076.2256 | 165.1252 | 0
1395 | 2 | 0 | 0 | 0.053743 | 2.1981 | 0 | 0 | 0 | 0 | 2.1981 | 0 | 245600 | 0 | 116076.2256 | 167.0306 | 0
1396 | 2 | 0 | 0 | 0.074169 | 3.0335 | 0 | 0 | 0 | 0 | 3.0335 | 0 | 245600 | 0 | 116076.2256 | 169.66 | 0
1397 | 2 | 0 | 0 | 0.068664 | 2.8084 | 0 | 0 | 0 | 0 | 2.8084 | 0 | 245600 | 0 | 116076.2256 | 172.0943 | 0
1398 | 2 | 0 | 0 | 0.061559 | 2.5178 | 0 | 0 | 0 | 0 | 2.5178 | 0 | 245600 | 0 | 116076.2256 | 174.2767 | 0
1399 | 2 | 0 | 0 | 0.087762 | 3.5895 | 0 | 0 | 0 | 0 | 3.5895 | 0 | 245600 | 0 | 116076.2256 | 177.388 | 0
1400 | 2 | 1 | 0.14693 | 0.086613 | 45.9756 | 200 | 45.9756 | 154.0244 | 200 | 0 | 0 | 245400 | 200 | 116276.2256 | 23.3636 | 0
1401 | 2 | 1 | 0.49632 | 0.16275 | 149.995 | 200 | 149.995 | 23.3636 | 173.3586 | 0 | 0 | 245200 | 173.3586 | 116449.5842 | 0 | 0
1402 | 2 | 0 | 0.8714 | 0.26668 | 262.568 | 0 | 0 | 0 | 0 | 180 | 82.568 | 245200 | 82.568 | 116532.1522 | 156.024 | 0
1403 | 2 | 0 | 1 | 0.29925 | 301.0393 | 0 | 0 | 0 | 0 | 180 | 121.0393 | 245200 | 121.0393 | 116653.1915 | 312.048 | 0
1404 | 2 | 0 | 1 | 0.27032 | 299.856 | 0 | 0 | 0 | 0 | 180 | 119.856 | 245200 | 119.856 | 116773.0475 | 468.072 | 0
1405 | 2 | 0 | 1 | 0.34241 | 302.8044 | 0 | 0 | 0 | 0 | 49.3055 | 200 | 245200 | 200 | 116973.0475 | 510.81 | 53.499
1406 | 2 | 0 | 1 | 0.40898 | 305.5272 | 0 | 0 | 0 | 0 | 0 | 200 | 245200 | 200 | 117173.0475 | 510.81 | 105.5272
1407 | 2 | 0 | 1 | 0.28891 | 300.6166 | 0 | 0 | 0 | 0 | 0 | 200 | 245200 | 200 | 117373.0475 | 510.81 | 100.6166
1408 | 2 | 0 | 0.8714 | 0.33748 | 265.4637 | 0 | 0 | 0 | 0 | 0 | 200 | 245200 | 200 | 117573.0475 | 510.81 | 65.4637
1409 | 2 | 0 | 0.49632 | 0.2366 | 153.0153 | 0 | 0 | 0 | 0 | 0 | 153.0153 | 245200 | 153.0153 | 117726.0628 | 510.81 | 0
1410 | 2 | 0 | 0.14693 | 0.24496 | 52.4521 | 0 | 0 | 0 | 0 | 0 | 52.4521 | 245200 | 52.4521 | 117778.5149 | 510.81 | 0
1411 | 2 | 0 | 0 | 0.29186 | 11.937 | 0 | 0 | 0 | 0 | 0 | 11.937 | 245200 | 11.937 | 117790.4519 | 510.81 | 0
1412 | 2 | 1 | 0 | 0.3348 | 13.6932 | 200 | 13.6932 | 180 | 193.6932 | 0 | 0 | 245000 | 193.6932 | 117984.1451 | 330.81 | 0
1413 | 2 | 1 | 0 | 0.34931 | 14.2866 | 200 | 14.2866 | 180 | 194.2866 | 0 | 0 | 244800 | 194.2866 | 118178.4317 | 150.81 | 0
1414 | 2 | 0 | 0 | 0.29211 | 11.9473 | 0 | 0 | 0 | 0 | 11.9473 | 0 | 244800 | 0 | 118178.4317 | 161.1659 | 0
1415 | 2 | 0 | 0 | 0.20384 | 8.3369 | 0 | 0 | 0 | 0 | 8.3369 | 0 | 244800 | 0 | 118178.4317 | 168.3923 | 0
1416 | 2 | 0 | 0 | 0.17126 | 7.0044 | 0 | 0 | 0 | 0 | 7.0044 | 0 | 244800 | 0 | 118178.4317 | 174.4637 | 0
1417 | 3 | 0 | 0 | 0.30861 | 12.6224 | 0 | 0 | 0 | 0 | 12.6224 | 0 | 244800 | 0 | 118178.4317 | 185.4048 | 0
1418 | 3 | 0 | 0 | 0.22962 | 9.3915 | 0 | 0 | 0 | 0 | 9.3915 | 0 | 244800 | 0 | 118178.4317 | 193.5453 | 0
1419 | 3 | 0 | 0 | 0.17615 | 7.2045 | 0 | 0 | 0 | 0 | 7.2045 | 0 | 244800 | 0 | 118178.4317 | 199.7902 | 0
1420 | 3 | 0 | 0 | 0.20539 | 8.4004 | 0 | 0 | 0 | 0 | 8.4004 | 0 | 244800 | 0 | 118178.4317 | 207.0717 | 0
1421 | 3 | 0 | 0 | 0.25204 | 10.3084 | 0 | 0 | 0 | 0 | 10.3084 | 0 | 244800 | 0 | 118178.4317 | 216.007 | 0
1422 | 3 | 0 | 0 | 0.31947 | 13.0663 | 0 | 0 | 0 | 0 | 13.0663 | 0 | 244800 | 0 | 118178.4317 | 227.3329 | 0
1423 | 3 | 0 | 0 | 0.22489 | 9.1981 | 0 | 0 | 0 | 0 | 9.1981 | 0 | 244800 | 0 | 118178.4317 | 235.3058 | 0
1424 | 3 | 1 | 0.24678 | 0.30064 | 83.5658 | 200 | 83.5658 | 116.4342 | 200 | 0 | 0 | 244600 | 200 | 118378.4317 | 118.8716 | 0
1425 | 3 | 1 | 0.6003 | 0.1671 | 180.202 | 200 | 180.202 | 19.798 | 200 | 0 | 0 | 244400 | 200 | 118578.4317 | 99.0736 | 0
1426 | 3 | 0 | 0.95844 | 0.16906 | 283.7129 | 0 | 0 | 0 | 0 | 180 | 103.7129 | 244400 | 103.7129 | 118682.1446 | 255.0976 | 0
1427 | 3 | 0 | 1 | 0.27619 | 300.0962 | 0 | 0 | 0 | 0 | 180 | 120.0962 | 244400 | 120.0962 | 118802.2408 | 411.1216 | 0
1428 | 3 | 0 | 1 | 0.33185 | 302.3728 | 0 | 0 | 0 | 0 | 115.0073 | 187.3655 | 244400 | 187.3655 | 118989.6063 | 510.81 | 0
1429 | 3 | 0 | 1 | 0.37628 | 304.1897 | 0 | 0 | 0 | 0 | 0 | 200 | 244400 | 200 | 119189.6063 | 510.81 | 104.1897
1430 | 3 | 0 | 1 | 0.38943 | 304.7278 | 0 | 0 | 0 | 0 | 0 | 200 | 244400 | 200 | 119389.6063 | 510.81 | 104.7278
1431 | 3 | 0 | 1 | 0.50297 | 309.3713 | 0 | 0 | 0 | 0 | 0 | 200 | 244400 | 200 | 119589.6063 | 510.81 | 109.3713
1432 | 3 | 0 | 0.95844 | 0.34518 | 290.9161 | 0 | 0 | 0 | 0 | 0 | 200 | 244400 | 200 | 119789.6063 | 510.81 | 90.9161
1433 | 3 | 0 | 0.6003 | 0.52222 | 194.7266 | 0 | 0 | 0 | 0 | 0 | 194.7266 | 244400 | 194.7266 | 119984.3329 | 510.81 | 0
1434 | 3 | 0 | 0.24678 | 0.45552 | 89.9002 | 0 | 0 | 0 | 0 | 0 | 89.9002 | 244400 | 89.9002 | 120074.2331 | 510.81 | 0
1435 | 3 | 0 | 0 | 0.2224 | 9.0963 | 0 | 0 | 0 | 0 | 0 | 9.0963 | 244400 | 9.0963 | 120083.3294 | 510.81 | 0
1436 | 3 | 1 | 0 | 0.18929 | 7.742 | 200 | 7.742 | 180 | 187.742 | 0 | 0 | 244200 | 187.742 | 120271.0714 | 330.81 | 0
1437 | 3 | 1 | 0 | 0.1346 | 5.5053 | 200 | 5.5053 | 180 | 185.5053 | 0 | 0 | 244000 | 185.5053 | 120456.5767 | 150.81 | 0
1438 | 3 | 0 | 0 | 0.17152 | 7.015 | 0 | 0 | 0 | 0 | 7.015 | 0 | 244000 | 0 | 120456.5767 | 156.8906 | 0
1439 | 3 | 0 | 0 | 0.18582 | 7.5999 | 0 | 0 | 0 | 0 | 7.5999 | 0 | 244000 | 0 | 120456.5767 | 163.4782 | 0
1440 | 3 | 0 | 0 | 0.134 | 5.4806 | 0 | 0 | 0 | 0 | 5.4806 | 0 | 244000 | 0 | 120456.5767 | 168.2288 | 0
1441 | 3 | 0 | 0 | 0.14582 | 5.964 | 0 | 0 | 0 | 0 | 5.964 | 0 | 244000 | 0 | 120456.5767 | 173.3984 | 0
1442 | 3 | 0 | 0 | 0.10688 | 4.3715 | 0 | 0 | 0 | 0 | 4.3715 | 0 | 244000 | 0 | 120456.5767 | 177.1877 | 0
1443 | 3 | 0 | 0 | 0.092317 | 3.7758 | 0 | 0 | 0 | 0 | 3.7758 | 0 | 244000 | 0 | 120456.5767 | 180.4605 | 0
1444 | 3 | 0 | 0 | 0.10867 | 4.4445 | 0 | 0 | 0 | 0 | 4.4445 | 0 | 244000 | 0 | 120456.5767 | 184.313 | 0
1445 | 3 | 0 | 0 | 0.063324 | 2.59 | 0 | 0 | 0 | 0 | 2.59 | 0 | 244000 | 0 | 120456.5767 | 186.5579 | 0
1446 | 3 | 0 | 0 | 0.092465 | 3.7818 | 0 | 0 | 0 | 0 | 3.7818 | 0 | 244000 | 0 | 120456.5767 | 189.836 | 0
1447 | 3 | 0 | 0 | 0.089447 | 3.6584 | 0 | 0 | 0 | 0 | 3.6584 | 0 | 244000 | 0 | 120456.5767 | 193.0071 | 0
1448 | 3 | 1 | 0.20991 | 0.082429 | 63.9928 | 200 | 63.9928 | 136.0072 | 200 | 0 | 0 | 243800 | 200 | 120656.5767 | 56.9999 | 0
1449 | 3 | 1 | 0.51061 | 0.1038 | 151.7109 | 200 | 151.7109 | 48.2891 | 200 | 0 | 0 | 243600 | 200 | 120856.5767 | 8.7108 | 0
1450 | 3 | 0 | 0.81524 | 0.11736 | 240.2426 | 0 | 0 | 0 | 0 | 180 | 60.2426 | 243600 | 60.2426 | 120916.8193 | 164.7348 | 0
1451 | 3 | 0 | 1 | 0.14903 | 294.8954 | 0 | 0 | 0 | 0 | 180 | 114.8954 | 243600 | 114.8954 | 121031.7146 | 320.7588 | 0
1452 | 3 | 0 | 1 | 0.12555 | 293.9349 | 0 | 0 | 0 | 0 | 180 | 113.9349 | 243600 | 113.9349 | 121145.6495 | 476.7828 | 0
1453 | 3 | 0 | 1 | 0.13995 | 294.5242 | 0 | 0 | 0 | 0 | 39.2561 | 200 | 243600 | 200 | 121345.6495 | 510.81 | 55.2681
1454 | 3 | 0 | 1 | 0.22179 | 297.8713 | 0 | 0 | 0 | 0 | 0 | 200 | 243600 | 200 | 121545.6495 | 510.81 | 97.8713
1455 | 3 | 0 | 1 | 0.16923 | 295.7216 | 0 | 0 | 0 | 0 | 0 | 200 | 243600 | 200 | 121745.6495 | 510.81 | 95.7216
1456 | 3 | 0 | 0.81524 | 0.26021 | 246.0852 | 0 | 0 | 0 | 0 | 0 | 200 | 243600 | 200 | 121945.6495 | 510.81 | 46.0852
1457 | 3 | 0 | 0.51061 | 0.22207 | 156.5478 | 0 | 0 | 0 | 0 | 0 | 156.5478 | 243600 | 156.5478 | 122102.1973 | 510.81 | 0
1458 | 3 | 0 | 0.20991 | 0.20791 | 69.1249 | 0 | 0 | 0 | 0 | 0 | 69.1249 | 243600 | 69.1249 | 122171.3222 | 510.81 | 0
1459 | 3 | 0 | 0 | 0.20137 | 8.2359 | 0 | 0 | 0 | 0 | 0 | 8.2359 | 243600 | 8.2359 | 122179.5581 | 510.81 | 0
1460 | 3 | 1 | 0 | 0.1529 | 6.2534 | 200 | 6.2534 | 180 | 186.2534 | 0 | 0 | 243400 | 186.2534 | 122365.8116 | 330.81 | 0
1461 | 3 | 1 | 0 | 0.27137 | 11.099 | 200 | 11.099 | 180 | 191.099 | 0 | 0 | 243200 | 191.099 | 122556.9106 | 150.81 | 0
1462 | 3 | 0 | 0 | 0.32647 | 13.3525 | 0 | 0 | 0 | 0 | 13.3525 | 0 | 243200 | 0 | 122556.9106 | 162.3839 | 0
1463 | 3 | 0 | 0 | 0.56155 | 22.9674 | 0 | 0 | 0 | 0 | 22.9674 | 0 | 243200 | 0 | 122556.9106 | 182.292 | 0
1464 | 3 | 0 | 0 | 0.51534 | 21.0776 | 0 | 0 | 0 | 0 | 21.0776 | 0 | 243200 | 0 | 122556.9106 | 200.5621 | 0
1465 | 3 | 0 | 0 | 0.38761 | 15.8535 | 0 | 0 | 0 | 0 | 15.8535 | 0 | 243200 | 0 | 122556.9106 | 214.3039 | 0
1466 | 3 | 0 | 0 | 0.40801 | 16.6874 | 0 | 0 | 0 | 0 | 16.6874 | 0 | 243200 | 0 | 122556.9106 | 228.7685 | 0
1467 | 3 | 0 | 0 | 0.33943 | 13.8829 | 0 | 0 | 0 | 0 | 13.8829 | 0 | 243200 | 0 | 122556.9106 | 240.8022 | 0
1468 | 3 | 0 | 0 | 0.2199 | 8.9941 | 0 | 0 | 0 | 0 | 8.9941 | 0 | 243200 | 0 | 122556.9106 | 248.5983 | 0
1469 | 3 | 0 | 0 | 0.23402 | 9.5715 | 0 | 0 | 0 | 0 | 9.5715 | 0 | 243200 | 0 | 122556.9106 | 256.8949 | 0
1470 | 3 | 0 | 0 | 0.23624 | 9.6621 | 0 | 0 | 0 | 0 | 9.6621 | 0 | 243200 | 0 | 122556.9106 | 265.27 | 0
1471 | 3 | 0 | 0 | 0.45953 | 18.7948 | 0 | 0 | 0 | 0 | 18.7948 | 0 | 243200 | 0 | 122556.9106 | 281.5614 | 0
1472 | 3 | 1 | 0.25093 | 0.27489 | 83.7115 | 200 | 83.7115 | 116.2885 | 200 | 0 | 0 | 243000 | 200 | 122756.9106 | 165.2729 | 0
1473 | 3 | 1 | 0.6104 | 0.28011 | 187.7413 | 200 | 187.7413 | 12.2587 | 200 | 0 | 0 | 242800 | 200 | 122956.9106 | 153.0142 | 0
1474 | 3 | 0 | 0.97457 | 0.39575 | 297.6416 | 0 | 0 | 0 | 0 | 180 | 117.6416 | 242800 | 117.6416 | 123074.5522 | 309.0382 | 0
1475 | 3 | 0 | 1 | 0.36984 | 303.9267 | 0 | 0 | 0 | 0 | 180 | 123.9267 | 242800 | 123.9267 | 123198.4789 | 465.0622 | 0
1476 | 3 | 0 | 1 | 0.39894 | 305.1167 | 0 | 0 | 0 | 0 | 52.7778 | 200 | 242800 | 200 | 123398.4789 | 510.81 | 52.3389
1477 | 3 | 0 | 1 | 0.41494 | 305.7711 | 0 | 0 | 0 | 0 | 0 | 200 | 242800 | 200 | 123598.4789 | 510.81 | 105.7711
1478 | 3 | 0 | 1 | 0.41558 | 305.7972 | 0 | 0 | 0 | 0 | 0 | 200 | 242800 | 200 | 123798.4789 | 510.81 | 105.7972
1479 | 3 | 0 | 1 | 0.40234 | 305.2559 | 0 | 0 | 0 | 0 | 0 | 200 | 242800 | 200 | 123998.4789 | 510.81 | 105.2559
1480 | 3 | 0 | 0.97457 | 0.47659 | 300.9482 | 0 | 0 | 0 | 0 | 0 | 200 | 242800 | 200 | 124198.4789 | 510.81 | 100.9482
1481 | 3 | 0 | 0.6104 | 0.72578 | 205.9692 | 0 | 0 | 0 | 0 | 0 | 200 | 242800 | 200 | 124398.4789 | 510.81 | 5.9692
1482 | 3 | 0 | 0.25093 | 0.76085 | 103.5872 | 0 | 0 | 0 | 0 | 0 | 103.5872 | 242800 | 103.5872 | 124502.066 | 510.81 | 0
1483 | 3 | 0 | 0 | 0.87863 | 35.9359 | 0 | 0 | 0 | 0 | 0 | 35.9359 | 242800 | 35.9359 | 124538.0019 | 510.81 | 0
1484 | 3 | 1 | 0 | 0.78039 | 31.9182 | 200 | 31.9182 | 168.0818 | 200 | 0 | 0 | 242600 | 200 | 124738.0019 | 342.7282 | 0
1485 | 3 | 1 | 0 | 0.93977 | 38.4366 | 200 | 38.4366 | 161.5634 | 200 | 0 | 0 | 242400 | 200 | 124938.0019 | 181.1648 | 0
1486 | 3 | 0 | 0 | 0.60686 | 24.8207 | 0 | 0 | 0 | 0 | 24.8207 | 0 | 242400 | 0 | 124938.0019 | 202.6794 | 0
1487 | 3 | 0 | 0 | 0.56059 | 22.928 | 0 | 0 | 0 | 0 | 22.928 | 0 | 242400 | 0 | 124938.0019 | 222.5534 | 0
1488 | 3 | 0 | 0 | 0.49731 | 20.3399 | 0 | 0 | 0 | 0 | 20.3399 | 0 | 242400 | 0 | 124938.0019 | 240.184 | 0
1489 | 3 | 0 | 0 | 0.49483 | 20.2385 | 0 | 0 | 0 | 0 | 20.2385 | 0 | 242400 | 0 | 124938.0019 | 257.7267 | 0
1490 | 3 | 0 | 0 | 0.49677 | 20.3177 | 0 | 0 | 0 | 0 | 20.3177 | 0 | 242400 | 0 | 124938.0019 | 275.3381 | 0
1491 | 3 | 0 | 0 | 0.41485 | 16.9673 | 0 | 0 | 0 | 0 | 16.9673 | 0 | 242400 | 0 | 124938.0019 | 290.0454 | 0
1492 | 3 | 0 | 0 | 0.43703 | 17.8744 | 0 | 0 | 0 | 0 | 17.8744 | 0 | 242400 | 0 | 124938.0019 | 305.5389 | 0
1493 | 3 | 0 | 0 | 0.5884 | 24.0657 | 0 | 0 | 0 | 0 | 24.0657 | 0 | 242400 | 0 | 124938.0019 | 326.3991 | 0
1494 | 3 | 0 | 0 | 0.58179 | 23.7953 | 0 | 0 | 0 | 0 | 23.7953 | 0 | 242400 | 0 | 124938.0019 | 347.0248 | 0
1495 | 3 | 0 | 0 | 0.49642 | 20.3035 | 0 | 0 | 0 | 0 | 20.3035 | 0 | 242400 | 0 | 124938.0019 | 364.6239 | 0
1496 | 3 | 1 | 0.24021 | 0.66364 | 96.5151 | 200 | 96.5151 | 103.4849 | 200 | 0 | 0 | 242200 | 200 | 125138.0019 | 261.139 | 0
1497 | 3 | 1 | 0.58432 | 0.54439 | 191.0179 | 200 | 191.0179 | 8.9821 | 200 | 0 | 0 | 242000 | 200 | 125338.0019 | 252.1569 | 0
1498 | 3 | 0 | 0.93293 | 0.5673 | 292.6318 | 0 | 0 | 0 | 0 | 180 | 112.6318 | 242000 | 112.6318 | 125450.6337 | 408.1809 | 0
1499 | 3 | 0 | 1 | 0.61094 | 313.7873 | 0 | 0 | 0 | 0 | 118.4 | 195.3872 | 242000 | 195.3872 | 125646.021 | 510.81 | 0
1500 | 3 | 0 | 1 | 0.53915 | 310.8513 | 0 | 0 | 0 | 0 | 0 | 200 | 242000 | 200 | 125846.021 | 510.81 | 110.8513
1501 | 3 | 0 | 1 | 0.49926 | 309.2197 | 0 | 0 | 0 | 0 | 0 | 200 | 242000 | 200 | 126046.021 | 510.81 | 109.2197
1502 | 3 | 0 | 1 | 0.40465 | 305.3502 | 0 | 0 | 0 | 0 | 0 | 200 | 242000 | 200 | 126246.021 | 510.81 | 105.3502
1503 | 3 | 0 | 1 | 0.48608 | 308.6806 | 0 | 0 | 0 | 0 | 0 | 200 | 242000 | 200 | 126446.021 | 510.81 | 108.6806
1504 | 3 | 0 | 0.93293 | 0.51097 | 290.328 | 0 | 0 | 0 | 0 | 0 | 200 | 242000 | 200 | 126646.021 | 510.81 | 90.328
1505 | 3 | 0 | 0.58432 | 0.46534 | 187.7846 | 0 | 0 | 0 | 0 | 0 | 187.7846 | 242000 | 187.7846 | 126833.8056 | 510.81 | 0
1506 | 3 | 0 | 0.24021 | 0.44788 | 87.6904 | 0 | 0 | 0 | 0 | 0 | 87.6904 | 242000 | 87.6904 | 126921.496 | 510.81 | 0
1507 | 3 | 0 | 0 | 0.44964 | 18.3901 | 0 | 0 | 0 | 0 | 0 | 18.3901 | 242000 | 18.3901 | 126939.8861 | 510.81 | 0
1508 | 3 | 1 | 0 | 0.50287 | 20.5676 | 200 | 20.5676 | 179.4324 | 200 | 0 | 0 | 241800 | 200 | 127139.8861 | 331.3776 | 0
1509 | 3 | 1 | 0 | 0.47754 | 19.5314 | 200 | 19.5314 | 180 | 199.5314 | 0 | 0 | 241600 | 199.5314 | 127339.4176 | 151.3776 | 0
1510 | 3 | 0 | 0 | 0.24 | 9.8158 | 0 | 0 | 0 | 0 | 9.8158 | 0 | 241600 | 0 | 127339.4176 | 159.886 | 0
1511 | 3 | 0 | 0 | 0.17983 | 7.3552 | 0 | 0 | 0 | 0 | 7.3552 | 0 | 241600 | 0 | 127339.4176 | 166.2614 | 0
1512 | 3 | 0 | 0 | 0.15731 | 6.4338 | 0 | 0 | 0 | 0 | 6.4338 | 0 | 241600 | 0 | 127339.4176 | 171.8382 | 0
1513 | 3 | 0 | 0 | 0.1319 | 5.3945 | 0 | 0 | 0 | 0 | 5.3945 | 0 | 241600 | 0 | 127339.4176 | 176.5142 | 0
1514 | 3 | 0 | 0 | 0.15379 | 6.2901 | 0 | 0 | 0 | 0 | 6.2901 | 0 | 241600 | 0 | 127339.4176 | 181.9664 | 0
1515 | 3 | 0 | 0 | 0.15683 | 6.4145 | 0 | 0 | 0 | 0 | 6.4145 | 0 | 241600 | 0 | 127339.4176 | 187.5265 | 0
1516 | 3 | 0 | 0 | 0.15491 | 6.3358 | 0 | 0 | 0 | 0 | 6.3358 | 0 | 241600 | 0 | 127339.4176 | 193.0184 | 0
1517 | 3 | 0 | 0 | 0.17395 | 7.1145 | 0 | 0 | 0 | 0 | 7.1145 | 0 | 241600 | 0 | 127339.4176 | 199.1852 | 0
1518 | 3 | 0 | 0 | 0.26613 | 10.8846 | 0 | 0 | 0 | 0 | 10.8846 | 0 | 241600 | 0 | 127339.4176 | 208.62 | 0
1519 | 3 | 0 | 0 | 0.23627 | 9.6635 | 0 | 0 | 0 | 0 | 9.6635 | 0 | 241600 | 0 | 127339.4176 | 216.9964 | 0
1520 | 3 | 1 | 0.27245 | 0.17425 | 85.8103 | 200 | 85.8103 | 114.1897 | 200 | 0 | 0 | 241400 | 200 | 127539.4176 | 102.8066 | 0
1521 | 3 | 1 | 0.66275 | 0.14757 | 197.4379 | 200 | 197.4379 | 2.5621 | 200 | 0 | 0 | 241200 | 200 | 127739.4176 | 100.2446 | 0
1522 | 3 | 0 | 1 | 0.24907 | 298.9868 | 0 | 0 | 0 | 0 | 180 | 118.9868 | 241200 | 118.9868 | 127858.4043 | 256.2686 | 0
1523 | 3 | 0 | 1 | 0.21292 | 297.5083 | 0 | 0 | 0 | 0 | 180 | 117.5083 | 241200 | 117.5083 | 127975.9126 | 412.2926 | 0
1524 | 3 | 0 | 1 | 0.22575 | 298.0331 | 0 | 0 | 0 | 0 | 113.6565 | 184.3767 | 241200 | 184.3767 | 128160.2893 | 510.81 | 0
1525 | 3 | 0 | 1 | 0.21004 | 297.3907 | 0 | 0 | 0 | 0 | 0 | 200 | 241200 | 200 | 128360.2893 | 510.81 | 97.3907
1526 | 3 | 0 | 1 | 0.16876 | 295.7024 | 0 | 0 | 0 | 0 | 0 | 200 | 241200 | 200 | 128560.2893 | 510.81 | 95.7024
1527 | 3 | 0 | 1 | 0.19416 | 296.741 | 0 | 0 | 0 | 0 | 0 | 200 | 241200 | 200 | 128760.2893 | 510.81 | 96.741
1528 | 3 | 0 | 1 | 0.14511 | 294.735 | 0 | 0 | 0 | 0 | 0 | 200 | 241200 | 200 | 128960.2893 | 510.81 | 94.735
1529 | 3 | 0 | 0.66275 | 0.18632 | 199.0225 | 0 | 0 | 0 | 0 | 0 | 199.0225 | 241200 | 199.0225 | 129159.3118 | 510.81 | 0
1530 | 3 | 0 | 0.27245 | 0.23735 | 88.391 | 0 | 0 | 0 | 0 | 0 | 88.391 | 241200 | 88.391 | 129247.7028 | 510.81 | 0
1531 | 3 | 0 | 0 | 0.26399 | 10.7971 | 0 | 0 | 0 | 0 | 0 | 10.7971 | 241200 | 10.7971 | 129258.4999 | 510.81 | 0
1532 | 3 | 1 | 0 | 0.26592 | 10.8763 | 200 | 10.8763 | 180 | 190.8763 | 0 | 0 | 241000 | 190.8763 | 129449.3762 | 330.81 | 0
1533 | 3 | 1 | 0 | 0.30592 | 12.512 | 200 | 12.512 | 180 | 192.512 | 0 | 0 | 240800 | 192.512 | 129641.8882 | 150.81 | 0
1534 | 3 | 0 | 0 | 0.31371 | 12.8306 | 0 | 0 | 0 | 0 | 12.8306 | 0 | 240800 | 0 | 129641.8882 | 161.9315 | 0
1535 | 3 | 0 | 0 | 0.26862 | 10.9867 | 0 | 0 | 0 | 0 | 10.9867 | 0 | 240800 | 0 | 129641.8882 | 171.4548 | 0
1536 | 3 | 0 | 0 | 0.26752 | 10.9415 | 0 | 0 | 0 | 0 | 10.9415 | 0 | 240800 | 0 | 129641.8882 | 180.9389 | 0
1537 | 3 | 0 | 0 | 0.18702 | 7.6493 | 0 | 0 | 0 | 0 | 7.6493 | 0 | 240800 | 0 | 129641.8882 | 187.5693 | 0
1538 | 3 | 0 | 0 | 0.175 | 7.1577 | 0 | 0 | 0 | 0 | 7.1577 | 0 | 240800 | 0 | 129641.8882 | 193.7736 | 0
1539 | 3 | 0 | 0 | 0.20506 | 8.3868 | 0 | 0 | 0 | 0 | 8.3868 | 0 | 240800 | 0 | 129641.8882 | 201.0432 | 0
1540 | 3 | 0 | 0 | 0.23788 | 9.7293 | 0 | 0 | 0 | 0 | 9.7293 | 0 | 240800 | 0 | 129641.8882 | 209.4766 | 0
1541 | 3 | 0 | 0 | 0.22408 | 9.165 | 0 | 0 | 0 | 0 | 9.165 | 0 | 240800 | 0 | 129641.8882 | 217.4208 | 0
1542 | 3 | 0 | 0 | 0.42012 | 17.1828 | 0 | 0 | 0 | 0 | 17.1828 | 0 | 240800 | 0 | 129641.8882 | 232.3148 | 0
1543 | 3 | 0 | 0 | 0.4212 | 17.227 | 0 | 0 | 0 | 0 | 17.227 | 0 | 240800 | 0 | 129641.8882 | 247.2471 | 0
1544 | 3 | 1 | 0.2754 | 0.3299 | 93.0294 | 200 | 93.0294 | 106.9706 | 200 | 0 | 0 | 240600 | 200 | 129841.8882 | 140.2765 | 0
1545 | 3 | 1 | 0.66994 | 0.39007 | 209.4317 | 200 | 200 | 0 | 200 | 9.4317 | 0 | 240400 | 200 | 130041.8882 | 148.4519 | 0
1546 | 3 | 0 | 1 | 0.34639 | 302.9672 | 0 | 0 | 0 | 0 | 180 | 122.9672 | 240400 | 122.9672 | 130164.8554 | 304.4759 | 0
1547 | 3 | 0 | 1 | 0.23204 | 298.2903 | 0 | 0 | 0 | 0 | 180 | 118.2903 | 240400 | 118.2903 | 130283.1457 | 460.4999 | 0
1548 | 3 | 0 | 1 | 0.31603 | 301.7258 | 0 | 0 | 0 | 0 | 58.0412 | 200 | 240400 | 200 | 130483.1457 | 510.81 | 43.6846
1549 | 3 | 0 | 1 | 0.24696 | 298.9006 | 0 | 0 | 0 | 0 | 0 | 200 | 240400 | 200 | 130683.1457 | 510.81 | 98.9006
1550 | 3 | 0 | 1 | 0.29288 | 300.7788 | 0 | 0 | 0 | 0 | 0 | 200 | 240400 | 200 | 130883.1457 | 510.81 | 100.7788
1551 | 3 | 0 | 1 | 0.32227 | 301.9808 | 0 | 0 | 0 | 0 | 0 | 200 | 240400 | 200 | 131083.1457 | 510.81 | 101.9808
1552 | 3 | 0 | 1 | 0.38891 | 304.7066 | 0 | 0 | 0 | 0 | 0 | 200 | 240400 | 200 | 131283.1457 | 510.81 | 104.7066
1553 | 3 | 0 | 0.66994 | 0.3601 | 208.206 | 0 | 0 | 0 | 0 | 0 | 200 | 240400 | 200 | 131483.1457 | 510.81 | 8.206
1554 | 3 | 0 | 0.2754 | 0.29799 | 91.7242 | 0 | 0 | 0 | 0 | 0 | 91.7242 | 240400 | 91.7242 | 131574.8699 | 510.81 | 0
1555 | 3 | 0 | 0 | 0.19485 | 7.9695 | 0 | 0 | 0 | 0 | 0 | 7.9695 | 240400 | 7.9695 | 131582.8394 | 510.81 | 0
1556 | 3 | 1 | 0 | 0.1631 | 6.6709 | 200 | 6.6709 | 180 | 186.6709 | 0 | 0 | 240200 | 186.6709 | 131769.5103 | 330.81 | 0
1557 | 3 | 1 | 0 | 0.16025 | 6.5543 | 200 | 6.5543 | 180 | 186.5543 | 0 | 0 | 240000 | 186.5543 | 131956.0646 | 150.81 | 0
1558 | 3 | 0 | 0 | 0.22406 | 9.1638 | 0 | 0 | 0 | 0 | 9.1638 | 0 | 240000 | 0 | 131956.0646 | 158.7532 | 0
1559 | 3 | 0 | 0 | 0.16248 | 6.6453 | 0 | 0 | 0 | 0 | 6.6453 | 0 | 240000 | 0 | 131956.0646 | 164.5133 | 0
1560 | 3 | 0 | 0 | 0.12262 | 5.0152 | 0 | 0 | 0 | 0 | 5.0152 | 0 | 240000 | 0 | 131956.0646 | 168.8605 | 0
1561 | 3 | 0 | 0 | 0.12218 | 4.9972 | 0 | 0 | 0 | 0 | 4.9972 | 0 | 240000 | 0 | 131956.0646 | 173.1921 | 0
1562 | 3 | 0 | 0 | 0.17142 | 7.0112 | 0 | 0 | 0 | 0 | 7.0112 | 0 | 240000 | 0 | 131956.0646 | 179.2694 | 0
1563 | 3 | 0 | 0 | 0.21142 | 8.6471 | 0 | 0 | 0 | 0 | 8.6471 | 0 | 240000 | 0 | 131956.0646 | 186.7647 | 0
1564 | 3 | 0 | 0 | 0.24638 | 10.0769 | 0 | 0 | 0 | 0 | 10.0769 | 0 | 240000 | 0 | 131956.0646 | 195.4994 | 0
1565 | 3 | 0 | 0 | 0.28607 | 11.7001 | 0 | 0 | 0 | 0 | 11.7001 | 0 | 240000 | 0 | 131956.0646 | 205.641 | 0
1566 | 3 | 0 | 0 | 0.31174 | 12.7502 | 0 | 0 | 0 | 0 | 12.7502 | 0 | 240000 | 0 | 131956.0646 | 216.6929 | 0
1567 | 3 | 0 | 0 | 0.24716 | 10.1087 | 0 | 0 | 0 | 0 | 10.1087 | 0 | 240000 | 0 | 131956.0646 | 225.4551 | 0
1568 | 3 | 1 | 0.24467 | 0.25197 | 80.9667 | 200 | 80.9667 | 119.0333 | 200 | 0 | 0 | 239800 | 200 | 132156.0646 | 106.4218 | 0
1569 | 3 | 1 | 0.59518 | 0.32718 | 185.2689 | 200 | 185.2689 | 14.7311 | 200 | 0 | 0 | 239600 | 200 | 132356.0646 | 91.6907 | 0
1570 | 3 | 0 | 0.95026 | 0.33316 | 288.0608 | 0 | 0 | 0 | 0 | 180 | 108.0608 | 239600 | 108.0608 | 132464.1253 | 247.7147 | 0
1571 | 3 | 0 | 1 | 0.31562 | 301.7087 | 0 | 0 | 0 | 0 | 180 | 121.7087 | 239600 | 121.7087 | 132585.834 | 403.7387 | 0
1572 | 3 | 0 | 1 | 0.27718 | 300.1365 | 0 | 0 | 0 | 0 | 123.5248 | 176.6117 | 239600 | 176.6117 | 132762.4458 | 510.81 | 0
1573 | 3 | 0 | 1 | 0.21973 | 297.787 | 0 | 0 | 0 | 0 | 0 | 200 | 239600 | 200 | 132962.4458 | 510.81 | 97.787
1574 | 3 | 0 | 1 | 0.18697 | 296.4472 | 0 | 0 | 0 | 0 | 0 | 200 | 239600 | 200 | 133162.4458 | 510.81 | 96.4472
1575 | 3 | 0 | 1 | 0.22462 | 297.9868 | 0 | 0 | 0 | 0 | 0 | 200 | 239600 | 200 | 133362.4458 | 510.81 | 97.9868
1576 | 3 | 0 | 0.95026 | 0.29399 | 286.4587 | 0 | 0 | 0 | 0 | 0 | 200 | 239600 | 200 | 133562.4458 | 510.81 | 86.4587
1577 | 3 | 0 | 0.59518 | 0.30788 | 184.4794 | 0 | 0 | 0 | 0 | 0 | 184.4794 | 239600 | 184.4794 | 133746.9252 | 510.81 | 0
1578 | 3 | 0 | 0.24467 | 0.37643 | 86.0568 | 0 | 0 | 0 | 0 | 0 | 86.0568 | 239600 | 86.0568 | 133832.9819 | 510.81 | 0
1579 | 3 | 0 | 0 | 0.26785 | 10.9552 | 0 | 0 | 0 | 0 | 0 | 10.9552 | 239600 | 10.9552 | 133843.9371 | 510.81 | 0
1580 | 3 | 1 | 0 | 0.30224 | 12.3618 | 200 | 12.3618 | 180 | 192.3618 | 0 | 0 | 239400 | 192.3618 | 134036.2989 | 330.81 | 0
1581 | 3 | 1 | 0 | 0.45637 | 18.6653 | 200 | 18.6653 | 180 | 198.6653 | 0 | 0 | 239200 | 198.6653 | 134234.9643 | 150.81 | 0
1582 | 3 | 0 | 0 | 0.34715 | 14.1986 | 0 | 0 | 0 | 0 | 14.1986 | 0 | 239200 | 0 | 134234.9643 | 163.1174 | 0
1583 | 3 | 0 | 0 | 0.27226 | 11.1352 | 0 | 0 | 0 | 0 | 11.1352 | 0 | 239200 | 0 | 134234.9643 | 172.7694 | 0
1584 | 3 | 0 | 0 | 0.33513 | 13.7067 | 0 | 0 | 0 | 0 | 13.7067 | 0 | 239200 | 0 | 134234.9643 | 184.6504 | 0
1585 | 3 | 0 | 0 | 0.2033 | 8.3151 | 0 | 0 | 0 | 0 | 8.3151 | 0 | 239200 | 0 | 134234.9643 | 191.8579 | 0
1586 | 3 | 0 | 0 | 0.2163 | 8.8465 | 0 | 0 | 0 | 0 | 8.8465 | 0 | 239200 | 0 | 134234.9643 | 199.526 | 0
1587 | 3 | 0 | 0 | 0.25018 | 10.2323 | 0 | 0 | 0 | 0 | 10.2323 | 0 | 239200 | 0 | 134234.9643 | 208.3954 | 0
1588 | 3 | 0 | 0 | 0.18724 | 7.6581 | 0 | 0 | 0 | 0 | 7.6581 | 0 | 239200 | 0 | 134234.9643 | 215.0335 | 0
1589 | 3 | 0 | 0 | 0.18808 | 7.6926 | 0 | 0 | 0 | 0 | 7.6926 | 0 | 239200 | 0 | 134234.9643 | 221.7014 | 0
1590 | 3 | 0 | 0 | 0.25781 | 10.5443 | 0 | 0 | 0 | 0 | 10.5443 | 0 | 239200 | 0 | 134234.9643 | 230.8412 | 0
1591 | 3 | 0 | 0 | 0.29682 | 12.1398 | 0 | 0 | 0 | 0 | 12.1398 | 0 | 239200 | 0 | 134234.9643 | 241.364 | 0
1592 | 3 | 1 | 0.23969 | 0.3114 | 81.9581 | 200 | 81.9581 | 118.0419 | 200 | 0 | 0 | 239000 | 200 | 134434.9643 | 123.3221 | 0
1593 | 3 | 1 | 0.58306 | 0.29685 | 180.5279 | 200 | 180.5279 | 19.4721 | 200 | 0 | 0 | 238800 | 200 | 134634.9643 | 103.85 | 0
1594 | 3 | 0 | 0.9309 | 0.37789 | 284.3011 | 0 | 0 | 0 | 0 | 180 | 104.3011 | 238800 | 104.3011 | 134739.2654 | 259.874 | 0
1595 | 3 | 0 | 1 | 0.51911 | 310.0314 | 0 | 0 | 0 | 0 | 180 | 130.0314 | 238800 | 130.0314 | 134869.2969 | 415.898 | 0
1596 | 3 | 0 | 1 | 0.39615 | 305.0027 | 0 | 0 | 0 | 0 | 109.497 | 195.5057 | 238800 | 195.5057 | 135064.8025 | 510.81 | 0
1597 | 3 | 0 | 1 | 0.30693 | 301.3532 | 0 | 0 | 0 | 0 | 0 | 200 | 238800 | 200 | 135264.8025 | 510.81 | 101.3532
1598 | 3 | 0 | 1 | 0.44279 | 306.9102 | 0 | 0 | 0 | 0 | 0 | 200 | 238800 | 200 | 135464.8025 | 510.81 | 106.9102
1599 | 3 | 0 | 1 | 0.49006 | 308.8435 | 0 | 0 | 0 | 0 | 0 | 200 | 238800 | 200 | 135664.8025 | 510.81 | 108.8435
1600 | 3 | 0 | 0.9309 | 0.57294 | 292.2786 | 0 | 0 | 0 | 0 | 0 | 200 | 238800 | 200 | 135864.8025 | 510.81 | 92.2786
1601 | 3 | 0 | 0.58306 | 0.67535 | 196.0086 | 0 | 0 | 0 | 0 | 0 | 196.0086 | 238800 | 196.0086 | 136060.8111 | 510.81 | 0
1602 | 3 | 0 | 0.23969 | 0.59128 | 93.4054 | 0 | 0 | 0 | 0 | 0 | 93.4054 | 238800 | 93.4054 | 136154.2165 | 510.81 | 0
1603 | 3 | 0 | 0 | 0.81878 | 33.4881 | 0 | 0 | 0 | 0 | 0 | 33.4881 | 238800 | 33.4881 | 136187.7046 | 510.81 | 0
1604 | 3 | 1 | 0 | 0.91535 | 37.4379 | 200 | 37.4379 | 162.5621 | 200 | 0 | 0 | 238600 | 200 | 136387.7046 | 348.2479 | 0
1605 | 3 | 1 | 0 | 0.91766 | 37.5325 | 200 | 37.5325 | 162.4675 | 200 | 0 | 0 | 238400 | 200 | 136587.7046 | 185.7804 | 0
1606 | 3 | 0 | 0 | 0.65399 | 26.7483 | 0 | 0 | 0 | 0 | 26.7483 | 0 | 238400 | 0 | 136587.7046 | 208.9658 | 0
1607 | 3 | 0 | 0 | 0.34182 | 13.9804 | 0 | 0 | 0 | 0 | 13.9804 | 0 | 238400 | 0 | 136587.7046 | 221.084 | 0
1608 | 3 | 0 | 0 | 0.39678 | 16.2281 | 0 | 0 | 0 | 0 | 16.2281 | 0 | 238400 | 0 | 136587.7046 | 235.1506 | 0
1609 | 3 | 0 | 0 | 0.55579 | 22.7317 | 0 | 0 | 0 | 0 | 22.7317 | 0 | 238400 | 0 | 136587.7046 | 254.8544 | 0
1610 | 3 | 0 | 0 | 0.45668 | 18.6784 | 0 | 0 | 0 | 0 | 18.6784 | 0 | 238400 | 0 | 136587.7046 | 271.0448 | 0
1611 | 3 | 0 | 0 | 0.526 | 21.5135 | 0 | 0 | 0 | 0 | 21.5135 | 0 | 238400 | 0 | 136587.7046 | 289.6927 | 0
1612 | 3 | 0 | 0 | 0.51309 | 20.9853 | 0 | 0 | 0 | 0 | 20.9853 | 0 | 238400 | 0 | 136587.7046 | 307.8827 | 0
1613 | 3 | 0 | 0 | 0.61746 | 25.254 | 0 | 0 | 0 | 0 | 25.254 | 0 | 238400 | 0 | 136587.7046 | 329.7729 | 0
1614 | 3 | 0 | 0 | 0.67329 | 27.5374 | 0 | 0 | 0 | 0 | 27.5374 | 0 | 238400 | 0 | 136587.7046 | 353.6424 | 0
1615 | 3 | 0 | 0 | 0.64997 | 26.5837 | 0 | 0 | 0 | 0 | 26.5837 | 0 | 238400 | 0 | 136587.7046 | 376.6851 | 0
1616 | 3 | 1 | 0.25018 | 0.90922 | 109.4383 | 200 | 109.4383 | 90.5617 | 200 | 0 | 0 | 238200 | 200 | 136787.7046 | 286.1234 | 0
1617 | 3 | 1 | 0.60857 | 0.74644 | 206.2846 | 200 | 200 | 0 | 200 | 6.2846 | 0 | 238000 | 200 | 136987.7046 | 291.5709 | 0
1618 | 3 | 0 | 0.97164 | 0.66644 | 307.8679 | 0 | 0 | 0 | 0 | 180 | 127.8679 | 238000 | 127.8679 | 137115.5725 | 447.5949 | 0
1619 | 3 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 72.9293 | 200 | 238000 | 200 | 137315.5725 | 510.81 | 56.7707
1620 | 3 | 0 | 1 | 0.95897 | 328.0219 | 0 | 0 | 0 | 0 | 0 | 200 | 238000 | 200 | 137515.5725 | 510.81 | 128.0219
1621 | 3 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 0 | 200 | 238000 | 200 | 137715.5725 | 510.81 | 129.7
1622 | 3 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 0 | 200 | 238000 | 200 | 137915.5725 | 510.81 | 129.7
1623 | 3 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 0 | 200 | 238000 | 200 | 138115.5725 | 510.81 | 129.7
1624 | 3 | 0 | 0.97164 | 1 | 321.5105 | 0 | 0 | 0 | 0 | 0 | 200 | 238000 | 200 | 138315.5725 | 510.81 | 121.5105
1625 | 3 | 0 | 0.60857 | 0.64913 | 202.3046 | 0 | 0 | 0 | 0 | 0 | 200 | 238000 | 200 | 138515.5725 | 510.81 | 2.3046
1626 | 3 | 0 | 0.25018 | 0.66116 | 99.2924 | 0 | 0 | 0 | 0 | 0 | 99.2924 | 238000 | 99.2924 | 138614.8649 | 510.81 | 0
1627 | 3 | 0 | 0 | 0.51985 | 21.2621 | 0 | 0 | 0 | 0 | 0 | 21.2621 | 238000 | 21.2621 | 138636.127 | 510.81 | 0
1628 | 3 | 1 | 0 | 0.5591 | 22.8672 | 200 | 22.8672 | 177.1328 | 200 | 0 | 0 | 237800 | 200 | 138836.127 | 333.6772 | 0
1629 | 3 | 1 | 0 | 0.44098 | 18.0362 | 200 | 18.0362 | 180 | 198.0362 | 0 | 0 | 237600 | 198.0362 | 139034.1632 | 153.6772 | 0
1630 | 3 | 0 | 0 | 0.31318 | 12.8092 | 0 | 0 | 0 | 0 | 12.8092 | 0 | 237600 | 0 | 139034.1632 | 164.7802 | 0
1631 | 3 | 0 | 0 | 0.30738 | 12.5718 | 0 | 0 | 0 | 0 | 12.5718 | 0 | 237600 | 0 | 139034.1632 | 175.6775 | 0
1632 | 3 | 0 | 0 | 0.26795 | 10.9592 | 0 | 0 | 0 | 0 | 10.9592 | 0 | 237600 | 0 | 139034.1632 | 185.1769 | 0
1633 | 3 | 0 | 0 | 0.24835 | 10.1574 | 0 | 0 | 0 | 0 | 10.1574 | 0 | 237600 | 0 | 139034.1632 | 193.9813 | 0
1634 | 3 | 0 | 0 | 0.30583 | 12.5084 | 0 | 0 | 0 | 0 | 12.5084 | 0 | 237600 | 0 | 139034.1632 | 204.8236 | 0
1635 | 3 | 0 | 0 | 0.19974 | 8.1695 | 0 | 0 | 0 | 0 | 8.1695 | 0 | 237600 | 0 | 139034.1632 | 211.905 | 0
1636 | 3 | 0 | 0 | 0.15417 | 6.3056 | 0 | 0 | 0 | 0 | 6.3056 | 0 | 237600 | 0 | 139034.1632 | 217.3706 | 0
1637 | 3 | 0 | 0 | 0.18158 | 7.4266 | 0 | 0 | 0 | 0 | 7.4266 | 0 | 237600 | 0 | 139034.1632 | 223.808 | 0
1638 | 3 | 0 | 0 | 0.16936 | 6.927 | 0 | 0 | 0 | 0 | 6.927 | 0 | 237600 | 0 | 139034.1632 | 229.8124 | 0
1639 | 3 | 0 | 0 | 0.18867 | 7.7165 | 0 | 0 | 0 | 0 | 7.7165 | 0 | 237600 | 0 | 139034.1632 | 236.501 | 0
1640 | 3 | 1 | 0.19152 | 0.21254 | 64.0034 | 200 | 64.0034 | 135.9966 | 200 | 0 | 0 | 237400 | 200 | 139234.1632 | 100.5044 | 0
1641 | 3 | 1 | 0.46588 | 0.20875 | 143.0844 | 200 | 143.0844 | 56.9156 | 200 | 0 | 0 | 237200 | 200 | 139434.1632 | 43.5888 | 0
1642 | 3 | 0 | 0.74382 | 0.18305 | 222.3031 | 0 | 0 | 0 | 0 | 180 | 42.3031 | 237200 | 42.3031 | 139476.4663 | 199.6128 | 0
1643 | 3 | 0 | 0.97798 | 0.25461 | 292.8553 | 0 | 0 | 0 | 0 | 180 | 112.8553 | 237200 | 112.8553 | 139589.3216 | 355.6368 | 0
1644 | 3 | 0 | 1 | 0.18163 | 296.2288 | 0 | 0 | 0 | 0 | 179.0185 | 117.2103 | 237200 | 117.2103 | 139706.5319 | 510.81 | 0
1645 | 3 | 0 | 1 | 0.21722 | 297.6845 | 0 | 0 | 0 | 0 | 0 | 200 | 237200 | 200 | 139906.5319 | 510.81 | 97.6845
1646 | 3 | 0 | 1 | 0.36329 | 303.6584 | 0 | 0 | 0 | 0 | 0 | 200 | 237200 | 200 | 140106.5319 | 510.81 | 103.6584
1647 | 3 | 0 | 0.97798 | 0.2631 | 293.2024 | 0 | 0 | 0 | 0 | 0 | 200 | 237200 | 200 | 140306.5319 | 510.81 | 93.2024
1648 | 3 | 0 | 0.74382 | 0.17883 | 222.1304 | 0 | 0 | 0 | 0 | 0 | 200 | 237200 | 200 | 140506.5319 | 510.81 | 22.1304
1649 | 3 | 0 | 0.46588 | 0.20507 | 142.9337 | 0 | 0 | 0 | 0 | 0 | 142.9337 | 237200 | 142.9337 | 140649.4656 | 510.81 | 0
1650 | 3 | 0 | 0.19152 | 0.22923 | 64.6858 | 0 | 0 | 0 | 0 | 0 | 64.6858 | 237200 | 64.6858 | 140714.1513 | 510.81 | 0
1651 | 3 | 0 | 0 | 0.35209 | 14.4003 | 0 | 0 | 0 | 0 | 0 | 14.4003 | 237200 | 14.4003 | 140728.5517 | 510.81 | 0
1652 | 3 | 1 | 0 | 0.22753 | 9.3061 | 200 | 9.3061 | 180 | 189.3061 | 0 | 0 | 237000 | 189.3061 | 140917.8577 | 330.81 | 0
1653 | 3 | 1 | 0 | 0.18904 | 7.7317 | 200 | 7.7317 | 180 | 187.7317 | 0 | 0 | 236800 | 187.7317 | 141105.5894 | 150.81 | 0
1654 | 3 | 0 | 0 | 0.23867 | 9.7615 | 0 | 0 | 0 | 0 | 9.7615 | 0 | 236800 | 0 | 141105.5894 | 159.2713 | 0
1655 | 3 | 0 | 0 | 0.24658 | 10.0853 | 0 | 0 | 0 | 0 | 10.0853 | 0 | 236800 | 0 | 141105.5894 | 168.0132 | 0
1656 | 3 | 0 | 0 | 0.21599 | 8.8342 | 0 | 0 | 0 | 0 | 8.8342 | 0 | 236800 | 0 | 141105.5894 | 175.6707 | 0
1657 | 3 | 0 | 0 | 0.26549 | 10.8585 | 0 | 0 | 0 | 0 | 10.8585 | 0 | 236800 | 0 | 141105.5894 | 185.0828 | 0
1658 | 3 | 0 | 0 | 0.32899 | 13.4557 | 0 | 0 | 0 | 0 | 13.4557 | 0 | 236800 | 0 | 141105.5894 | 196.7462 | 0
1659 | 3 | 0 | 0 | 0.24798 | 10.1423 | 0 | 0 | 0 | 0 | 10.1423 | 0 | 236800 | 0 | 141105.5894 | 205.5376 | 0
1660 | 3 | 0 | 0 | 0.20573 | 8.4142 | 0 | 0 | 0 | 0 | 8.4142 | 0 | 236800 | 0 | 141105.5894 | 212.831 | 0
1661 | 3 | 0 | 0 | 0.17586 | 7.1925 | 0 | 0 | 0 | 0 | 7.1925 | 0 | 236800 | 0 | 141105.5894 | 219.0654 | 0
1662 | 3 | 0 | 0 | 0.21733 | 8.8888 | 0 | 0 | 0 | 0 | 8.8888 | 0 | 236800 | 0 | 141105.5894 | 226.7703 | 0
1663 | 3 | 0 | 0 | 0.18539 | 7.5823 | 0 | 0 | 0 | 0 | 7.5823 | 0 | 236800 | 0 | 141105.5894 | 233.3426 | 0
1664 | 3 | 1 | 0.26177 | 0.15004 | 81.7348 | 200 | 81.7348 | 118.2652 | 200 | 0 | 0 | 236600 | 200 | 141305.5894 | 115.0774 | 0
1665 | 3 | 1 | 0.63677 | 0.154 | 190.1964 | 200 | 190.1964 | 9.8036 | 200 | 0 | 0 | 236400 | 200 | 141505.5894 | 105.2738 | 0
1666 | 3 | 0 | 1 | 0.14163 | 294.5925 | 0 | 0 | 0 | 0 | 180 | 114.5925 | 236400 | 114.5925 | 141620.1819 | 261.2978 | 0
1667 | 3 | 0 | 1 | 0.15448 | 295.1182 | 0 | 0 | 0 | 0 | 180 | 115.1182 | 236400 | 115.1182 | 141735.3001 | 417.3218 | 0
1668 | 3 | 0 | 1 | 0.24773 | 298.9322 | 0 | 0 | 0 | 0 | 107.8545 | 191.0777 | 236400 | 191.0777 | 141926.3778 | 510.81 | 0
1669 | 3 | 0 | 1 | 0.23471 | 298.3997 | 0 | 0 | 0 | 0 | 0 | 200 | 236400 | 200 | 142126.3778 | 510.81 | 98.3997
1670 | 3 | 0 | 1 | 0.22482 | 297.9951 | 0 | 0 | 0 | 0 | 0 | 200 | 236400 | 200 | 142326.3778 | 510.81 | 97.9951
1671 | 3 | 0 | 1 | 0.18715 | 296.4544 | 0 | 0 | 0 | 0 | 0 | 200 | 236400 | 200 | 142526.3778 | 510.81 | 96.4544
1672 | 3 | 0 | 1 | 0.17441 | 295.9335 | 0 | 0 | 0 | 0 | 0 | 200 | 236400 | 200 | 142726.3778 | 510.81 | 95.9335
1673 | 3 | 0 | 0.63677 | 0.26505 | 194.7384 | 0 | 0 | 0 | 0 | 0 | 194.7384 | 236400 | 194.7384 | 142921.1162 | 510.81 | 0
1674 | 3 | 0 | 0.26177 | 0.34151 | 89.5661 | 0 | 0 | 0 | 0 | 0 | 89.5661 | 236400 | 89.5661 | 143010.6824 | 510.81 | 0
1675 | 3 | 0 | 0 | 0.28164 | 11.5189 | 0 | 0 | 0 | 0 | 0 | 11.5189 | 236400 | 11.5189 | 143022.2012 | 510.81 | 0
1676 | 3 | 1 | 0 | 0.24334 | 9.9527 | 200 | 9.9527 | 180 | 189.9527 | 0 | 0 | 236200 | 189.9527 | 143212.154 | 330.81 | 0
1677 | 3 | 1 | 0 | 0.23864 | 9.7603 | 200 | 9.7603 | 180 | 189.7603 | 0 | 0 | 236000 | 189.7603 | 143401.9143 | 150.81 | 0
1678 | 3 | 0 | 0 | 0.32367 | 13.2381 | 0 | 0 | 0 | 0 | 13.2381 | 0 | 236000 | 0 | 143401.9143 | 162.2848 | 0
1679 | 3 | 0 | 0 | 0.3733 | 15.2679 | 0 | 0 | 0 | 0 | 15.2679 | 0 | 236000 | 0 | 143401.9143 | 175.519 | 0
1680 | 3 | 0 | 0 | 0.57617 | 23.5653 | 0 | 0 | 0 | 0 | 23.5653 | 0 | 236000 | 0 | 143401.9143 | 195.9454 | 0
1681 | 3 | 0 | 0 | 0.48285 | 19.7486 | 0 | 0 | 0 | 0 | 19.7486 | 0 | 236000 | 0 | 143401.9143 | 213.0636 | 0
1682 | 3 | 0 | 0 | 0.37701 | 15.4199 | 0 | 0 | 0 | 0 | 15.4199 | 0 | 236000 | 0 | 143401.9143 | 226.4295 | 0
1683 | 3 | 0 | 0 | 0.43316 | 17.7162 | 0 | 0 | 0 | 0 | 17.7162 | 0 | 236000 | 0 | 143401.9143 | 241.7859 | 0
1684 | 3 | 0 | 0 | 0.33488 | 13.6967 | 0 | 0 | 0 | 0 | 13.6967 | 0 | 236000 | 0 | 143401.9143 | 253.6582 | 0
1685 | 3 | 0 | 0 | 0.56541 | 23.1252 | 0 | 0 | 0 | 0 | 23.1252 | 0 | 236000 | 0 | 143401.9143 | 273.7031 | 0
1686 | 3 | 0 | 0 | 0.57724 | 23.6091 | 0 | 0 | 0 | 0 | 23.6091 | 0 | 236000 | 0 | 143401.9143 | 294.1675 | 0
1687 | 3 | 0 | 0 | 0.5076 | 20.7608 | 0 | 0 | 0 | 0 | 20.7608 | 0 | 236000 | 0 | 143401.9143 | 312.1629 | 0
1688 | 3 | 1 | 0.23125 | 0.3891 | 82.6994 | 200 | 82.6994 | 117.3006 | 200 | 0 | 0 | 235800 | 200 | 143601.9143 | 194.8623 | 0
1689 | 3 | 1 | 0.56253 | 0.36009 | 177.1863 | 200 | 177.1863 | 22.8137 | 200 | 0 | 0 | 235600 | 200 | 143801.9143 | 172.0487 | 0
1690 | 3 | 0 | 0.89813 | 0.31061 | 272.0852 | 0 | 0 | 0 | 0 | 180 | 92.0852 | 235600 | 92.0852 | 143893.9995 | 328.0727 | 0
1691 | 3 | 0 | 1 | 0.35878 | 303.4739 | 0 | 0 | 0 | 0 | 180 | 123.4739 | 235600 | 123.4739 | 144017.4734 | 484.0967 | 0
1692 | 3 | 0 | 1 | 0.48209 | 308.5176 | 0 | 0 | 0 | 0 | 30.8184 | 200 | 235600 | 200 | 144217.4734 | 510.81 | 77.6993
1693 | 3 | 0 | 1 | 0.50132 | 309.304 | 0 | 0 | 0 | 0 | 0 | 200 | 235600 | 200 | 144417.4734 | 510.81 | 109.304
1694 | 3 | 0 | 1 | 0.5214 | 310.1254 | 0 | 0 | 0 | 0 | 0 | 200 | 235600 | 200 | 144617.4734 | 510.81 | 110.1254
1695 | 3 | 0 | 1 | 0.85447 | 323.7477 | 0 | 0 | 0 | 0 | 0 | 200 | 235600 | 200 | 144817.4734 | 510.81 | 123.7477
1696 | 3 | 0 | 0.89813 | 1 | 300.2811 | 0 | 0 | 0 | 0 | 0 | 200 | 235600 | 200 | 145017.4734 | 510.81 | 100.2811
1697 | 3 | 0 | 0.56253 | 1 | 203.3587 | 0 | 0 | 0 | 0 | 0 | 200 | 235600 | 200 | 145217.4734 | 510.81 | 3.3587
1698 | 3 | 0 | 0.23125 | 0.9603 | 106.0614 | 0 | 0 | 0 | 0 | 0 | 106.0614 | 235600 | 106.0614 | 145323.5348 | 510.81 | 0
1699 | 3 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 0 | 40.9 | 235600 | 40.9 | 145364.4348 | 510.81 | 0
1700 | 3 | 1 | 0 | 0.86176 | 35.2459 | 200 | 35.2459 | 164.7541 | 200 | 0 | 0 | 235400 | 200 | 145564.4348 | 346.0559 | 0
1701 | 3 | 1 | 0 | 0.57067 | 23.3404 | 200 | 23.3404 | 176.6596 | 200 | 0 | 0 | 235200 | 200 | 145764.4348 | 169.3963 | 0
1702 | 3 | 0 | 0 | 0.36374 | 14.8771 | 0 | 0 | 0 | 0 | 14.8771 | 0 | 235200 | 0 | 145764.4348 | 182.2918 | 0
1703 | 3 | 0 | 0 | 0.45814 | 18.7377 | 0 | 0 | 0 | 0 | 18.7377 | 0 | 235200 | 0 | 145764.4348 | 198.5337 | 0
1704 | 3 | 0 | 0 | 0.36441 | 14.9043 | 0 | 0 | 0 | 0 | 14.9043 | 0 | 235200 | 0 | 145764.4348 | 211.4527 | 0
1705 | 3 | 0 | 0 | 0.31928 | 13.0586 | 0 | 0 | 0 | 0 | 13.0586 | 0 | 235200 | 0 | 145764.4348 | 222.7719 | 0
1706 | 3 | 0 | 0 | 0.28333 | 11.5882 | 0 | 0 | 0 | 0 | 11.5882 | 0 | 235200 | 0 | 145764.4348 | 232.8166 | 0
1707 | 3 | 0 | 0 | 0.20872 | 8.5365 | 0 | 0 | 0 | 0 | 8.5365 | 0 | 235200 | 0 | 145764.4348 | 240.216 | 0
1708 | 3 | 0 | 0 | 0.26573 | 10.8683 | 0 | 0 | 0 | 0 | 10.8683 | 0 | 235200 | 0 | 145764.4348 | 249.6366 | 0
1709 | 3 | 0 | 0 | 0.24626 | 10.0722 | 0 | 0 | 0 | 0 | 10.0722 | 0 | 235200 | 0 | 145764.4348 | 258.3672 | 0
1710 | 3 | 0 | 0 | 0.25906 | 10.5956 | 0 | 0 | 0 | 0 | 10.5956 | 0 | 235200 | 0 | 145764.4348 | 267.5515 | 0
1711 | 3 | 0 | 0 | 0.22119 | 9.0468 | 0 | 0 | 0 | 0 | 9.0468 | 0 | 235200 | 0 | 145764.4348 | 275.3932 | 0
1712 | 3 | 1 | 0.22337 | 0.16528 | 71.2698 | 200 | 71.2698 | 128.7302 | 200 | 0 | 0 | 235000 | 200 | 145964.4348 | 146.663 | 0
1713 | 3 | 1 | 0.54337 | 0.21767 | 165.8271 | 200 | 165.8271 | 34.1729 | 200 | 0 | 0 | 234800 | 200 | 146164.4348 | 112.4901 | 0
1714 | 3 | 0 | 0.86754 | 0.16185 | 257.1648 | 0 | 0 | 0 | 0 | 180 | 77.1648 | 234800 | 77.1648 | 146241.5996 | 268.5141 | 0
1715 | 3 | 0 | 1 | 0.14286 | 294.6432 | 0 | 0 | 0 | 0 | 180 | 114.6432 | 234800 | 114.6432 | 146356.2428 | 424.5381 | 0
1716 | 3 | 0 | 1 | 0.1461 | 294.7756 | 0 | 0 | 0 | 0 | 99.5291 | 195.2464 | 234800 | 195.2464 | 146551.4892 | 510.81 | 0
1717 | 3 | 0 | 1 | 0.17509 | 295.9612 | 0 | 0 | 0 | 0 | 0 | 200 | 234800 | 200 | 146751.4892 | 510.81 | 95.9612
1718 | 3 | 0 | 1 | 0.161 | 295.3851 | 0 | 0 | 0 | 0 | 0 | 200 | 234800 | 200 | 146951.4892 | 510.81 | 95.3851
1719 | 3 | 0 | 1 | 0.23748 | 298.5129 | 0 | 0 | 0 | 0 | 0 | 200 | 234800 | 200 | 147151.4892 | 510.81 | 98.5129
1720 | 3 | 0 | 0.86754 | 0.22338 | 259.6812 | 0 | 0 | 0 | 0 | 0 | 200 | 234800 | 200 | 147351.4892 | 510.81 | 59.6812
1721 | 3 | 0 | 0.54337 | 0.26751 | 167.8657 | 0 | 0 | 0 | 0 | 0 | 167.8657 | 234800 | 167.8657 | 147519.3549 | 510.81 | 0
1722 | 3 | 0 | 0.22337 | 0.19052 | 72.3021 | 0 | 0 | 0 | 0 | 0 | 72.3021 | 234800 | 72.3021 | 147591.657 | 510.81 | 0
1723 | 3 | 0 | 0 | 0.19589 | 8.012 | 0 | 0 | 0 | 0 | 0 | 8.012 | 234800 | 8.012 | 147599.669 | 510.81 | 0
1724 | 3 | 1 | 0 | 0.15332 | 6.2706 | 200 | 6.2706 | 180 | 186.2706 | 0 | 0 | 234600 | 186.2706 | 147785.9396 | 330.81 | 0
1725 | 3 | 1 | 0 | 0.14946 | 6.1128 | 200 | 6.1128 | 180 | 186.1128 | 0 | 0 | 234400 | 186.1128 | 147972.0523 | 150.81 | 0
1726 | 3 | 0 | 0 | 0.195 | 7.9753 | 0 | 0 | 0 | 0 | 7.9753 | 0 | 234400 | 0 | 147972.0523 | 157.723 | 0
1727 | 3 | 0 | 0 | 0.1748 | 7.1495 | 0 | 0 | 0 | 0 | 7.1495 | 0 | 234400 | 0 | 147972.0523 | 163.9202 | 0
1728 | 3 | 0 | 0 | 0.21968 | 8.9849 | 0 | 0 | 0 | 0 | 8.9849 | 0 | 234400 | 0 | 147972.0523 | 171.7083 | 0
1729 | 3 | 0 | 0 | 0.16666 | 6.8165 | 0 | 0 | 0 | 0 | 6.8165 | 0 | 234400 | 0 | 147972.0523 | 177.6168 | 0
1730 | 3 | 0 | 0 | 0.0976 | 3.9918 | 0 | 0 | 0 | 0 | 3.9918 | 0 | 234400 | 0 | 147972.0523 | 181.077 | 0
1731 | 3 | 0 | 0 | 0.16739 | 6.8465 | 0 | 0 | 0 | 0 | 6.8465 | 0 | 234400 | 0 | 147972.0523 | 187.0115 | 0
1732 | 3 | 0 | 0 | 0.30428 | 12.445 | 0 | 0 | 0 | 0 | 12.445 | 0 | 234400 | 0 | 147972.0523 | 197.7988 | 0
1733 | 3 | 0 | 0 | 0.30469 | 12.4618 | 0 | 0 | 0 | 0 | 12.4618 | 0 | 234400 | 0 | 147972.0523 | 208.6007 | 0
1734 | 3 | 0 | 0 | 0.45931 | 18.7859 | 0 | 0 | 0 | 0 | 18.7859 | 0 | 234400 | 0 | 147972.0523 | 224.8843 | 0
1735 | 3 | 0 | 0 | 0.6962 | 28.4744 | 0 | 0 | 0 | 0 | 28.4744 | 0 | 234400 | 0 | 147972.0523 | 249.5659 | 0
1736 | 3 | 1 | 0.23646 | 0.53832 | 90.306 | 200 | 90.306 | 109.694 | 200 | 0 | 0 | 234200 | 200 | 148172.0523 | 139.8719 | 0
1737 | 3 | 1 | 0.5752 | 0.38066 | 181.6863 | 200 | 181.6863 | 18.3137 | 200 | 0 | 0 | 234000 | 200 | 148372.0523 | 121.5582 | 0
1738 | 3 | 0 | 0.91836 | 0.43187 | 282.8854 | 0 | 0 | 0 | 0 | 180 | 102.8854 | 234000 | 102.8854 | 148474.9378 | 277.5822 | 0
1739 | 3 | 0 | 1 | 0.29833 | 301.0017 | 0 | 0 | 0 | 0 | 180 | 121.0017 | 234000 | 121.0017 | 148595.9394 | 433.6062 | 0
1740 | 3 | 0 | 1 | 0.27074 | 299.8733 | 0 | 0 | 0 | 0 | 89.0676 | 200 | 234000 | 200 | 148795.9394 | 510.81 | 10.8057
1741 | 3 | 0 | 1 | 0.19628 | 296.8278 | 0 | 0 | 0 | 0 | 0 | 200 | 234000 | 200 | 148995.9394 | 510.81 | 96.8278
1742 | 3 | 0 | 1 | 0.21113 | 297.4353 | 0 | 0 | 0 | 0 | 0 | 200 | 234000 | 200 | 149195.9394 | 510.81 | 97.4353
1743 | 3 | 0 | 1 | 0.18695 | 296.4464 | 0 | 0 | 0 | 0 | 0 | 200 | 234000 | 200 | 149395.9394 | 510.81 | 96.4464
1744 | 3 | 0 | 0.91836 | 0.19702 | 273.2803 | 0 | 0 | 0 | 0 | 0 | 200 | 234000 | 200 | 149595.9394 | 510.81 | 73.2803
1745 | 3 | 0 | 0.5752 | 0.19496 | 174.091 | 0 | 0 | 0 | 0 | 0 | 174.091 | 234000 | 174.091 | 149770.0304 | 510.81 | 0
1746 | 3 | 0 | 0.23646 | 0.20424 | 76.6422 | 0 | 0 | 0 | 0 | 0 | 76.6422 | 234000 | 76.6422 | 149846.6726 | 510.81 | 0
1747 | 3 | 0 | 0 | 0.24719 | 10.11 | 0 | 0 | 0 | 0 | 0 | 10.11 | 234000 | 10.11 | 149856.7826 | 510.81 | 0
1748 | 3 | 1 | 0 | 0.39359 | 16.0978 | 200 | 16.0978 | 180 | 196.0978 | 0 | 0 | 233800 | 196.0978 | 150052.8804 | 330.81 | 0
1749 | 3 | 1 | 0 | 0.3372 | 13.7914 | 200 | 13.7914 | 180 | 193.7914 | 0 | 0 | 233600 | 193.7914 | 150246.6718 | 150.81 | 0
1750 | 3 | 0 | 0 | 0.32604 | 13.3349 | 0 | 0 | 0 | 0 | 13.3349 | 0 | 233600 | 0 | 150246.6718 | 162.3687 | 0
1751 | 3 | 0 | 0 | 0.34998 | 14.3144 | 0 | 0 | 0 | 0 | 14.3144 | 0 | 233600 | 0 | 150246.6718 | 174.7764 | 0
1752 | 3 | 0 | 0 | 0.46557 | 19.0419 | 0 | 0 | 0 | 0 | 19.0419 | 0 | 233600 | 0 | 150246.6718 | 191.282 | 0
1753 | 3 | 0 | 0 | 0.5515 | 22.5562 | 0 | 0 | 0 | 0 | 22.5562 | 0 | 233600 | 0 | 150246.6718 | 210.8337 | 0
1754 | 3 | 0 | 0 | 0.36908 | 15.0955 | 0 | 0 | 0 | 0 | 15.0955 | 0 | 233600 | 0 | 150246.6718 | 223.9184 | 0
1755 | 3 | 0 | 0 | 0.25647 | 10.4896 | 0 | 0 | 0 | 0 | 10.4896 | 0 | 233600 | 0 | 150246.6718 | 233.0108 | 0
1756 | 3 | 0 | 0 | 0.34799 | 14.2328 | 0 | 0 | 0 | 0 | 14.2328 | 0 | 233600 | 0 | 150246.6718 | 245.3478 | 0
1757 | 3 | 0 | 0 | 0.4585 | 18.7527 | 0 | 0 | 0 | 0 | 18.7527 | 0 | 233600 | 0 | 150246.6718 | 261.6027 | 0
1758 | 3 | 0 | 0 | 0.4454 | 18.217 | 0 | 0 | 0 | 0 | 18.217 | 0 | 233600 | 0 | 150246.6718 | 277.3932 | 0
1759 | 3 | 0 | 0 | 0.65795 | 26.9103 | 0 | 0 | 0 | 0 | 26.9103 | 0 | 233600 | 0 | 150246.6718 | 300.719 | 0
1760 | 3 | 1 | 0.22564 | 0.54625 | 87.5055 | 200 | 87.5055 | 112.4945 | 200 | 0 | 0 | 233400 | 200 | 150446.6718 | 188.2245 | 0
1761 | 3 | 1 | 0.54887 | 0.39764 | 174.7784 | 200 | 174.7784 | 25.2216 | 200 | 0 | 0 | 233200 | 200 | 150646.6718 | 163.0029 | 0
1762 | 3 | 0 | 0.87633 | 0.45725 | 271.7858 | 0 | 0 | 0 | 0 | 180 | 91.7858 | 233200 | 91.7858 | 150738.4575 | 319.0269 | 0
1763 | 3 | 0 | 1 | 0.39537 | 304.9707 | 0 | 0 | 0 | 0 | 180 | 124.9707 | 233200 | 124.9707 | 150863.4282 | 475.0509 | 0
1764 | 3 | 0 | 1 | 0.35022 | 303.1241 | 0 | 0 | 0 | 0 | 41.2541 | 200 | 233200 | 200 | 151063.4282 | 510.81 | 61.8699
1765 | 3 | 0 | 1 | 0.24855 | 298.9659 | 0 | 0 | 0 | 0 | 0 | 200 | 233200 | 200 | 151263.4282 | 510.81 | 98.9659
1766 | 3 | 0 | 1 | 0.26888 | 299.7974 | 0 | 0 | 0 | 0 | 0 | 200 | 233200 | 200 | 151463.4282 | 510.81 | 99.7974
1767 | 3 | 0 | 1 | 0.34863 | 303.0588 | 0 | 0 | 0 | 0 | 0 | 200 | 233200 | 200 | 151663.4282 | 510.81 | 103.0588
1768 | 3 | 0 | 0.87633 | 0.25816 | 263.6429 | 0 | 0 | 0 | 0 | 0 | 200 | 233200 | 200 | 151863.4282 | 510.81 | 63.6429
1769 | 3 | 0 | 0.54887 | 0.17486 | 165.6666 | 0 | 0 | 0 | 0 | 0 | 165.6666 | 233200 | 165.6666 | 152029.0948 | 510.81 | 0
1770 | 3 | 0 | 0.22564 | 0.16443 | 71.8889 | 0 | 0 | 0 | 0 | 0 | 71.8889 | 233200 | 71.8889 | 152100.9838 | 510.81 | 0
1771 | 3 | 0 | 0 | 0.14694 | 6.0099 | 0 | 0 | 0 | 0 | 0 | 6.0099 | 233200 | 6.0099 | 152106.9937 | 510.81 | 0
1772 | 3 | 1 | 0 | 0.23106 | 9.4504 | 200 | 9.4504 | 180 | 189.4504 | 0 | 0 | 233000 | 189.4504 | 152296.444 | 330.81 | 0
1773 | 3 | 1 | 0 | 0.22761 | 9.3092 | 200 | 9.3092 | 180 | 189.3092 | 0 | 0 | 232800 | 189.3092 | 152485.7533 | 150.81 | 0
1774 | 3 | 0 | 0 | 0.28059 | 11.476 | 0 | 0 | 0 | 0 | 11.476 | 0 | 232800 | 0 | 152485.7533 | 160.7574 | 0
1775 | 3 | 0 | 0 | 0.26314 | 10.7626 | 0 | 0 | 0 | 0 | 10.7626 | 0 | 232800 | 0 | 152485.7533 | 170.0865 | 0
1776 | 3 | 0 | 0 | 0.21486 | 8.7877 | 0 | 0 | 0 | 0 | 8.7877 | 0 | 232800 | 0 | 152485.7533 | 177.7037 | 0
1777 | 3 | 0 | 0 | 0.30594 | 12.5131 | 0 | 0 | 0 | 0 | 12.5131 | 0 | 232800 | 0 | 152485.7533 | 188.55 | 0
1778 | 3 | 0 | 0 | 0.29689 | 12.1428 | 0 | 0 | 0 | 0 | 12.1428 | 0 | 232800 | 0 | 152485.7533 | 199.0754 | 0
1779 | 3 | 0 | 0 | 0.27785 | 11.3641 | 0 | 0 | 0 | 0 | 11.3641 | 0 | 232800 | 0 | 152485.7533 | 208.9258 | 0
1780 | 3 | 0 | 0 | 0.32126 | 13.1393 | 0 | 0 | 0 | 0 | 13.1393 | 0 | 232800 | 0 | 152485.7533 | 220.315 | 0
1781 | 3 | 0 | 0 | 0.54664 | 22.3576 | 0 | 0 | 0 | 0 | 22.3576 | 0 | 232800 | 0 | 152485.7533 | 239.6946 | 0
1782 | 3 | 0 | 0 | 0.38164 | 15.6089 | 0 | 0 | 0 | 0 | 15.6089 | 0 | 232800 | 0 | 152485.7533 | 253.2244 | 0
1783 | 3 | 0 | 0 | 0.39977 | 16.3507 | 0 | 0 | 0 | 0 | 16.3507 | 0 | 232800 | 0 | 152485.7533 | 267.3972 | 0
1784 | 3 | 1 | 0.21071 | 0.4326 | 78.546 | 200 | 78.546 | 121.454 | 200 | 0 | 0 | 232600 | 200 | 152685.7533 | 145.9432 | 0
1785 | 3 | 1 | 0.51256 | 0.35744 | 162.6475 | 200 | 162.6475 | 37.3525 | 200 | 0 | 0 | 232400 | 200 | 152885.7533 | 108.5907 | 0
1786 | 3 | 0 | 0.81836 | 0.35652 | 250.9231 | 0 | 0 | 0 | 0 | 180 | 70.9231 | 232400 | 70.9231 | 152956.6763 | 264.6147 | 0
1787 | 3 | 0 | 1 | 0.64766 | 315.2893 | 0 | 0 | 0 | 0 | 180 | 135.2893 | 232400 | 135.2893 | 153091.9657 | 420.6387 | 0
1788 | 3 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 104.0278 | 200 | 232400 | 200 | 153291.9657 | 510.81 | 25.6722
1789 | 3 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 0 | 200 | 232400 | 200 | 153491.9657 | 510.81 | 129.7
1790 | 3 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 0 | 200 | 232400 | 200 | 153691.9657 | 510.81 | 129.7
1791 | 3 | 0 | 1 | 0.69047 | 317.0402 | 0 | 0 | 0 | 0 | 0 | 200 | 232400 | 200 | 153891.9657 | 510.81 | 117.0402
1792 | 3 | 0 | 0.81836 | 0.70515 | 265.1821 | 0 | 0 | 0 | 0 | 0 | 200 | 232400 | 200 | 154091.9657 | 510.81 | 65.1821
1793 | 3 | 0 | 0.51256 | 1 | 188.9282 | 0 | 0 | 0 | 0 | 0 | 188.9282 | 232400 | 188.9282 | 154280.8939 | 510.81 | 0
1794 | 3 | 0 | 0.21071 | 0.98814 | 101.2678 | 0 | 0 | 0 | 0 | 0 | 101.2678 | 232400 | 101.2678 | 154382.1617 | 510.81 | 0
1795 | 3 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 0 | 40.9 | 232400 | 40.9 | 154423.0617 | 510.81 | 0
1796 | 3 | 1 | 0 | 0.87134 | 35.6379 | 200 | 35.6379 | 164.3621 | 200 | 0 | 0 | 232200 | 200 | 154623.0617 | 346.4479 | 0
1797 | 3 | 1 | 0 | 0.83902 | 34.3159 | 200 | 34.3159 | 165.6841 | 200 | 0 | 0 | 232000 | 200 | 154823.0617 | 180.7638 | 0
1798 | 3 | 0 | 0 | 0.97493 | 39.8745 | 0 | 0 | 0 | 0 | 39.8745 | 0 | 232000 | 0 | 154823.0617 | 215.327 | 0
1799 | 3 | 0 | 0 | 0.95377 | 39.0091 | 0 | 0 | 0 | 0 | 39.0091 | 0 | 232000 | 0 | 154823.0617 | 249.1401 | 0
1800 | 3 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 232000 | 0 | 154823.0617 | 284.5922 | 0
1801 | 3 | 0 | 0 | 0.73091 | 29.894 | 0 | 0 | 0 | 0 | 29.894 | 0 | 232000 | 0 | 154823.0617 | 310.5043 | 0
1802 | 3 | 0 | 0 | 0.66388 | 27.1527 | 0 | 0 | 0 | 0 | 27.1527 | 0 | 232000 | 0 | 154823.0617 | 334.0403 | 0
1803 | 3 | 0 | 0 | 0.60381 | 24.6956 | 0 | 0 | 0 | 0 | 24.6956 | 0 | 232000 | 0 | 154823.0617 | 355.4464 | 0
1804 | 3 | 0 | 0 | 0.4254 | 17.3991 | 0 | 0 | 0 | 0 | 17.3991 | 0 | 232000 | 0 | 154823.0617 | 370.5279 | 0
1805 | 3 | 0 | 0 | 0.39243 | 16.0506 | 0 | 0 | 0 | 0 | 16.0506 | 0 | 232000 | 0 | 154823.0617 | 384.4406 | 0
1806 | 3 | 0 | 0 | 0.43097 | 17.6266 | 0 | 0 | 0 | 0 | 17.6266 | 0 | 232000 | 0 | 154823.0617 | 399.7193 | 0
1807 | 3 | 0 | 0 | 0.53785 | 21.9982 | 0 | 0 | 0 | 0 | 21.9982 | 0 | 232000 | 0 | 154823.0617 | 418.7873 | 0
1808 | 3 | 1 | 0.22402 | 0.55285 | 87.3092 | 200 | 87.3092 | 112.6908 | 200 | 0 | 0 | 231800 | 200 | 155023.0617 | 306.0966 | 0
1809 | 3 | 1 | 0.54495 | 0.94194 | 195.907 | 200 | 195.907 | 4.093 | 200 | 0 | 0 | 231600 | 200 | 155223.0617 | 302.0036 | 0
1810 | 3 | 0 | 0.87006 | 0.60207 | 275.8995 | 0 | 0 | 0 | 0 | 180 | 95.8995 | 231600 | 95.8995 | 155318.9612 | 458.0276 | 0
1811 | 3 | 0 | 1 | 0.80041 | 321.5366 | 0 | 0 | 0 | 0 | 60.8934 | 200 | 231600 | 200 | 155518.9612 | 510.81 | 60.6432
1812 | 3 | 0 | 1 | 0.99443 | 329.4723 | 0 | 0 | 0 | 0 | 0 | 200 | 231600 | 200 | 155718.9612 | 510.81 | 129.4723
1813 | 3 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 0 | 200 | 231600 | 200 | 155918.9612 | 510.81 | 129.7
1814 | 3 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 0 | 200 | 231600 | 200 | 156118.9612 | 510.81 | 129.7
1815 | 3 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 0 | 200 | 231600 | 200 | 156318.9612 | 510.81 | 129.7
1816 | 3 | 0 | 0.87006 | 1 | 292.1748 | 0 | 0 | 0 | 0 | 0 | 200 | 231600 | 200 | 156518.9612 | 510.81 | 92.1748
1817 | 3 | 0 | 0.54495 | 0.90997 | 194.5992 | 0 | 0 | 0 | 0 | 0 | 194.5992 | 231600 | 194.5992 | 156713.5604 | 510.81 | 0
1818 | 3 | 0 | 0.22402 | 0.98602 | 105.0262 | 0 | 0 | 0 | 0 | 0 | 105.0262 | 231600 | 105.0262 | 156818.5865 | 510.81 | 0
1819 | 3 | 0 | 0 | 0.79888 | 32.6742 | 0 | 0 | 0 | 0 | 0 | 32.6742 | 231600 | 32.6742 | 156851.2607 | 510.81 | 0
1820 | 3 | 1 | 0 | 0.90807 | 37.1401 | 200 | 37.1401 | 162.8599 | 200 | 0 | 0 | 231400 | 200 | 157051.2607 | 347.9501 | 0
1821 | 3 | 1 | 0 | 0.79822 | 32.647 | 200 | 32.647 | 167.353 | 200 | 0 | 0 | 231200 | 200 | 157251.2607 | 180.5971 | 0
1822 | 3 | 0 | 0 | 0.61536 | 25.1683 | 0 | 0 | 0 | 0 | 25.1683 | 0 | 231200 | 0 | 157251.2607 | 202.413 | 0
1823 | 3 | 0 | 0 | 0.7696 | 31.4764 | 0 | 0 | 0 | 0 | 31.4764 | 0 | 231200 | 0 | 157251.2607 | 229.6968 | 0
1824 | 3 | 0 | 0 | 0.6021 | 24.6258 | 0 | 0 | 0 | 0 | 24.6258 | 0 | 231200 | 0 | 157251.2607 | 251.0424 | 0
1825 | 3 | 0 | 0 | 0.60884 | 24.9016 | 0 | 0 | 0 | 0 | 24.9016 | 0 | 231200 | 0 | 157251.2607 | 272.6271 | 0
1826 | 3 | 0 | 0 | 0.85003 | 34.7661 | 0 | 0 | 0 | 0 | 34.7661 | 0 | 231200 | 0 | 157251.2607 | 302.7624 | 0
1827 | 3 | 0 | 0 | 0.63695 | 26.0513 | 0 | 0 | 0 | 0 | 26.0513 | 0 | 231200 | 0 | 157251.2607 | 325.3436 | 0
1828 | 3 | 0 | 0 | 0.87929 | 35.963 | 0 | 0 | 0 | 0 | 35.963 | 0 | 231200 | 0 | 157251.2607 | 356.5164 | 0
1829 | 3 | 0 | 0 | 0.62838 | 25.7007 | 0 | 0 | 0 | 0 | 25.7007 | 0 | 231200 | 0 | 157251.2607 | 378.7937 | 0
1830 | 3 | 0 | 0 | 0.69269 | 28.3311 | 0 | 0 | 0 | 0 | 28.3311 | 0 | 231200 | 0 | 157251.2607 | 403.3511 | 0
1831 | 3 | 0 | 0 | 0.45789 | 18.7279 | 0 | 0 | 0 | 0 | 18.7279 | 0 | 231200 | 0 | 157251.2607 | 419.5844 | 0
1832 | 3 | 1 | 0.23901 | 0.37216 | 84.2485 | 200 | 84.2485 | 115.7515 | 200 | 0 | 0 | 231000 | 200 | 157451.2607 | 303.8329 | 0
1833 | 3 | 1 | 0.58142 | 0.47523 | 187.3499 | 200 | 187.3499 | 12.6501 | 200 | 0 | 0 | 230800 | 200 | 157651.2607 | 291.1828 | 0
1834 | 3 | 0 | 0.92829 | 0.62589 | 293.6881 | 0 | 0 | 0 | 0 | 180 | 113.6881 | 230800 | 113.6881 | 157764.9488 | 447.2068 | 0
1835 | 3 | 0 | 1 | 0.60689 | 313.6219 | 0 | 0 | 0 | 0 | 73.377 | 200 | 230800 | 200 | 157964.9488 | 510.81 | 40.2449
1836 | 3 | 0 | 1 | 0.42211 | 306.0643 | 0 | 0 | 0 | 0 | 0 | 200 | 230800 | 200 | 158164.9488 | 510.81 | 106.0643
1837 | 3 | 0 | 1 | 0.40183 | 305.235 | 0 | 0 | 0 | 0 | 0 | 200 | 230800 | 200 | 158364.9488 | 510.81 | 105.235
1838 | 3 | 0 | 1 | 0.43485 | 306.5854 | 0 | 0 | 0 | 0 | 0 | 200 | 230800 | 200 | 158564.9488 | 510.81 | 106.5854
1839 | 3 | 0 | 1 | 0.31006 | 301.4814 | 0 | 0 | 0 | 0 | 0 | 200 | 230800 | 200 | 158764.9488 | 510.81 | 101.4814
1840 | 3 | 0 | 0.92829 | 0.35783 | 282.7244 | 0 | 0 | 0 | 0 | 0 | 200 | 230800 | 200 | 158964.9488 | 510.81 | 82.7244
1841 | 3 | 0 | 0.58142 | 0.27587 | 179.1961 | 0 | 0 | 0 | 0 | 0 | 179.1961 | 230800 | 179.1961 | 159144.145 | 510.81 | 0
1842 | 3 | 0 | 0.23901 | 0.28072 | 80.5088 | 0 | 0 | 0 | 0 | 0 | 80.5088 | 230800 | 80.5088 | 159224.6537 | 510.81 | 0
1843 | 3 | 0 | 0 | 0.42869 | 17.5335 | 0 | 0 | 0 | 0 | 0 | 17.5335 | 230800 | 17.5335 | 159242.1873 | 510.81 | 0
1844 | 3 | 1 | 0 | 0.46743 | 19.1178 | 200 | 19.1178 | 180 | 199.1178 | 0 | 0 | 230600 | 199.1178 | 159441.3051 | 330.81 | 0
1845 | 3 | 1 | 0 | 0.66717 | 27.287 | 200 | 27.287 | 172.713 | 200 | 0 | 0 | 230400 | 200 | 159641.3051 | 158.097 | 0
1846 | 3 | 0 | 0 | 0.62038 | 25.3734 | 0 | 0 | 0 | 0 | 25.3734 | 0 | 230400 | 0 | 159641.3051 | 180.0907 | 0
1847 | 3 | 0 | 0 | 0.4689 | 19.1779 | 0 | 0 | 0 | 0 | 19.1779 | 0 | 230400 | 0 | 159641.3051 | 196.7141 | 0
1848 | 3 | 0 | 0 | 0.37152 | 15.1952 | 0 | 0 | 0 | 0 | 15.1952 | 0 | 230400 | 0 | 159641.3051 | 209.8853 | 0
1849 | 3 | 0 | 0 | 0.35257 | 14.4199 | 0 | 0 | 0 | 0 | 14.4199 | 0 | 230400 | 0 | 159641.3051 | 222.3845 | 0
1850 | 3 | 0 | 0 | 0.24445 | 9.9981 | 0 | 0 | 0 | 0 | 9.9981 | 0 | 230400 | 0 | 159641.3051 | 231.0509 | 0
1851 | 3 | 0 | 0 | 0.25849 | 10.572 | 0 | 0 | 0 | 0 | 10.572 | 0 | 230400 | 0 | 159641.3051 | 240.2148 | 0
1852 | 3 | 0 | 0 | 0.29371 | 12.0127 | 0 | 0 | 0 | 0 | 12.0127 | 0 | 230400 | 0 | 159641.3051 | 250.6273 | 0
1853 | 3 | 0 | 0 | 0.2646 | 10.8221 | 0 | 0 | 0 | 0 | 10.8221 | 0 | 230400 | 0 | 159641.3051 | 260.008 | 0
1854 | 3 | 0 | 0 | 0.24199 | 9.8974 | 0 | 0 | 0 | 0 | 9.8974 | 0 | 230400 | 0 | 159641.3051 | 268.587 | 0
1855 | 3 | 0 | 0 | 0.17056 | 6.9757 | 0 | 0 | 0 | 0 | 6.9757 | 0 | 230400 | 0 | 159641.3051 | 274.6336 | 0
1856 | 3 | 1 | 0.2443 | 0.22049 | 79.5723 | 200 | 79.5723 | 120.4277 | 200 | 0 | 0 | 230200 | 200 | 159841.3051 | 154.2059 | 0
1857 | 3 | 1 | 0.59428 | 0.34059 | 185.5581 | 200 | 185.5581 | 14.4419 | 200 | 0 | 0 | 230000 | 200 | 160041.3051 | 139.764 | 0
1858 | 3 | 0 | 0.94882 | 0.39036 | 289.9862 | 0 | 0 | 0 | 0 | 180 | 109.9862 | 230000 | 109.9862 | 160151.2913 | 295.788 | 0
1859 | 3 | 0 | 1 | 0.4864 | 308.6938 | 0 | 0 | 0 | 0 | 180 | 128.6938 | 230000 | 128.6938 | 160279.9851 | 451.812 | 0
1860 | 3 | 0 | 1 | 0.52073 | 310.0979 | 0 | 0 | 0 | 0 | 68.0642 | 200 | 230000 | 200 | 160479.9851 | 510.81 | 42.0337
1861 | 3 | 0 | 1 | 0.55674 | 311.5708 | 0 | 0 | 0 | 0 | 0 | 200 | 230000 | 200 | 160679.9851 | 510.81 | 111.5708
1862 | 3 | 0 | 1 | 0.48506 | 308.6389 | 0 | 0 | 0 | 0 | 0 | 200 | 230000 | 200 | 160879.9851 | 510.81 | 108.6389
1863 | 3 | 0 | 1 | 0.44022 | 306.805 | 0 | 0 | 0 | 0 | 0 | 200 | 230000 | 200 | 161079.9851 | 510.81 | 106.805
1864 | 3 | 0 | 0.94882 | 0.36547 | 288.968 | 0 | 0 | 0 | 0 | 0 | 200 | 230000 | 200 | 161279.9851 | 510.81 | 88.968
1865 | 3 | 0 | 0.59428 | 0.44653 | 189.8908 | 0 | 0 | 0 | 0 | 0 | 189.8908 | 230000 | 189.8908 | 161469.8759 | 510.81 | 0
1866 | 3 | 0 | 0.2443 | 0.32566 | 83.8737 | 0 | 0 | 0 | 0 | 0 | 83.8737 | 230000 | 83.8737 | 161553.7496 | 510.81 | 0
1867 | 3 | 0 | 0 | 0.26217 | 10.7229 | 0 | 0 | 0 | 0 | 0 | 10.7229 | 230000 | 10.7229 | 161564.4725 | 510.81 | 0
1868 | 3 | 1 | 0 | 0.25028 | 10.2366 | 200 | 10.2366 | 180 | 190.2366 | 0 | 0 | 229800 | 190.2366 | 161754.7091 | 330.81 | 0
1869 | 3 | 1 | 0 | 0.1884 | 7.7058 | 200 | 7.7058 | 180 | 187.7058 | 0 | 0 | 229600 | 187.7058 | 161942.4149 | 150.81 | 0
1870 | 3 | 0 | 0 | 0.21687 | 8.87 | 0 | 0 | 0 | 0 | 8.87 | 0 | 229600 | 0 | 161942.4149 | 158.4985 | 0
1871 | 3 | 0 | 0 | 0.2012 | 8.229 | 0 | 0 | 0 | 0 | 8.229 | 0 | 229600 | 0 | 161942.4149 | 165.6314 | 0
1872 | 3 | 0 | 0 | 0.23923 | 9.7845 | 0 | 0 | 0 | 0 | 9.7845 | 0 | 229600 | 0 | 161942.4149 | 174.1126 | 0
1873 | 3 | 0 | 0 | 0.20734 | 8.4801 | 0 | 0 | 0 | 0 | 8.4801 | 0 | 229600 | 0 | 161942.4149 | 181.4632 | 0
1874 | 3 | 0 | 0 | 0.1433 | 5.861 | 0 | 0 | 0 | 0 | 5.861 | 0 | 229600 | 0 | 161942.4149 | 186.5435 | 0
1875 | 3 | 0 | 0 | 0.1374 | 5.6196 | 0 | 0 | 0 | 0 | 5.6196 | 0 | 229600 | 0 | 161942.4149 | 191.4146 | 0
1876 | 3 | 0 | 0 | 0.1393 | 5.6974 | 0 | 0 | 0 | 0 | 5.6974 | 0 | 229600 | 0 | 161942.4149 | 196.3531 | 0
1877 | 3 | 0 | 0 | 0.13532 | 5.5347 | 0 | 0 | 0 | 0 | 5.5347 | 0 | 229600 | 0 | 161942.4149 | 201.1506 | 0
1878 | 3 | 0 | 0 | 0.13366 | 5.4669 | 0 | 0 | 0 | 0 | 5.4669 | 0 | 229600 | 0 | 161942.4149 | 205.8892 | 0
1879 | 3 | 0 | 0 | 0.15374 | 6.2879 | 0 | 0 | 0 | 0 | 6.2879 | 0 | 229600 | 0 | 161942.4149 | 211.3396 | 0
1880 | 3 | 1 | 0.22752 | 0.18116 | 73.1171 | 200 | 73.1171 | 126.8829 | 200 | 0 | 0 | 229400 | 200 | 162142.4149 | 84.4567 | 0
1881 | 3 | 1 | 0.55346 | 0.32543 | 173.1483 | 200 | 173.1483 | 26.8517 | 200 | 0 | 0 | 229200 | 200 | 162342.4149 | 57.605 | 0
1882 | 3 | 0 | 0.88365 | 0.38258 | 270.8449 | 0 | 0 | 0 | 0 | 180 | 90.8449 | 229200 | 90.8449 | 162433.2598 | 213.629 | 0
1883 | 3 | 0 | 1 | 0.58703 | 312.8096 | 0 | 0 | 0 | 0 | 180 | 132.8096 | 229200 | 132.8096 | 162566.0694 | 369.653 | 0
1884 | 3 | 0 | 1 | 0.87229 | 324.4767 | 0 | 0 | 0 | 0 | 162.8484 | 161.6283 | 229200 | 161.6283 | 162727.6977 | 510.81 | 0
1885 | 3 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 0 | 200 | 229200 | 200 | 162927.6977 | 510.81 | 129.7
1886 | 3 | 0 | 1 | 0.97023 | 328.4823 | 0 | 0 | 0 | 0 | 0 | 200 | 229200 | 200 | 163127.6977 | 510.81 | 128.4823
1887 | 3 | 0 | 1 | 0.68045 | 316.6303 | 0 | 0 | 0 | 0 | 0 | 200 | 229200 | 200 | 163327.6977 | 510.81 | 116.6303
1888 | 3 | 0 | 0.88365 | 0.69023 | 283.4281 | 0 | 0 | 0 | 0 | 0 | 200 | 229200 | 200 | 163527.6977 | 510.81 | 83.4281
1889 | 3 | 0 | 0.55346 | 0.70303 | 188.5924 | 0 | 0 | 0 | 0 | 0 | 188.5924 | 229200 | 188.5924 | 163716.2901 | 510.81 | 0
1890 | 3 | 0 | 0.22752 | 1 | 106.6078 | 0 | 0 | 0 | 0 | 0 | 106.6078 | 229200 | 106.6078 | 163822.8979 | 510.81 | 0
1891 | 3 | 0 | 0 | 0.8437 | 34.5073 | 0 | 0 | 0 | 0 | 0 | 34.5073 | 229200 | 34.5073 | 163857.4052 | 510.81 | 0
1892 | 3 | 1 | 0 | 0.53904 | 22.0467 | 200 | 22.0467 | 177.9533 | 200 | 0 | 0 | 229000 | 200 | 164057.4052 | 332.8567 | 0
1893 | 3 | 1 | 0 | 0.46726 | 19.1111 | 200 | 19.1111 | 180 | 199.1111 | 0 | 0 | 228800 | 199.1111 | 164256.5163 | 152.8567 | 0
1894 | 3 | 0 | 0 | 0.32247 | 13.1889 | 0 | 0 | 0 | 0 | 13.1889 | 0 | 228800 | 0 | 164256.5163 | 164.2888 | 0
1895 | 3 | 0 | 0 | 0.34523 | 14.1199 | 0 | 0 | 0 | 0 | 14.1199 | 0 | 228800 | 0 | 164256.5163 | 176.5279 | 0
1896 | 3 | 0 | 0 | 0.30781 | 12.5895 | 0 | 0 | 0 | 0 | 12.5895 | 0 | 228800 | 0 | 164256.5163 | 187.4404 | 0
1897 | 3 | 0 | 0 | 0.27381 | 11.1988 | 0 | 0 | 0 | 0 | 11.1988 | 0 | 228800 | 0 | 164256.5163 | 197.1476 | 0
1898 | 3 | 0 | 0 | 0.13732 | 5.6163 | 0 | 0 | 0 | 0 | 5.6163 | 0 | 228800 | 0 | 164256.5163 | 202.0158 | 0
1899 | 3 | 0 | 0 | 0.098488 | 4.0282 | 0 | 0 | 0 | 0 | 4.0282 | 0 | 228800 | 0 | 164256.5163 | 205.5074 | 0
1900 | 3 | 0 | 0 | 0.17449 | 7.1367 | 0 | 0 | 0 | 0 | 7.1367 | 0 | 228800 | 0 | 164256.5163 | 211.6935 | 0
1901 | 3 | 0 | 0 | 0.15372 | 6.2872 | 0 | 0 | 0 | 0 | 6.2872 | 0 | 228800 | 0 | 164256.5163 | 217.1432 | 0
1902 | 3 | 0 | 0 | 0.17708 | 7.2424 | 0 | 0 | 0 | 0 | 7.2424 | 0 | 228800 | 0 | 164256.5163 | 223.4209 | 0
1903 | 3 | 0 | 0 | 0.22329 | 9.1325 | 0 | 0 | 0 | 0 | 9.1325 | 0 | 228800 | 0 | 164256.5163 | 231.3369 | 0
1904 | 3 | 1 | 0.20867 | 0.23197 | 69.7517 | 200 | 69.7517 | 130.2483 | 200 | 0 | 0 | 228600 | 200 | 164456.5163 | 101.0886 | 0
1905 | 3 | 1 | 0.5076 | 0.13885 | 152.2752 | 200 | 152.2752 | 47.7248 | 200 | 0 | 0 | 228400 | 200 | 164656.5163 | 53.3638 | 0
1906 | 3 | 0 | 0.81044 | 0.10243 | 238.2447 | 0 | 0 | 0 | 0 | 180 | 58.2447 | 228400 | 58.2447 | 164714.761 | 209.3878 | 0
1907 | 3 | 0 | 1 | 0.11435 | 293.4771 | 0 | 0 | 0 | 0 | 180 | 113.4771 | 228400 | 113.4771 | 164828.2381 | 365.4118 | 0
1908 | 3 | 0 | 1 | 0.17926 | 296.1318 | 0 | 0 | 0 | 0 | 167.7414 | 128.3904 | 228400 | 128.3904 | 164956.6285 | 510.81 | 0
1909 | 3 | 0 | 1 | 0.2344 | 298.387 | 0 | 0 | 0 | 0 | 0 | 200 | 228400 | 200 | 165156.6285 | 510.81 | 98.387
1910 | 3 | 0 | 1 | 0.19527 | 296.7864 | 0 | 0 | 0 | 0 | 0 | 200 | 228400 | 200 | 165356.6285 | 510.81 | 96.7864
1911 | 3 | 0 | 1 | 0.19331 | 296.7063 | 0 | 0 | 0 | 0 | 0 | 200 | 228400 | 200 | 165556.6285 | 510.81 | 96.7063
1912 | 3 | 0 | 0.81044 | 0.17324 | 241.1404 | 0 | 0 | 0 | 0 | 0 | 200 | 228400 | 200 | 165756.6285 | 510.81 | 41.1404
1913 | 3 | 0 | 0.5076 | 0.1386 | 152.2651 | 0 | 0 | 0 | 0 | 0 | 152.2651 | 228400 | 152.2651 | 165908.8936 | 510.81 | 0
1914 | 3 | 0 | 0.20867 | 0.12385 | 65.3292 | 0 | 0 | 0 | 0 | 0 | 65.3292 | 228400 | 65.3292 | 165974.2229 | 510.81 | 0
1915 | 3 | 0 | 0 | 0.16959 | 6.9363 | 0 | 0 | 0 | 0 | 0 | 6.9363 | 228400 | 6.9363 | 165981.1592 | 510.81 | 0
1916 | 3 | 1 | 0 | 0.1944 | 7.9508 | 200 | 7.9508 | 180 | 187.9508 | 0 | 0 | 228200 | 187.9508 | 166169.1099 | 330.81 | 0
1917 | 3 | 1 | 0 | 0.17321 | 7.0841 | 200 | 7.0841 | 180 | 187.0841 | 0 | 0 | 228000 | 187.0841 | 166356.194 | 150.81 | 0
1918 | 3 | 0 | 0 | 0.28881 | 11.8124 | 0 | 0 | 0 | 0 | 11.8124 | 0 | 228000 | 0 | 166356.194 | 161.049 | 0
1919 | 3 | 0 | 0 | 0.35596 | 14.559 | 0 | 0 | 0 | 0 | 14.559 | 0 | 228000 | 0 | 166356.194 | 173.6687 | 0
1920 | 3 | 0 | 0 | 0.27635 | 11.3027 | 0 | 0 | 0 | 0 | 11.3027 | 0 | 228000 | 0 | 166356.194 | 183.4658 | 0
1921 | 3 | 0 | 0 | 0.31442 | 12.8599 | 0 | 0 | 0 | 0 | 12.8599 | 0 | 228000 | 0 | 166356.194 | 194.6128 | 0
1922 | 3 | 0 | 0 | 0.32694 | 13.3717 | 0 | 0 | 0 | 0 | 13.3717 | 0 | 228000 | 0 | 166356.194 | 206.2034 | 0
1923 | 3 | 0 | 0 | 0.36971 | 15.1211 | 0 | 0 | 0 | 0 | 15.1211 | 0 | 228000 | 0 | 166356.194 | 219.3104 | 0
1924 | 3 | 0 | 0 | 0.2864 | 11.7138 | 0 | 0 | 0 | 0 | 11.7138 | 0 | 228000 | 0 | 166356.194 | 229.4639 | 0
1925 | 3 | 0 | 0 | 0.37472 | 15.3261 | 0 | 0 | 0 | 0 | 15.3261 | 0 | 228000 | 0 | 166356.194 | 242.7486 | 0
1926 | 3 | 0 | 0 | 0.44225 | 18.0881 | 0 | 0 | 0 | 0 | 18.0881 | 0 | 228000 | 0 | 166356.194 | 258.4274 | 0
1927 | 3 | 0 | 0 | 0.59447 | 24.3137 | 0 | 0 | 0 | 0 | 24.3137 | 0 | 228000 | 0 | 166356.194 | 279.5025 | 0
1928 | 3 | 1 | 0.24835 | 0.4052 | 88.2954 | 200 | 88.2954 | 111.7046 | 200 | 0 | 0 | 227800 | 200 | 166556.194 | 167.7979 | 0
1929 | 3 | 1 | 0.60412 | 0.40005 | 190.833 | 200 | 190.833 | 9.167 | 200 | 0 | 0 | 227600 | 200 | 166756.194 | 158.6309 | 0
1930 | 3 | 0 | 0.96454 | 0.40404 | 295.0851 | 0 | 0 | 0 | 0 | 180 | 115.0851 | 227600 | 115.0851 | 166871.2791 | 314.6549 | 0
1931 | 3 | 0 | 1 | 0.36874 | 303.8817 | 0 | 0 | 0 | 0 | 180 | 123.8817 | 227600 | 123.8817 | 166995.1608 | 470.6789 | 0
1932 | 3 | 0 | 1 | 0.39438 | 304.9301 | 0 | 0 | 0 | 0 | 46.298 | 200 | 227600 | 200 | 167195.1608 | 510.81 | 58.6321
1933 | 3 | 0 | 1 | 0.52443 | 310.2491 | 0 | 0 | 0 | 0 | 0 | 200 | 227600 | 200 | 167395.1608 | 510.81 | 110.2491
1934 | 3 | 0 | 1 | 0.53429 | 310.6527 | 0 | 0 | 0 | 0 | 0 | 200 | 227600 | 200 | 167595.1608 | 510.81 | 110.6527
1935 | 3 | 0 | 1 | 0.53011 | 310.4814 | 0 | 0 | 0 | 0 | 0 | 200 | 227600 | 200 | 167795.1608 | 510.81 | 110.4814
1936 | 3 | 0 | 0.96454 | 0.50591 | 299.2514 | 0 | 0 | 0 | 0 | 0 | 200 | 227600 | 200 | 167995.1608 | 510.81 | 99.2514
1937 | 3 | 0 | 0.60412 | 0.46884 | 193.6465 | 0 | 0 | 0 | 0 | 0 | 193.6465 | 227600 | 193.6465 | 168188.8073 | 510.81 | 0
1938 | 3 | 0 | 0.24835 | 0.3904 | 87.6904 | 0 | 0 | 0 | 0 | 0 | 87.6904 | 227600 | 87.6904 | 168276.4977 | 510.81 | 0
1939 | 3 | 0 | 0 | 0.28625 | 11.7077 | 0 | 0 | 0 | 0 | 0 | 11.7077 | 227600 | 11.7077 | 168288.2054 | 510.81 | 0
1940 | 3 | 1 | 0 | 0.22162 | 9.0642 | 200 | 9.0642 | 180 | 189.0642 | 0 | 0 | 227400 | 189.0642 | 168477.2695 | 330.81 | 0
1941 | 3 | 1 | 0 | 0.18378 | 7.5164 | 200 | 7.5164 | 180 | 187.5164 | 0 | 0 | 227200 | 187.5164 | 168664.786 | 150.81 | 0
1942 | 3 | 0 | 0 | 0.15616 | 6.3869 | 0 | 0 | 0 | 0 | 6.3869 | 0 | 227200 | 0 | 168664.786 | 156.3462 | 0
1943 | 3 | 0 | 0 | 0.29052 | 11.8822 | 0 | 0 | 0 | 0 | 11.8822 | 0 | 227200 | 0 | 168664.786 | 166.6456 | 0
1944 | 3 | 0 | 0 | 0.31553 | 12.9051 | 0 | 0 | 0 | 0 | 12.9051 | 0 | 227200 | 0 | 168664.786 | 177.8318 | 0
1945 | 3 | 0 | 0 | 0.34879 | 14.2656 | 0 | 0 | 0 | 0 | 14.2656 | 0 | 227200 | 0 | 168664.786 | 190.1973 | 0
1946 | 3 | 0 | 0 | 0.29901 | 12.2297 | 0 | 0 | 0 | 0 | 12.2297 | 0 | 227200 | 0 | 168664.786 | 200.798 | 0
1947 | 3 | 0 | 0 | 0.22584 | 9.2367 | 0 | 0 | 0 | 0 | 9.2367 | 0 | 227200 | 0 | 168664.786 | 208.8044 | 0
1948 | 3 | 0 | 0 | 0.2631 | 10.7607 | 0 | 0 | 0 | 0 | 10.7607 | 0 | 227200 | 0 | 168664.786 | 218.1318 | 0
1949 | 3 | 0 | 0 | 0.34993 | 14.3121 | 0 | 0 | 0 | 0 | 14.3121 | 0 | 227200 | 0 | 168664.786 | 230.5375 | 0
1950 | 3 | 0 | 0 | 0.32238 | 13.1854 | 0 | 0 | 0 | 0 | 13.1854 | 0 | 227200 | 0 | 168664.786 | 241.9666 | 0
1951 | 3 | 0 | 0 | 0.24586 | 10.0558 | 0 | 0 | 0 | 0 | 10.0558 | 0 | 227200 | 0 | 168664.786 | 250.6829 | 0
1952 | 3 | 1 | 0.21486 | 0.29076 | 73.9429 | 200 | 73.9429 | 126.0571 | 200 | 0 | 0 | 227000 | 200 | 168864.786 | 124.6259 | 0
1953 | 3 | 1 | 0.52265 | 0.2633 | 161.711 | 200 | 161.711 | 38.289 | 200 | 0 | 0 | 226800 | 200 | 169064.786 | 86.3368 | 0
1954 | 3 | 0 | 0.83447 | 0.33006 | 254.4934 | 0 | 0 | 0 | 0 | 180 | 74.4934 | 226800 | 74.4934 | 169139.2793 | 242.3608 | 0
1955 | 3 | 0 | 1 | 0.35089 | 303.1516 | 0 | 0 | 0 | 0 | 180 | 123.1516 | 226800 | 123.1516 | 169262.4309 | 398.3848 | 0
1956 | 3 | 0 | 1 | 0.37191 | 304.011 | 0 | 0 | 0 | 0 | 129.7014 | 174.3096 | 226800 | 174.3096 | 169436.7405 | 510.81 | 0
1957 | 3 | 0 | 1 | 0.50626 | 309.506 | 0 | 0 | 0 | 0 | 0 | 200 | 226800 | 200 | 169636.7405 | 510.81 | 109.506
1958 | 3 | 0 | 1 | 0.49241 | 308.9397 | 0 | 0 | 0 | 0 | 0 | 200 | 226800 | 200 | 169836.7405 | 510.81 | 108.9397
1959 | 3 | 0 | 1 | 0.37351 | 304.0766 | 0 | 0 | 0 | 0 | 0 | 200 | 226800 | 200 | 170036.7405 | 510.81 | 104.0766
1960 | 3 | 0 | 0.83447 | 0.38699 | 256.8215 | 0 | 0 | 0 | 0 | 0 | 200 | 226800 | 200 | 170236.7405 | 510.81 | 56.8215
1961 | 3 | 0 | 0.52265 | 0.26205 | 161.6599 | 0 | 0 | 0 | 0 | 0 | 161.6599 | 226800 | 161.6599 | 170398.4004 | 510.81 | 0
1962 | 3 | 0 | 0.21486 | 0.27435 | 73.2715 | 0 | 0 | 0 | 0 | 0 | 73.2715 | 226800 | 73.2715 | 170471.6718 | 510.81 | 0
1963 | 3 | 0 | 0 | 0.30618 | 12.5227 | 0 | 0 | 0 | 0 | 0 | 12.5227 | 226800 | 12.5227 | 170484.1946 | 510.81 | 0
1964 | 3 | 1 | 0 | 0.23313 | 9.5351 | 200 | 9.5351 | 180 | 189.5351 | 0 | 0 | 226600 | 189.5351 | 170673.7297 | 330.81 | 0
1965 | 3 | 1 | 0 | 0.23161 | 9.473 | 200 | 9.473 | 180 | 189.473 | 0 | 0 | 226400 | 189.473 | 170863.2027 | 150.81 | 0
1966 | 3 | 0 | 0 | 0.25252 | 10.3281 | 0 | 0 | 0 | 0 | 10.3281 | 0 | 226400 | 0 | 170863.2027 | 159.7624 | 0
1967 | 3 | 0 | 0 | 0.24882 | 10.1768 | 0 | 0 | 0 | 0 | 10.1768 | 0 | 226400 | 0 | 170863.2027 | 168.5836 | 0
1968 | 3 | 0 | 0 | 0.21914 | 8.9629 | 0 | 0 | 0 | 0 | 8.9629 | 0 | 226400 | 0 | 170863.2027 | 176.3527 | 0
1969 | 3 | 0 | 0 | 0.24378 | 9.9704 | 0 | 0 | 0 | 0 | 9.9704 | 0 | 226400 | 0 | 170863.2027 | 184.9951 | 0
1970 | 3 | 0 | 0 | 0.39048 | 15.9707 | 0 | 0 | 0 | 0 | 15.9707 | 0 | 226400 | 0 | 170863.2027 | 198.8385 | 0
1971 | 3 | 0 | 0 | 0.33702 | 13.784 | 0 | 0 | 0 | 0 | 13.784 | 0 | 226400 | 0 | 170863.2027 | 210.7865 | 0
1972 | 3 | 0 | 0 | 0.43914 | 17.9609 | 0 | 0 | 0 | 0 | 17.9609 | 0 | 226400 | 0 | 170863.2027 | 226.3551 | 0
1973 | 3 | 0 | 0 | 0.65643 | 26.8479 | 0 | 0 | 0 | 0 | 26.8479 | 0 | 226400 | 0 | 170863.2027 | 249.6268 | 0
1974 | 3 | 0 | 0 | 0.95657 | 39.1239 | 0 | 0 | 0 | 0 | 39.1239 | 0 | 226400 | 0 | 170863.2027 | 283.5394 | 0
1975 | 3 | 0 | 0 | 0.9783 | 40.0123 | 0 | 0 | 0 | 0 | 40.0123 | 0 | 226400 | 0 | 170863.2027 | 318.2221 | 0
1976 | 3 | 1 | 0.22521 | 1 | 105.9398 | 200 | 105.9398 | 94.0602 | 200 | 0 | 0 | 226200 | 200 | 171063.2027 | 224.1619 | 0
1977 | 3 | 1 | 0.54783 | 1 | 199.1136 | 200 | 199.1136 | 0.88641 | 200 | 0 | 0 | 226000 | 200 | 171263.2027 | 223.2754 | 0
1978 | 3 | 0 | 0.87467 | 1 | 293.5033 | 0 | 0 | 0 | 0 | 180 | 113.5033 | 226000 | 113.5033 | 171376.706 | 379.2994 | 0
1979 | 3 | 0 | 1 | 0.89013 | 325.2062 | 0 | 0 | 0 | 0 | 151.7196 | 173.4866 | 226000 | 173.4866 | 171550.1926 | 510.81 | 0
1980 | 3 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 0 | 200 | 226000 | 200 | 171750.1926 | 510.81 | 129.7
1981 | 3 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 0 | 200 | 226000 | 200 | 171950.1926 | 510.81 | 129.7
1982 | 3 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 0 | 200 | 226000 | 200 | 172150.1926 | 510.81 | 129.7
1983 | 3 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 0 | 200 | 226000 | 200 | 172350.1926 | 510.81 | 129.7
1984 | 3 | 0 | 0.87467 | 1 | 293.5033 | 0 | 0 | 0 | 0 | 0 | 200 | 226000 | 200 | 172550.1926 | 510.81 | 93.5033
1985 | 3 | 0 | 0.54783 | 0.89283 | 194.7305 | 0 | 0 | 0 | 0 | 0 | 194.7305 | 226000 | 194.7305 | 172744.9231 | 510.81 | 0
1986 | 3 | 0 | 0.22521 | 1 | 105.9398 | 0 | 0 | 0 | 0 | 0 | 105.9398 | 226000 | 105.9398 | 172850.8628 | 510.81 | 0
1987 | 3 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 0 | 40.9 | 226000 | 40.9 | 172891.7628 | 510.81 | 0
1988 | 3 | 1 | 0 | 1 | 40.9 | 200 | 40.9 | 159.1 | 200 | 0 | 0 | 225800 | 200 | 173091.7628 | 351.71 | 0
1989 | 3 | 1 | 0 | 1 | 40.9 | 200 | 40.9 | 159.1 | 200 | 0 | 0 | 225600 | 200 | 173291.7628 | 192.61 | 0
1990 | 3 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 225600 | 0 | 173291.7628 | 228.0621 | 0
1991 | 3 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 225600 | 0 | 173291.7628 | 263.5142 | 0
1992 | 3 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 225600 | 0 | 173291.7628 | 298.9664 | 0
1993 | 3 | 0 | 0 | 0.64607 | 26.4245 | 0 | 0 | 0 | 0 | 26.4245 | 0 | 225600 | 0 | 173291.7628 | 321.8711 | 0
1994 | 3 | 0 | 0 | 0.42672 | 17.4527 | 0 | 0 | 0 | 0 | 17.4527 | 0 | 225600 | 0 | 173291.7628 | 336.9991 | 0
1995 | 3 | 0 | 0 | 0.60771 | 24.8551 | 0 | 0 | 0 | 0 | 24.8551 | 0 | 225600 | 0 | 173291.7628 | 358.5435 | 0
1996 | 3 | 0 | 0 | 0.70173 | 28.7008 | 0 | 0 | 0 | 0 | 28.7008 | 0 | 225600 | 0 | 173291.7628 | 383.4214 | 0
1997 | 3 | 0 | 0 | 0.37033 | 15.1463 | 0 | 0 | 0 | 0 | 15.1463 | 0 | 225600 | 0 | 173291.7628 | 396.5502 | 0
1998 | 3 | 0 | 0 | 0.40624 | 16.6153 | 0 | 0 | 0 | 0 | 16.6153 | 0 | 225600 | 0 | 173291.7628 | 410.9524 | 0
1999 | 3 | 0 | 0 | 0.66215 | 27.0819 | 0 | 0 | 0 | 0 | 27.0819 | 0 | 225600 | 0 | 173291.7628 | 434.427 | 0
2000 | 3 | 1 | 0.23004 | 0.44523 | 84.6452 | 200 | 84.6452 | 115.3548 | 200 | 0 | 0 | 225400 | 200 | 173491.7628 | 319.0722 | 0
2001 | 3 | 1 | 0.55959 | 0.38783 | 177.4708 | 200 | 177.4708 | 22.5292 | 200 | 0 | 0 | 225200 | 200 | 173691.7628 | 296.5429 | 0
2002 | 3 | 0 | 0.89343 | 0.4134 | 274.9315 | 0 | 0 | 0 | 0 | 180 | 94.9315 | 225200 | 94.9315 | 173786.6943 | 452.5669 | 0
2003 | 3 | 0 | 1 | 0.36276 | 303.6369 | 0 | 0 | 0 | 0 | 67.1932 | 200 | 225200 | 200 | 173986.6943 | 510.81 | 36.4437
2004 | 3 | 0 | 1 | 0.37719 | 304.227 | 0 | 0 | 0 | 0 | 0 | 200 | 225200 | 200 | 174186.6943 | 510.81 | 104.227
2005 | 3 | 0 | 1 | 0.32985 | 302.291 | 0 | 0 | 0 | 0 | 0 | 200 | 225200 | 200 | 174386.6943 | 510.81 | 102.291
2006 | 3 | 0 | 1 | 0.33039 | 302.3131 | 0 | 0 | 0 | 0 | 0 | 200 | 225200 | 200 | 174586.6943 | 510.81 | 102.3131
2007 | 3 | 0 | 1 | 0.43822 | 306.7234 | 0 | 0 | 0 | 0 | 0 | 200 | 225200 | 200 | 174786.6943 | 510.81 | 106.7234
2008 | 3 | 0 | 0.89343 | 0.36297 | 272.869 | 0 | 0 | 0 | 0 | 0 | 200 | 225200 | 200 | 174986.6943 | 510.81 | 72.869
2009 | 3 | 0 | 0.55959 | 0.32406 | 174.8624 | 0 | 0 | 0 | 0 | 0 | 174.8624 | 225200 | 174.8624 | 175161.5568 | 510.81 | 0
2010 | 3 | 0 | 0.23004 | 0.38521 | 82.1904 | 0 | 0 | 0 | 0 | 0 | 82.1904 | 225200 | 82.1904 | 175243.7471 | 510.81 | 0
2011 | 3 | 0 | 0 | 0.24227 | 9.9088 | 0 | 0 | 0 | 0 | 0 | 9.9088 | 225200 | 9.9088 | 175253.6559 | 510.81 | 0
2012 | 3 | 1 | 0 | 0.20947 | 8.5671 | 200 | 8.5671 | 180 | 188.5671 | 0 | 0 | 225000 | 188.5671 | 175442.223 | 330.81 | 0
2013 | 3 | 1 | 0 | 0.17214 | 7.0404 | 200 | 7.0404 | 180 | 187.0404 | 0 | 0 | 224800 | 187.0404 | 175629.2634 | 150.81 | 0
2014 | 3 | 0 | 0 | 0.14115 | 5.7729 | 0 | 0 | 0 | 0 | 5.7729 | 0 | 224800 | 0 | 175629.2634 | 155.8139 | 0
2015 | 3 | 0 | 0 | 0.1556 | 6.3642 | 0 | 0 | 0 | 0 | 6.3642 | 0 | 224800 | 0 | 175629.2634 | 161.3304 | 0
2016 | 3 | 0 | 0 | 0.16406 | 6.7098 | 0 | 0 | 0 | 0 | 6.7098 | 0 | 224800 | 0 | 175629.2634 | 167.1465 | 0
2017 | 3 | 0 | 0 | 0.13424 | 5.4905 | 0 | 0 | 0 | 0 | 5.4905 | 0 | 224800 | 0 | 175629.2634 | 171.9057 | 0
2018 | 3 | 0 | 0 | 0.13464 | 5.5069 | 0 | 0 | 0 | 0 | 5.5069 | 0 | 224800 | 0 | 175629.2634 | 176.6791 | 0
2019 | 3 | 0 | 0 | 0.14943 | 6.1118 | 0 | 0 | 0 | 0 | 6.1118 | 0 | 224800 | 0 | 175629.2634 | 181.9768 | 0
2020 | 3 | 0 | 0 | 0.13308 | 5.4431 | 0 | 0 | 0 | 0 | 5.4431 | 0 | 224800 | 0 | 175629.2634 | 186.6948 | 0
2021 | 3 | 0 | 0 | 0.12407 | 5.0746 | 0 | 0 | 0 | 0 | 5.0746 | 0 | 224800 | 0 | 175629.2634 | 191.0935 | 0
2022 | 3 | 0 | 0 | 0.11571 | 4.7325 | 0 | 0 | 0 | 0 | 4.7325 | 0 | 224800 | 0 | 175629.2634 | 195.1956 | 0
2023 | 3 | 0 | 0 | 0.10368 | 4.2406 | 0 | 0 | 0 | 0 | 4.2406 | 0 | 224800 | 0 | 175629.2634 | 198.8714 | 0
2024 | 3 | 1 | 0.22697 | 0.12241 | 70.5554 | 200 | 70.5554 | 129.4446 | 200 | 0 | 0 | 224600 | 200 | 175829.2634 | 69.4268 | 0
2025 | 3 | 1 | 0.55212 | 0.15209 | 165.6723 | 200 | 165.6723 | 34.3277 | 200 | 0 | 0 | 224400 | 200 | 176029.2634 | 35.0991 | 0
2026 | 3 | 0 | 0.88151 | 0.17822 | 261.8694 | 0 | 0 | 0 | 0 | 180 | 81.8694 | 224400 | 81.8694 | 176111.1329 | 191.1231 | 0
2027 | 3 | 0 | 1 | 0.20078 | 297.0117 | 0 | 0 | 0 | 0 | 180 | 117.0117 | 224400 | 117.0117 | 176228.1445 | 347.1471 | 0
2028 | 3 | 0 | 1 | 0.25179 | 299.0981 | 0 | 0 | 0 | 0 | 180 | 119.0981 | 224400 | 119.0981 | 176347.2427 | 503.1711 | 0
2029 | 3 | 0 | 1 | 0.22013 | 297.8032 | 0 | 0 | 0 | 0 | 8.8127 | 200 | 224400 | 200 | 176547.2427 | 510.81 | 88.9905
2030 | 3 | 0 | 1 | 0.26362 | 299.5819 | 0 | 0 | 0 | 0 | 0 | 200 | 224400 | 200 | 176747.2427 | 510.81 | 99.5819
2031 | 3 | 0 | 1 | 0.16543 | 295.566 | 0 | 0 | 0 | 0 | 0 | 200 | 224400 | 200 | 176947.2427 | 510.81 | 95.566
2032 | 3 | 0 | 0.88151 | 0.16281 | 261.2392 | 0 | 0 | 0 | 0 | 0 | 200 | 224400 | 200 | 177147.2427 | 510.81 | 61.2392
2033 | 3 | 0 | 0.55212 | 0.14836 | 165.5196 | 0 | 0 | 0 | 0 | 0 | 165.5196 | 224400 | 165.5196 | 177312.7623 | 510.81 | 0
2034 | 3 | 0 | 0.22697 | 0.1282 | 70.7921 | 0 | 0 | 0 | 0 | 0 | 70.7921 | 224400 | 70.7921 | 177383.5544 | 510.81 | 0
2035 | 3 | 0 | 0 | 0.15008 | 6.1384 | 0 | 0 | 0 | 0 | 0 | 6.1384 | 224400 | 6.1384 | 177389.6928 | 510.81 | 0
2036 | 3 | 1 | 0 | 0.1116 | 4.5643 | 200 | 4.5643 | 180 | 184.5643 | 0 | 0 | 224200 | 184.5643 | 177574.2571 | 330.81 | 0
2037 | 3 | 1 | 0 | 0.086933 | 3.5556 | 200 | 3.5556 | 180 | 183.5556 | 0 | 0 | 224000 | 183.5556 | 177757.8127 | 150.81 | 0
2038 | 3 | 0 | 0 | 0.065836 | 2.6927 | 0 | 0 | 0 | 0 | 2.6927 | 0 | 224000 | 0 | 177757.8127 | 153.144 | 0
2039 | 3 | 0 | 0 | 0.071503 | 2.9245 | 0 | 0 | 0 | 0 | 2.9245 | 0 | 224000 | 0 | 177757.8127 | 155.679 | 0
2040 | 3 | 0 | 0 | 0.0942 | 3.8528 | 0 | 0 | 0 | 0 | 3.8528 | 0 | 224000 | 0 | 177757.8127 | 159.0185 | 0
2041 | 3 | 0 | 0 | 0.094114 | 3.8493 | 0 | 0 | 0 | 0 | 3.8493 | 0 | 224000 | 0 | 177757.8127 | 162.3551 | 0
2042 | 3 | 0 | 0 | 0.11056 | 4.5219 | 0 | 0 | 0 | 0 | 4.5219 | 0 | 224000 | 0 | 177757.8127 | 166.2747 | 0
2043 | 3 | 0 | 0 | 0.1811 | 7.407 | 0 | 0 | 0 | 0 | 7.407 | 0 | 224000 | 0 | 177757.8127 | 172.6951 | 0
2044 | 3 | 0 | 0 | 0.18467 | 7.5531 | 0 | 0 | 0 | 0 | 7.5531 | 0 | 224000 | 0 | 177757.8127 | 179.2421 | 0
2045 | 3 | 0 | 0 | 0.14886 | 6.0884 | 0 | 0 | 0 | 0 | 6.0884 | 0 | 224000 | 0 | 177757.8127 | 184.5195 | 0
2046 | 3 | 0 | 0 | 0.22068 | 9.026 | 0 | 0 | 0 | 0 | 9.026 | 0 | 224000 | 0 | 177757.8127 | 192.3432 | 0
2047 | 3 | 0 | 0 | 0.25238 | 10.3222 | 0 | 0 | 0 | 0 | 10.3222 | 0 | 224000 | 0 | 177757.8127 | 201.2905 | 0
2048 | 3 | 1 | 0.24061 | 0.24502 | 79.5083 | 200 | 79.5083 | 120.4917 | 200 | 0 | 0 | 223800 | 200 | 177957.8127 | 80.7988 | 0
2049 | 3 | 1 | 0.58529 | 0.22587 | 178.2696 | 200 | 178.2696 | 21.7304 | 200 | 0 | 0 | 223600 | 200 | 178157.8127 | 59.0684 | 0
2050 | 3 | 0 | 0.93447 | 0.21791 | 278.7877 | 0 | 0 | 0 | 0 | 180 | 98.7877 | 223600 | 98.7877 | 178256.6004 | 215.0924 | 0
2051 | 3 | 0 | 1 | 0.16434 | 295.5217 | 0 | 0 | 0 | 0 | 180 | 115.5217 | 223600 | 115.5217 | 178372.1221 | 371.1164 | 0
2052 | 3 | 0 | 1 | 0.27339 | 299.9816 | 0 | 0 | 0 | 0 | 161.1601 | 138.8215 | 223600 | 138.8215 | 178510.9436 | 510.81 | 0
2053 | 3 | 0 | 1 | 0.21805 | 297.7181 | 0 | 0 | 0 | 0 | 0 | 200 | 223600 | 200 | 178710.9436 | 510.81 | 97.7181
2054 | 3 | 0 | 1 | 0.17051 | 295.7737 | 0 | 0 | 0 | 0 | 0 | 200 | 223600 | 200 | 178910.9436 | 510.81 | 95.7737
2055 | 3 | 0 | 1 | 0.18605 | 296.4094 | 0 | 0 | 0 | 0 | 0 | 200 | 223600 | 200 | 179110.9436 | 510.81 | 96.4094
2056 | 3 | 0 | 0.93447 | 0.18896 | 277.6038 | 0 | 0 | 0 | 0 | 0 | 200 | 223600 | 200 | 179310.9436 | 510.81 | 77.6038
2057 | 3 | 0 | 0.58529 | 0.24942 | 179.2332 | 0 | 0 | 0 | 0 | 0 | 179.2332 | 223600 | 179.2332 | 179490.1768 | 510.81 | 0
2058 | 3 | 0 | 0.24061 | 0.40794 | 86.1718 | 0 | 0 | 0 | 0 | 0 | 86.1718 | 223600 | 86.1718 | 179576.3486 | 510.81 | 0
2059 | 3 | 0 | 0 | 0.47466 | 19.4135 | 0 | 0 | 0 | 0 | 0 | 19.4135 | 223600 | 19.4135 | 179595.7621 | 510.81 | 0
2060 | 3 | 1 | 0 | 0.33028 | 13.5084 | 200 | 13.5084 | 180 | 193.5084 | 0 | 0 | 223400 | 193.5084 | 179789.2705 | 330.81 | 0
2061 | 3 | 1 | 0 | 0.35102 | 14.3567 | 200 | 14.3567 | 180 | 194.3567 | 0 | 0 | 223200 | 194.3567 | 179983.6272 | 150.81 | 0
2062 | 3 | 0 | 0 | 0.3189 | 13.0431 | 0 | 0 | 0 | 0 | 13.0431 | 0 | 223200 | 0 | 179983.6272 | 162.1157 | 0
2063 | 3 | 0 | 0 | 0.27646 | 11.3071 | 0 | 0 | 0 | 0 | 11.3071 | 0 | 223200 | 0 | 179983.6272 | 171.9167 | 0
2064 | 3 | 0 | 0 | 0.34666 | 14.1783 | 0 | 0 | 0 | 0 | 14.1783 | 0 | 223200 | 0 | 179983.6272 | 184.2065 | 0
2065 | 3 | 0 | 0 | 0.27524 | 11.2573 | 0 | 0 | 0 | 0 | 11.2573 | 0 | 223200 | 0 | 179983.6272 | 193.9643 | 0
2066 | 3 | 0 | 0 | 0.30532 | 12.4875 | 0 | 0 | 0 | 0 | 12.4875 | 0 | 223200 | 0 | 179983.6272 | 204.7885 | 0
2067 | 3 | 0 | 0 | 0.35759 | 14.6253 | 0 | 0 | 0 | 0 | 14.6253 | 0 | 223200 | 0 | 179983.6272 | 217.4657 | 0
2068 | 3 | 0 | 0 | 0.26198 | 10.7151 | 0 | 0 | 0 | 0 | 10.7151 | 0 | 223200 | 0 | 179983.6272 | 226.7535 | 0
2069 | 3 | 0 | 0 | 0.21238 | 8.6861 | 0 | 0 | 0 | 0 | 8.6861 | 0 | 223200 | 0 | 179983.6272 | 234.2827 | 0
2070 | 3 | 0 | 0 | 0.26655 | 10.9018 | 0 | 0 | 0 | 0 | 10.9018 | 0 | 223200 | 0 | 179983.6272 | 243.7324 | 0
2071 | 3 | 0 | 0 | 0.30843 | 12.6146 | 0 | 0 | 0 | 0 | 12.6146 | 0 | 223200 | 0 | 179983.6272 | 254.6667 | 0
2072 | 3 | 1 | 0.25501 | 0.24739 | 83.7659 | 200 | 83.7659 | 116.2341 | 200 | 0 | 0 | 223000 | 200 | 180183.6272 | 138.4327 | 0
2073 | 3 | 1 | 0.62033 | 0.25899 | 189.7456 | 200 | 189.7456 | 10.2544 | 200 | 0 | 0 | 222800 | 200 | 180383.6272 | 128.1783 | 0
2074 | 3 | 0 | 0.99042 | 0.28373 | 297.6392 | 0 | 0 | 0 | 0 | 180 | 117.6392 | 222800 | 117.6392 | 180501.2663 | 284.2023 | 0
2075 | 3 | 0 | 1 | 0.2824 | 300.3501 | 0 | 0 | 0 | 0 | 180 | 120.3501 | 222800 | 120.3501 | 180621.6164 | 440.2263 | 0
2076 | 3 | 0 | 1 | 0.34299 | 302.8283 | 0 | 0 | 0 | 0 | 81.4302 | 200 | 222800 | 200 | 180821.6164 | 510.81 | 21.3981
2077 | 3 | 0 | 1 | 0.30983 | 301.4721 | 0 | 0 | 0 | 0 | 0 | 200 | 222800 | 200 | 181021.6164 | 510.81 | 101.4721
2078 | 3 | 0 | 1 | 0.22484 | 297.9959 | 0 | 0 | 0 | 0 | 0 | 200 | 222800 | 200 | 181221.6164 | 510.81 | 97.9959
2079 | 3 | 0 | 1 | 0.20673 | 297.2554 | 0 | 0 | 0 | 0 | 0 | 200 | 222800 | 200 | 181421.6164 | 510.81 | 97.2554
2080 | 3 | 0 | 0.99042 | 0.14668 | 292.034 | 0 | 0 | 0 | 0 | 0 | 200 | 222800 | 200 | 181621.6164 | 510.81 | 92.034
2081 | 3 | 0 | 0.62033 | 0.156 | 185.533 | 0 | 0 | 0 | 0 | 0 | 185.533 | 222800 | 185.533 | 181807.1494 | 510.81 | 0
2082 | 3 | 0 | 0.25501 | 0.10219 | 77.8273 | 0 | 0 | 0 | 0 | 0 | 77.8273 | 222800 | 77.8273 | 181884.9767 | 510.81 | 0
2083 | 3 | 0 | 0 | 0.13167 | 5.3854 | 0 | 0 | 0 | 0 | 0 | 5.3854 | 222800 | 5.3854 | 181890.3621 | 510.81 | 0
2084 | 3 | 1 | 0 | 0.15047 | 6.1541 | 200 | 6.1541 | 180 | 186.1541 | 0 | 0 | 222600 | 186.1541 | 182076.5162 | 330.81 | 0
2085 | 3 | 1 | 0 | 0.17132 | 7.0069 | 200 | 7.0069 | 180 | 187.0069 | 0 | 0 | 222400 | 187.0069 | 182263.523 | 150.81 | 0
2086 | 3 | 0 | 0 | 0.21855 | 8.9387 | 0 | 0 | 0 | 0 | 8.9387 | 0 | 222400 | 0 | 182263.523 | 158.5581 | 0
2087 | 3 | 0 | 0 | 0.27581 | 11.2808 | 0 | 0 | 0 | 0 | 11.2808 | 0 | 222400 | 0 | 182263.523 | 168.3362 | 0
2088 | 3 | 0 | 0 | 0.29774 | 12.1774 | 0 | 0 | 0 | 0 | 12.1774 | 0 | 222400 | 0 | 182263.523 | 178.8916 | 0
2089 | 3 | 0 | 0 | 0.20972 | 8.5773 | 0 | 0 | 0 | 0 | 8.5773 | 0 | 222400 | 0 | 182263.523 | 186.3264 | 0
2090 | 3 | 0 | 0 | 0.2239 | 9.1573 | 0 | 0 | 0 | 0 | 9.1573 | 0 | 222400 | 0 | 182263.523 | 194.264 | 0
2091 | 3 | 0 | 0 | 0.20552 | 8.4059 | 0 | 0 | 0 | 0 | 8.4059 | 0 | 222400 | 0 | 182263.523 | 201.5502 | 0
2092 | 3 | 0 | 0 | 0.19232 | 7.8658 | 0 | 0 | 0 | 0 | 7.8658 | 0 | 222400 | 0 | 182263.523 | 208.3683 | 0
2093 | 3 | 0 | 0 | 0.1467 | 5.9999 | 0 | 0 | 0 | 0 | 5.9999 | 0 | 222400 | 0 | 182263.523 | 213.569 | 0
2094 | 3 | 0 | 0 | 0.097232 | 3.9768 | 0 | 0 | 0 | 0 | 3.9768 | 0 | 222400 | 0 | 182263.523 | 217.0161 | 0
2095 | 3 | 0 | 0 | 0.10931 | 4.4709 | 0 | 0 | 0 | 0 | 4.4709 | 0 | 222400 | 0 | 182263.523 | 220.8914 | 0
2096 | 3 | 1 | 0.19404 | 0.16406 | 62.7489 | 200 | 62.7489 | 137.2511 | 200 | 0 | 0 | 222200 | 200 | 182463.523 | 83.6403 | 0
2097 | 3 | 1 | 0.47202 | 0.22108 | 145.3608 | 200 | 145.3608 | 54.6392 | 200 | 0 | 0 | 222000 | 200 | 182663.523 | 29.0012 | 0
2098 | 3 | 0 | 0.75362 | 0.36552 | 232.5958 | 0 | 0 | 0 | 0 | 180 | 52.5958 | 222000 | 52.5958 | 182716.1189 | 185.0252 | 0
2099 | 3 | 0 | 0.99087 | 0.27478 | 297.4009 | 0 | 0 | 0 | 0 | 180 | 117.4009 | 222000 | 117.4009 | 182833.5198 | 341.0492 | 0
2100 | 3 | 0 | 1 | 0.27227 | 299.936 | 0 | 0 | 0 | 0 | 180 | 119.936 | 222000 | 119.936 | 182953.4558 | 497.0732 | 0
2101 | 3 | 0 | 1 | 0.30679 | 301.3478 | 0 | 0 | 0 | 0 | 15.8478 | 200 | 222000 | 200 | 183153.4558 | 510.81 | 85.5
2102 | 3 | 0 | 1 | 0.298 | 300.9881 | 0 | 0 | 0 | 0 | 0 | 200 | 222000 | 200 | 183353.4558 | 510.81 | 100.9881
2103 | 3 | 0 | 0.99087 | 0.26615 | 297.048 | 0 | 0 | 0 | 0 | 0 | 200 | 222000 | 200 | 183553.4558 | 510.81 | 97.048
2104 | 3 | 0 | 0.75362 | 0.34486 | 231.751 | 0 | 0 | 0 | 0 | 0 | 200 | 222000 | 200 | 183753.4558 | 510.81 | 31.751
2105 | 3 | 0 | 0.47202 | 0.49897 | 156.7266 | 0 | 0 | 0 | 0 | 0 | 156.7266 | 222000 | 156.7266 | 183910.1824 | 510.81 | 0
2106 | 3 | 0 | 0.19404 | 0.42541 | 73.4383 | 0 | 0 | 0 | 0 | 0 | 73.4383 | 222000 | 73.4383 | 183983.6207 | 510.81 | 0
2107 | 3 | 0 | 0 | 0.47615 | 19.4744 | 0 | 0 | 0 | 0 | 0 | 19.4744 | 222000 | 19.4744 | 184003.0951 | 510.81 | 0
2108 | 3 | 1 | 0 | 0.48611 | 19.882 | 200 | 19.882 | 180 | 199.882 | 0 | 0 | 221800 | 199.882 | 184202.9771 | 330.81 | 0
2109 | 3 | 1 | 0 | 0.37779 | 15.4514 | 200 | 15.4514 | 180 | 195.4514 | 0 | 0 | 221600 | 195.4514 | 184398.4286 | 150.81 | 0
2110 | 3 | 0 | 0 | 0.29038 | 11.8764 | 0 | 0 | 0 | 0 | 11.8764 | 0 | 221600 | 0 | 184398.4286 | 161.1044 | 0
2111 | 3 | 0 | 0 | 0.34805 | 14.2353 | 0 | 0 | 0 | 0 | 14.2353 | 0 | 221600 | 0 | 184398.4286 | 173.4436 | 0
2112 | 3 | 0 | 0 | 0.38463 | 15.7312 | 0 | 0 | 0 | 0 | 15.7312 | 0 | 221600 | 0 | 184398.4286 | 187.0794 | 0
2113 | 3 | 0 | 0 | 0.36784 | 15.0445 | 0 | 0 | 0 | 0 | 15.0445 | 0 | 221600 | 0 | 184398.4286 | 200.1199 | 0
2114 | 3 | 0 | 0 | 0.41364 | 16.9179 | 0 | 0 | 0 | 0 | 16.9179 | 0 | 221600 | 0 | 184398.4286 | 214.7844 | 0
2115 | 3 | 0 | 0 | 0.40597 | 16.6043 | 0 | 0 | 0 | 0 | 16.6043 | 0 | 221600 | 0 | 184398.4286 | 229.177 | 0
2116 | 3 | 0 | 0 | 0.39049 | 15.9708 | 0 | 0 | 0 | 0 | 15.9708 | 0 | 221600 | 0 | 184398.4286 | 243.0205 | 0
2117 | 3 | 0 | 0 | 0.51719 | 21.153 | 0 | 0 | 0 | 0 | 21.153 | 0 | 221600 | 0 | 184398.4286 | 261.3559 | 0
2118 | 3 | 0 | 0 | 0.90884 | 37.1714 | 0 | 0 | 0 | 0 | 37.1714 | 0 | 221600 | 0 | 184398.4286 | 293.5761 | 0
2119 | 3 | 0 | 0 | 0.50919 | 20.8258 | 0 | 0 | 0 | 0 | 20.8258 | 0 | 221600 | 0 | 184398.4286 | 311.628 | 0
2120 | 3 | 1 | 0.25518 | 0.42665 | 91.1455 | 200 | 91.1455 | 108.8545 | 200 | 0 | 0 | 221400 | 200 | 184598.4286 | 202.7735 | 0
2121 | 3 | 1 | 0.62074 | 0.35441 | 193.7644 | 200 | 193.7644 | 6.2356 | 200 | 0 | 0 | 221200 | 200 | 184798.4286 | 196.5379 | 0
2122 | 3 | 0 | 0.99107 | 0.36102 | 300.9859 | 0 | 0 | 0 | 0 | 180 | 120.9859 | 221200 | 120.9859 | 184919.4145 | 352.5619 | 0
2123 | 3 | 0 | 1 | 0.41452 | 305.7537 | 0 | 0 | 0 | 0 | 180 | 125.7537 | 221200 | 125.7537 | 185045.1683 | 508.5859 | 0
2124 | 3 | 0 | 1 | 0.38228 | 304.4353 | 0 | 0 | 0 | 0 | 2.5659 | 200 | 221200 | 200 | 185245.1683 | 510.81 | 101.8694
2125 | 3 | 0 | 1 | 0.2857 | 300.4853 | 0 | 0 | 0 | 0 | 0 | 200 | 221200 | 200 | 185445.1683 | 510.81 | 100.4853
2126 | 3 | 0 | 1 | 0.41177 | 305.6413 | 0 | 0 | 0 | 0 | 0 | 200 | 221200 | 200 | 185645.1683 | 510.81 | 105.6413
2127 | 3 | 0 | 1 | 0.35548 | 303.3393 | 0 | 0 | 0 | 0 | 0 | 200 | 221200 | 200 | 185845.1683 | 510.81 | 103.3393
2128 | 3 | 0 | 0.99107 | 0.33615 | 299.9686 | 0 | 0 | 0 | 0 | 0 | 200 | 221200 | 200 | 186045.1683 | 510.81 | 99.9686
2129 | 3 | 0 | 0.62074 | 0.54082 | 201.3883 | 0 | 0 | 0 | 0 | 0 | 200 | 221200 | 200 | 186245.1683 | 510.81 | 1.3883
2130 | 3 | 0 | 0.25518 | 0.36211 | 88.5057 | 0 | 0 | 0 | 0 | 0 | 88.5057 | 221200 | 88.5057 | 186333.674 | 510.81 | 0
2131 | 3 | 0 | 0 | 0.32262 | 13.1952 | 0 | 0 | 0 | 0 | 0 | 13.1952 | 221200 | 13.1952 | 186346.8692 | 510.81 | 0
2132 | 3 | 1 | 0 | 0.28565 | 11.6832 | 200 | 11.6832 | 180 | 191.6832 | 0 | 0 | 221000 | 191.6832 | 186538.5525 | 330.81 | 0
2133 | 3 | 1 | 0 | 0.23348 | 9.5493 | 200 | 9.5493 | 180 | 189.5493 | 0 | 0 | 220800 | 189.5493 | 186728.1017 | 150.81 | 0
2134 | 3 | 0 | 0 | 0.20412 | 8.3485 | 0 | 0 | 0 | 0 | 8.3485 | 0 | 220800 | 0 | 186728.1017 | 158.0465 | 0
2135 | 3 | 0 | 0 | 0.2635 | 10.7773 | 0 | 0 | 0 | 0 | 10.7773 | 0 | 220800 | 0 | 186728.1017 | 167.3882 | 0
2136 | 3 | 0 | 0 | 0.24223 | 9.9072 | 0 | 0 | 0 | 0 | 9.9072 | 0 | 220800 | 0 | 186728.1017 | 175.9758 | 0
2137 | 3 | 0 | 0 | 0.3052 | 12.4827 | 0 | 0 | 0 | 0 | 12.4827 | 0 | 220800 | 0 | 186728.1017 | 186.7958 | 0
2138 | 3 | 0 | 0 | 0.24876 | 10.1743 | 0 | 0 | 0 | 0 | 10.1743 | 0 | 220800 | 0 | 186728.1017 | 195.6149 | 0
2139 | 3 | 0 | 0 | 0.3486 | 14.2578 | 0 | 0 | 0 | 0 | 14.2578 | 0 | 220800 | 0 | 186728.1017 | 207.9736 | 0
2140 | 3 | 0 | 0 | 0.42081 | 17.2111 | 0 | 0 | 0 | 0 | 17.2111 | 0 | 220800 | 0 | 186728.1017 | 222.8922 | 0
2141 | 3 | 0 | 0 | 0.55506 | 22.702 | 0 | 0 | 0 | 0 | 22.702 | 0 | 220800 | 0 | 186728.1017 | 242.5703 | 0
2142 | 3 | 0 | 0 | 0.38812 | 15.8741 | 0 | 0 | 0 | 0 | 15.8741 | 0 | 220800 | 0 | 186728.1017 | 256.33 | 0
2143 | 3 | 0 | 0 | 0.51375 | 21.0124 | 0 | 0 | 0 | 0 | 21.0124 | 0 | 220800 | 0 | 186728.1017 | 274.5436 | 0
2144 | 3 | 1 | 0.24094 | 0.26456 | 80.4025 | 200 | 80.4025 | 119.5975 | 200 | 0 | 0 | 220600 | 200 | 186928.1017 | 154.9461 | 0
2145 | 3 | 1 | 0.58609 | 0.16906 | 176.1776 | 200 | 176.1776 | 23.8224 | 200 | 0 | 0 | 220400 | 200 | 187128.1017 | 131.1236 | 0
2146 | 3 | 0 | 0.93575 | 0.21212 | 278.9201 | 0 | 0 | 0 | 0 | 180 | 98.9201 | 220400 | 98.9201 | 187227.0218 | 287.1476 | 0
2147 | 3 | 0 | 1 | 0.27714 | 300.1351 | 0 | 0 | 0 | 0 | 180 | 120.1351 | 220400 | 120.1351 | 187347.1569 | 443.1716 | 0
2148 | 3 | 0 | 1 | 0.263 | 299.5567 | 0 | 0 | 0 | 0 | 78.0323 | 200 | 220400 | 200 | 187547.1569 | 510.81 | 21.5244
2149 | 3 | 0 | 1 | 0.23302 | 298.3305 | 0 | 0 | 0 | 0 | 0 | 200 | 220400 | 200 | 187747.1569 | 510.81 | 98.3305
2150 | 3 | 0 | 1 | 0.18885 | 296.5239 | 0 | 0 | 0 | 0 | 0 | 200 | 220400 | 200 | 187947.1569 | 510.81 | 96.5239
2151 | 3 | 0 | 1 | 0.19375 | 296.7242 | 0 | 0 | 0 | 0 | 0 | 200 | 220400 | 200 | 188147.1569 | 510.81 | 96.7242
2152 | 3 | 0 | 0.93575 | 0.15366 | 276.529 | 0 | 0 | 0 | 0 | 0 | 200 | 220400 | 200 | 188347.1569 | 510.81 | 76.529
2153 | 3 | 0 | 0.58609 | 0.22494 | 178.4627 | 0 | 0 | 0 | 0 | 0 | 178.4627 | 220400 | 178.4627 | 188525.6196 | 510.81 | 0
2154 | 3 | 0 | 0.24094 | 0.16136 | 76.1817 | 0 | 0 | 0 | 0 | 0 | 76.1817 | 220400 | 76.1817 | 188601.8013 | 510.81 | 0
2155 | 3 | 0 | 0 | 0.15107 | 6.1786 | 0 | 0 | 0 | 0 | 0 | 6.1786 | 220400 | 6.1786 | 188607.9799 | 510.81 | 0
2156 | 3 | 1 | 0 | 0.14771 | 6.0413 | 200 | 6.0413 | 180 | 186.0413 | 0 | 0 | 220200 | 186.0413 | 188794.0213 | 330.81 | 0
2157 | 3 | 1 | 0 | 0.24512 | 10.0253 | 200 | 10.0253 | 180 | 190.0253 | 0 | 0 | 220000 | 190.0253 | 188984.0466 | 150.81 | 0
2158 | 3 | 0 | 0 | 0.28016 | 11.4587 | 0 | 0 | 0 | 0 | 11.4587 | 0 | 220000 | 0 | 188984.0466 | 160.7424 | 0
2159 | 3 | 0 | 0 | 0.23207 | 9.4918 | 0 | 0 | 0 | 0 | 9.4918 | 0 | 220000 | 0 | 188984.0466 | 168.97 | 0
2160 | 3 | 0 | 0 | 0.20991 | 8.5853 | 0 | 0 | 0 | 0 | 8.5853 | 0 | 220000 | 0 | 188984.0466 | 176.4117 | 0
2161 | 4 | 0 | 0 | 0.23991 | 9.8124 | 0 | 0 | 0 | 0 | 9.8124 | 0 | 220000 | 0 | 188984.0466 | 184.9171 | 0
2162 | 4 | 0 | 0 | 0.20888 | 8.5433 | 0 | 0 | 0 | 0 | 8.5433 | 0 | 220000 | 0 | 188984.0466 | 192.3224 | 0
2163 | 4 | 0 | 0 | 0.27134 | 11.0977 | 0 | 0 | 0 | 0 | 11.0977 | 0 | 220000 | 0 | 188984.0466 | 201.9419 | 0
2164 | 4 | 0 | 0 | 0.30941 | 12.655 | 0 | 0 | 0 | 0 | 12.655 | 0 | 220000 | 0 | 188984.0466 | 212.9112 | 0
2165 | 4 | 0 | 0 | 0.31949 | 13.0671 | 0 | 0 | 0 | 0 | 13.0671 | 0 | 220000 | 0 | 188984.0466 | 224.2378 | 0
2166 | 4 | 0 | 0 | 0.43374 | 17.74 | 0 | 0 | 0 | 0 | 17.74 | 0 | 220000 | 0 | 188984.0466 | 239.6149 | 0
2167 | 4 | 0 | 0.059783 | 0.46474 | 36.2733 | 0 | 0 | 0 | 0 | 36.2733 | 0 | 220000 | 0 | 188984.0466 | 271.0565 | 0
2168 | 4 | 1 | 0.36127 | 0.423 | 121.6343 | 200 | 121.6343 | 78.3657 | 200 | 0 | 0 | 219800 | 200 | 189184.0466 | 192.6909 | 0
2169 | 4 | 1 | 0.72503 | 0.29398 | 221.412 | 200 | 200 | 0 | 200 | 21.412 | 0 | 219600 | 200 | 189384.0466 | 211.2508 | 0
2170 | 4 | 0 | 1 | 0.27384 | 300.0001 | 0 | 0 | 0 | 0 | 180 | 120.0001 | 219600 | 120.0001 | 189504.0467 | 367.2748 | 0
2171 | 4 | 0 | 1 | 0.21764 | 297.7016 | 0 | 0 | 0 | 0 | 165.592 | 132.1096 | 219600 | 132.1096 | 189636.1563 | 510.81 | 0
2172 | 4 | 0 | 1 | 0.29546 | 300.8843 | 0 | 0 | 0 | 0 | 0 | 200 | 219600 | 200 | 189836.1563 | 510.81 | 100.8843
2173 | 4 | 0 | 1 | 0.2209 | 297.8348 | 0 | 0 | 0 | 0 | 0 | 200 | 219600 | 200 | 190036.1563 | 510.81 | 97.8348
2174 | 4 | 0 | 1 | 0.34786 | 303.0276 | 0 | 0 | 0 | 0 | 0 | 200 | 219600 | 200 | 190236.1563 | 510.81 | 103.0276
2175 | 4 | 0 | 1 | 0.47665 | 308.2949 | 0 | 0 | 0 | 0 | 0 | 200 | 219600 | 200 | 190436.1563 | 510.81 | 108.2949
2176 | 4 | 0 | 1 | 0.3244 | 302.0678 | 0 | 0 | 0 | 0 | 0 | 200 | 219600 | 200 | 190636.1563 | 510.81 | 102.0678
2177 | 4 | 0 | 0.72503 | 0.33108 | 222.9294 | 0 | 0 | 0 | 0 | 0 | 200 | 219600 | 200 | 190836.1563 | 510.81 | 22.9294
2178 | 4 | 0 | 0.36127 | 0.60986 | 129.277 | 0 | 0 | 0 | 0 | 0 | 129.277 | 219600 | 129.277 | 190965.4332 | 510.81 | 0
2179 | 4 | 0 | 0.059783 | 0.60924 | 42.1833 | 0 | 0 | 0 | 0 | 0 | 42.1833 | 219600 | 42.1833 | 191007.6165 | 510.81 | 0
2180 | 4 | 1 | 0 | 0.80828 | 33.0586 | 200 | 33.0586 | 166.9414 | 200 | 0 | 0 | 219400 | 200 | 191207.6165 | 343.8686 | 0
2181 | 4 | 1 | 0 | 1 | 40.9 | 200 | 40.9 | 159.1 | 200 | 0 | 0 | 219200 | 200 | 191407.6165 | 184.7686 | 0
2182 | 4 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 219200 | 0 | 191407.6165 | 220.2207 | 0
2183 | 4 | 0 | 0 | 0.66257 | 27.099 | 0 | 0 | 0 | 0 | 27.099 | 0 | 219200 | 0 | 191407.6165 | 243.7102 | 0
2184 | 4 | 0 | 0 | 0.56147 | 22.9643 | 0 | 0 | 0 | 0 | 22.9643 | 0 | 219200 | 0 | 191407.6165 | 263.6156 | 0
2185 | 4 | 0 | 0 | 0.74754 | 30.5742 | 0 | 0 | 0 | 0 | 30.5742 | 0 | 219200 | 0 | 191407.6165 | 290.1174 | 0
2186 | 4 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 219200 | 0 | 191407.6165 | 325.5695 | 0
2187 | 4 | 0 | 0 | 0.62319 | 25.4885 | 0 | 0 | 0 | 0 | 25.4885 | 0 | 219200 | 0 | 191407.6165 | 347.6629 | 0
2188 | 4 | 0 | 0 | 0.7107 | 29.0675 | 0 | 0 | 0 | 0 | 29.0675 | 0 | 219200 | 0 | 191407.6165 | 372.8587 | 0
2189 | 4 | 0 | 0 | 0.68902 | 28.181 | 0 | 0 | 0 | 0 | 28.181 | 0 | 219200 | 0 | 191407.6165 | 397.2859 | 0
2190 | 4 | 0 | 0 | 0.48041 | 19.6489 | 0 | 0 | 0 | 0 | 19.6489 | 0 | 219200 | 0 | 191407.6165 | 414.3176 | 0
2191 | 4 | 0 | 0.054534 | 0.62278 | 41.221 | 0 | 0 | 0 | 0 | 41.221 | 0 | 219200 | 0 | 191407.6165 | 450.0479 | 0
2192 | 4 | 1 | 0.32955 | 0.49048 | 115.2348 | 200 | 115.2348 | 84.7652 | 200 | 0 | 0 | 219000 | 200 | 191607.6165 | 365.2828 | 0
2193 | 4 | 1 | 0.66138 | 0.49825 | 211.3845 | 200 | 200 | 0 | 200 | 11.3845 | 0 | 218800 | 200 | 191807.6165 | 375.1508 | 0
2194 | 4 | 0 | 0.98403 | 0.40223 | 300.6395 | 0 | 0 | 0 | 0 | 156.5057 | 144.1338 | 218800 | 144.1338 | 191951.7503 | 510.81 | 0
2195 | 4 | 0 | 1 | 0.39111 | 304.7964 | 0 | 0 | 0 | 0 | 0 | 200 | 218800 | 200 | 192151.7503 | 510.81 | 104.7964
2196 | 4 | 0 | 1 | 0.54404 | 311.0511 | 0 | 0 | 0 | 0 | 0 | 200 | 218800 | 200 | 192351.7503 | 510.81 | 111.0511
2197 | 4 | 0 | 1 | 0.64795 | 315.3012 | 0 | 0 | 0 | 0 | 0 | 200 | 218800 | 200 | 192551.7503 | 510.81 | 115.3012
2198 | 4 | 0 | 1 | 0.43294 | 306.5072 | 0 | 0 | 0 | 0 | 0 | 200 | 218800 | 200 | 192751.7503 | 510.81 | 106.5072
2199 | 4 | 0 | 1 | 0.50711 | 309.541 | 0 | 0 | 0 | 0 | 0 | 200 | 218800 | 200 | 192951.7503 | 510.81 | 109.541
2200 | 4 | 0 | 0.98403 | 0.44815 | 302.5179 | 0 | 0 | 0 | 0 | 0 | 200 | 218800 | 200 | 193151.7503 | 510.81 | 102.5179
2201 | 4 | 0 | 0.66138 | 0.36392 | 205.8903 | 0 | 0 | 0 | 0 | 0 | 200 | 218800 | 200 | 193351.7503 | 510.81 | 5.8903
2202 | 4 | 0 | 0.32955 | 0.32165 | 108.3294 | 0 | 0 | 0 | 0 | 0 | 108.3294 | 218800 | 108.3294 | 193460.0797 | 510.81 | 0
2203 | 4 | 0 | 0.054534 | 0.22001 | 24.7477 | 0 | 0 | 0 | 0 | 0 | 24.7477 | 218800 | 24.7477 | 193484.8274 | 510.81 | 0
2204 | 4 | 1 | 0 | 0.2747 | 11.2354 | 200 | 11.2354 | 180 | 191.2354 | 0 | 0 | 218600 | 191.2354 | 193676.0628 | 330.81 | 0
2205 | 4 | 1 | 0 | 0.26815 | 10.9673 | 200 | 10.9673 | 180 | 190.9673 | 0 | 0 | 218400 | 190.9673 | 193867.0301 | 150.81 | 0
2206 | 4 | 0 | 0 | 0.30551 | 12.4953 | 0 | 0 | 0 | 0 | 12.4953 | 0 | 218400 | 0 | 193867.0301 | 161.6409 | 0
2207 | 4 | 0 | 0 | 0.29357 | 12.0069 | 0 | 0 | 0 | 0 | 12.0069 | 0 | 218400 | 0 | 193867.0301 | 172.0485 | 0
2208 | 4 | 0 | 0 | 0.24844 | 10.1611 | 0 | 0 | 0 | 0 | 10.1611 | 0 | 218400 | 0 | 193867.0301 | 180.8561 | 0
2209 | 4 | 0 | 0 | 0.21569 | 8.8216 | 0 | 0 | 0 | 0 | 8.8216 | 0 | 218400 | 0 | 193867.0301 | 188.5027 | 0
2210 | 4 | 0 | 0 | 0.23514 | 9.6172 | 0 | 0 | 0 | 0 | 9.6172 | 0 | 218400 | 0 | 193867.0301 | 196.8388 | 0
2211 | 4 | 0 | 0 | 0.24353 | 9.9604 | 0 | 0 | 0 | 0 | 9.9604 | 0 | 218400 | 0 | 193867.0301 | 205.4725 | 0
2212 | 4 | 0 | 0 | 0.16248 | 6.6456 | 0 | 0 | 0 | 0 | 6.6456 | 0 | 218400 | 0 | 193867.0301 | 211.2329 | 0
2213 | 4 | 0 | 0 | 0.20703 | 8.4675 | 0 | 0 | 0 | 0 | 8.4675 | 0 | 218400 | 0 | 193867.0301 | 218.5725 | 0
2214 | 4 | 0 | 0 | 0.18025 | 7.3724 | 0 | 0 | 0 | 0 | 7.3724 | 0 | 218400 | 0 | 193867.0301 | 224.9629 | 0
2215 | 4 | 0 | 0.051399 | 0.18573 | 22.4403 | 0 | 0 | 0 | 0 | 22.4403 | 0 | 218400 | 0 | 193867.0301 | 244.4142 | 0
2216 | 4 | 1 | 0.3106 | 0.15611 | 96.0872 | 200 | 96.0872 | 103.9128 | 200 | 0 | 0 | 218200 | 200 | 194067.0301 | 140.5014 | 0
2217 | 4 | 1 | 0.62335 | 0.19929 | 188.1757 | 200 | 188.1757 | 11.8243 | 200 | 0 | 0 | 218000 | 200 | 194267.0301 | 128.6771 | 0
2218 | 4 | 0 | 0.92746 | 0.22104 | 276.8902 | 0 | 0 | 0 | 0 | 180 | 96.8902 | 218000 | 96.8902 | 194363.9203 | 284.7011 | 0
2219 | 4 | 0 | 1 | 0.23146 | 298.2666 | 0 | 0 | 0 | 0 | 180 | 118.2666 | 218000 | 118.2666 | 194482.1869 | 440.7251 | 0
2220 | 4 | 0 | 1 | 0.17787 | 296.075 | 0 | 0 | 0 | 0 | 80.8548 | 200 | 218000 | 200 | 194682.1869 | 510.81 | 15.2203
2221 | 4 | 0 | 1 | 0.18553 | 296.3883 | 0 | 0 | 0 | 0 | 0 | 200 | 218000 | 200 | 194882.1869 | 510.81 | 96.3883
2222 | 4 | 0 | 1 | 0.18156 | 296.2258 | 0 | 0 | 0 | 0 | 0 | 200 | 218000 | 200 | 195082.1869 | 510.81 | 96.2258
2223 | 4 | 0 | 1 | 0.22407 | 297.9644 | 0 | 0 | 0 | 0 | 0 | 200 | 218000 | 200 | 195282.1869 | 510.81 | 97.9644
2224 | 4 | 0 | 0.92746 | 0.26217 | 278.5726 | 0 | 0 | 0 | 0 | 0 | 200 | 218000 | 200 | 195482.1869 | 510.81 | 78.5726
2225 | 4 | 0 | 0.62335 | 0.20149 | 188.2655 | 0 | 0 | 0 | 0 | 0 | 188.2655 | 218000 | 188.2655 | 195670.4524 | 510.81 | 0
2226 | 4 | 0 | 0.3106 | 0.13493 | 95.2213 | 0 | 0 | 0 | 0 | 0 | 95.2213 | 218000 | 95.2213 | 195765.6737 | 510.81 | 0
2227 | 4 | 0 | 0.051399 | 0.12768 | 20.0663 | 0 | 0 | 0 | 0 | 0 | 20.0663 | 218000 | 20.0663 | 195785.74 | 510.81 | 0
2228 | 4 | 1 | 0 | 0.11797 | 4.8248 | 200 | 4.8248 | 180 | 184.8248 | 0 | 0 | 217800 | 184.8248 | 195970.5648 | 330.81 | 0
2229 | 4 | 1 | 0 | 0.079799 | 3.2638 | 200 | 3.2638 | 180 | 183.2638 | 0 | 0 | 217600 | 183.2638 | 196153.8285 | 150.81 | 0
2230 | 4 | 0 | 0 | 0.11543 | 4.7211 | 0 | 0 | 0 | 0 | 4.7211 | 0 | 217600 | 0 | 196153.8285 | 154.9023 | 0
2231 | 4 | 0 | 0 | 0.13499 | 5.5211 | 0 | 0 | 0 | 0 | 5.5211 | 0 | 217600 | 0 | 196153.8285 | 159.688 | 0
2232 | 4 | 0 | 0 | 0.18423 | 7.5352 | 0 | 0 | 0 | 0 | 7.5352 | 0 | 217600 | 0 | 196153.8285 | 166.2194 | 0
2233 | 4 | 0 | 0 | 0.18698 | 7.6476 | 0 | 0 | 0 | 0 | 7.6476 | 0 | 217600 | 0 | 196153.8285 | 172.8483 | 0
2234 | 4 | 0 | 0 | 0.27027 | 11.0542 | 0 | 0 | 0 | 0 | 11.0542 | 0 | 217600 | 0 | 196153.8285 | 182.4301 | 0
2235 | 4 | 0 | 0 | 0.19209 | 7.8565 | 0 | 0 | 0 | 0 | 7.8565 | 0 | 217600 | 0 | 196153.8285 | 189.2402 | 0
2236 | 4 | 0 | 0 | 0.2472 | 10.1104 | 0 | 0 | 0 | 0 | 10.1104 | 0 | 217600 | 0 | 196153.8285 | 198.0038 | 0
2237 | 4 | 0 | 0 | 0.26488 | 10.8334 | 0 | 0 | 0 | 0 | 10.8334 | 0 | 217600 | 0 | 196153.8285 | 207.3942 | 0
2238 | 4 | 0 | 0 | 0.22762 | 9.3097 | 0 | 0 | 0 | 0 | 9.3097 | 0 | 217600 | 0 | 196153.8285 | 215.4639 | 0
2239 | 4 | 0 | 0.063311 | 0.29134 | 30.2 | 0 | 0 | 0 | 0 | 30.2 | 0 | 217600 | 0 | 196153.8285 | 241.6412 | 0
2240 | 4 | 1 | 0.38259 | 0.19988 | 118.6674 | 200 | 118.6674 | 81.3326 | 200 | 0 | 0 | 217400 | 200 | 196353.8285 | 160.3086 | 0
2241 | 4 | 1 | 0.76782 | 0.16171 | 228.3616 | 200 | 200 | 0 | 200 | 28.3616 | 0 | 217200 | 200 | 196553.8285 | 184.8925 | 0
2242 | 4 | 0 | 1 | 0.20926 | 297.3586 | 0 | 0 | 0 | 0 | 180 | 117.3586 | 217200 | 117.3586 | 196671.1872 | 340.9165 | 0
2243 | 4 | 0 | 1 | 0.2306 | 298.2317 | 0 | 0 | 0 | 0 | 180 | 118.2317 | 217200 | 118.2317 | 196789.4189 | 496.9405 | 0
2244 | 4 | 0 | 1 | 0.32762 | 302.1996 | 0 | 0 | 0 | 0 | 16.0008 | 200 | 217200 | 200 | 196989.4189 | 510.81 | 86.1988
2245 | 4 | 0 | 1 | 0.22361 | 297.9456 | 0 | 0 | 0 | 0 | 0 | 200 | 217200 | 200 | 197189.4189 | 510.81 | 97.9456
2246 | 4 | 0 | 1 | 0.32132 | 301.942 | 0 | 0 | 0 | 0 | 0 | 200 | 217200 | 200 | 197389.4189 | 510.81 | 101.942
2247 | 4 | 0 | 1 | 0.29533 | 300.8788 | 0 | 0 | 0 | 0 | 0 | 200 | 217200 | 200 | 197589.4189 | 510.81 | 100.8788
2248 | 4 | 0 | 1 | 0.28864 | 300.6056 | 0 | 0 | 0 | 0 | 0 | 200 | 217200 | 200 | 197789.4189 | 510.81 | 100.6056
2249 | 4 | 0 | 0.76782 | 0.38576 | 237.5254 | 0 | 0 | 0 | 0 | 0 | 200 | 217200 | 200 | 197989.4189 | 510.81 | 37.5254
2250 | 4 | 0 | 0.38259 | 0.41735 | 127.562 | 0 | 0 | 0 | 0 | 0 | 127.562 | 217200 | 127.562 | 198116.9809 | 510.81 | 0
2251 | 4 | 0 | 0.063311 | 0.43914 | 36.2451 | 0 | 0 | 0 | 0 | 0 | 36.2451 | 217200 | 36.2451 | 198153.226 | 510.81 | 0
2252 | 4 | 1 | 0 | 0.51832 | 21.1994 | 200 | 21.1994 | 178.8006 | 200 | 0 | 0 | 217000 | 200 | 198353.226 | 332.0094 | 0
2253 | 4 | 1 | 0 | 0.56998 | 23.312 | 200 | 23.312 | 176.688 | 200 | 0 | 0 | 216800 | 200 | 198553.226 | 155.3214 | 0
2254 | 4 | 0 | 0 | 0.67299 | 27.5253 | 0 | 0 | 0 | 0 | 27.5253 | 0 | 216800 | 0 | 198553.226 | 179.1803 | 0
2255 | 4 | 0 | 0 | 0.63854 | 26.1163 | 0 | 0 | 0 | 0 | 26.1163 | 0 | 216800 | 0 | 198553.226 | 201.8179 | 0
2256 | 4 | 0 | 0 | 0.61422 | 25.1214 | 0 | 0 | 0 | 0 | 25.1214 | 0 | 216800 | 0 | 198553.226 | 223.5932 | 0
2257 | 4 | 0 | 0 | 0.62883 | 25.719 | 0 | 0 | 0 | 0 | 25.719 | 0 | 216800 | 0 | 198553.226 | 245.8864 | 0
2258 | 4 | 0 | 0 | 0.39076 | 15.9823 | 0 | 0 | 0 | 0 | 15.9823 | 0 | 216800 | 0 | 198553.226 | 259.7398 | 0
2259 | 4 | 0 | 0 | 0.45034 | 18.4189 | 0 | 0 | 0 | 0 | 18.4189 | 0 | 216800 | 0 | 198553.226 | 275.7053 | 0
2260 | 4 | 0 | 0 | 0.3934 | 16.0901 | 0 | 0 | 0 | 0 | 16.0901 | 0 | 216800 | 0 | 198553.226 | 289.6522 | 0
2261 | 4 | 0 | 0 | 0.44592 | 18.238 | 0 | 0 | 0 | 0 | 18.238 | 0 | 216800 | 0 | 198553.226 | 305.4609 | 0
2262 | 4 | 0 | 0 | 0.50801 | 20.7775 | 0 | 0 | 0 | 0 | 20.7775 | 0 | 216800 | 0 | 198553.226 | 323.4708 | 0
2263 | 4 | 0 | 0.056729 | 0.44594 | 34.6223 | 0 | 0 | 0 | 0 | 34.6223 | 0 | 216800 | 0 | 198553.226 | 353.4815 | 0
2264 | 4 | 1 | 0.34281 | 0.42288 | 116.3007 | 200 | 116.3007 | 83.6993 | 200 | 0 | 0 | 216600 | 200 | 198753.226 | 269.7821 | 0
2265 | 4 | 1 | 0.688 | 0.31952 | 211.7623 | 200 | 200 | 0 | 200 | 11.7623 | 0 | 216400 | 200 | 198953.226 | 279.9777 | 0
2266 | 4 | 0 | 1 | 0.3923 | 304.8452 | 0 | 0 | 0 | 0 | 180 | 124.8452 | 216400 | 124.8452 | 199078.0712 | 436.0017 | 0
2267 | 4 | 0 | 1 | 0.41325 | 305.7021 | 0 | 0 | 0 | 0 | 86.304 | 200 | 216400 | 200 | 199278.0712 | 510.81 | 19.3982
2268 | 4 | 0 | 1 | 0.6534 | 315.5239 | 0 | 0 | 0 | 0 | 0 | 200 | 216400 | 200 | 199478.0712 | 510.81 | 115.5239
2269 | 4 | 0 | 1 | 0.61449 | 313.9328 | 0 | 0 | 0 | 0 | 0 | 200 | 216400 | 200 | 199678.0712 | 510.81 | 113.9328
2270 | 4 | 0 | 1 | 0.48848 | 308.7788 | 0 | 0 | 0 | 0 | 0 | 200 | 216400 | 200 | 199878.0712 | 510.81 | 108.7788
2271 | 4 | 0 | 1 | 0.40027 | 305.1712 | 0 | 0 | 0 | 0 | 0 | 200 | 216400 | 200 | 200078.0712 | 510.81 | 105.1712
2272 | 4 | 0 | 1 | 0.30735 | 301.3707 | 0 | 0 | 0 | 0 | 0 | 200 | 216400 | 200 | 200278.0712 | 510.81 | 101.3707
2273 | 4 | 0 | 0.688 | 0.43958 | 216.6731 | 0 | 0 | 0 | 0 | 0 | 200 | 216400 | 200 | 200478.0712 | 510.81 | 16.6731
2274 | 4 | 0 | 0.34281 | 0.32391 | 112.2528 | 0 | 0 | 0 | 0 | 0 | 112.2528 | 216400 | 112.2528 | 200590.324 | 510.81 | 0
2275 | 4 | 0 | 0.056729 | 0.252 | 26.6901 | 0 | 0 | 0 | 0 | 0 | 26.6901 | 216400 | 26.6901 | 200617.0141 | 510.81 | 0
2276 | 4 | 1 | 0 | 0.16989 | 6.9483 | 200 | 6.9483 | 180 | 186.9483 | 0 | 0 | 216200 | 186.9483 | 200803.9624 | 330.81 | 0
2277 | 4 | 1 | 0 | 0.12196 | 4.9883 | 200 | 4.9883 | 180 | 184.9883 | 0 | 0 | 216000 | 184.9883 | 200988.9507 | 150.81 | 0
2278 | 4 | 0 | 0 | 0.20121 | 8.2296 | 0 | 0 | 0 | 0 | 8.2296 | 0 | 216000 | 0 | 200988.9507 | 157.9434 | 0
2279 | 4 | 0 | 0 | 0.21097 | 8.6285 | 0 | 0 | 0 | 0 | 8.6285 | 0 | 216000 | 0 | 200988.9507 | 165.4226 | 0
2280 | 4 | 0 | 0 | 0.20121 | 8.2293 | 0 | 0 | 0 | 0 | 8.2293 | 0 | 216000 | 0 | 200988.9507 | 172.5558 | 0
2281 | 4 | 0 | 0 | 0.1551 | 6.3436 | 0 | 0 | 0 | 0 | 6.3436 | 0 | 216000 | 0 | 200988.9507 | 178.0544 | 0
2282 | 4 | 0 | 0 | 0.1363 | 5.5745 | 0 | 0 | 0 | 0 | 5.5745 | 0 | 216000 | 0 | 200988.9507 | 182.8864 | 0
2283 | 4 | 0 | 0 | 0.11357 | 4.6451 | 0 | 0 | 0 | 0 | 4.6451 | 0 | 216000 | 0 | 200988.9507 | 186.9128 | 0
2284 | 4 | 0 | 0 | 0.16712 | 6.8354 | 0 | 0 | 0 | 0 | 6.8354 | 0 | 216000 | 0 | 200988.9507 | 192.8377 | 0
2285 | 4 | 0 | 0 | 0.15689 | 6.417 | 0 | 0 | 0 | 0 | 6.417 | 0 | 216000 | 0 | 200988.9507 | 198.4 | 0
2286 | 4 | 0 | 0 | 0.13944 | 5.703 | 0 | 0 | 0 | 0 | 5.703 | 0 | 216000 | 0 | 200988.9507 | 203.3433 | 0
2287 | 4 | 0 | 0.044887 | 0.1312 | 18.3297 | 0 | 0 | 0 | 0 | 18.3297 | 0 | 216000 | 0 | 200988.9507 | 219.2315 | 0
2288 | 4 | 1 | 0.27125 | 0.19356 | 86.2548 | 200 | 86.2548 | 113.7452 | 200 | 0 | 0 | 215800 | 200 | 201188.9507 | 105.4863 | 0
2289 | 4 | 1 | 0.54438 | 0.25464 | 167.6323 | 200 | 167.6323 | 32.3677 | 200 | 0 | 0 | 215600 | 200 | 201388.9507 | 73.1186 | 0
2290 | 4 | 0 | 0.80996 | 0.27826 | 245.2974 | 0 | 0 | 0 | 0 | 180 | 65.2974 | 215600 | 65.2974 | 201454.248 | 229.1426 | 0
2291 | 4 | 0 | 1 | 0.28658 | 300.5211 | 0 | 0 | 0 | 0 | 180 | 120.5211 | 215600 | 120.5211 | 201574.7692 | 385.1666 | 0
2292 | 4 | 0 | 1 | 0.28805 | 300.5812 | 0 | 0 | 0 | 0 | 144.9508 | 155.6303 | 215600 | 155.6303 | 201730.3995 | 510.81 | 0
2293 | 4 | 0 | 1 | 0.21369 | 297.5401 | 0 | 0 | 0 | 0 | 0 | 200 | 215600 | 200 | 201930.3995 | 510.81 | 97.5401
2294 | 4 | 0 | 1 | 0.14429 | 294.7015 | 0 | 0 | 0 | 0 | 0 | 200 | 215600 | 200 | 202130.3995 | 510.81 | 94.7015
2295 | 4 | 0 | 1 | 0.14855 | 294.8757 | 0 | 0 | 0 | 0 | 0 | 200 | 215600 | 200 | 202330.3995 | 510.81 | 94.8757
2296 | 4 | 0 | 0.80996 | 0.14646 | 239.9066 | 0 | 0 | 0 | 0 | 0 | 200 | 215600 | 200 | 202530.3995 | 510.81 | 39.9066
2297 | 4 | 0 | 0.54438 | 0.29803 | 169.4069 | 0 | 0 | 0 | 0 | 0 | 169.4069 | 215600 | 169.4069 | 202699.8064 | 510.81 | 0
2298 | 4 | 0 | 0.27125 | 0.23277 | 87.8585 | 0 | 0 | 0 | 0 | 0 | 87.8585 | 215600 | 87.8585 | 202787.6649 | 510.81 | 0
2299 | 4 | 0 | 0.044887 | 0.21228 | 21.6455 | 0 | 0 | 0 | 0 | 0 | 21.6455 | 215600 | 21.6455 | 202809.3104 | 510.81 | 0
2300 | 4 | 1 | 0 | 0.20511 | 8.389 | 200 | 8.389 | 180 | 188.389 | 0 | 0 | 215400 | 188.389 | 202997.6994 | 330.81 | 0
2301 | 4 | 1 | 0 | 0.23123 | 9.4574 | 200 | 9.4574 | 180 | 189.4574 | 0 | 0 | 215200 | 189.4574 | 203187.1568 | 150.81 | 0
2302 | 4 | 0 | 0 | 0.27832 | 11.3835 | 0 | 0 | 0 | 0 | 11.3835 | 0 | 215200 | 0 | 203187.1568 | 160.6772 | 0
2303 | 4 | 0 | 0 | 0.29421 | 12.0331 | 0 | 0 | 0 | 0 | 12.0331 | 0 | 215200 | 0 | 203187.1568 | 171.1075 | 0
2304 | 4 | 0 | 0 | 0.25596 | 10.4688 | 0 | 0 | 0 | 0 | 10.4688 | 0 | 215200 | 0 | 203187.1568 | 180.1819 | 0
2305 | 4 | 0 | 0 | 0.30701 | 12.5565 | 0 | 0 | 0 | 0 | 12.5565 | 0 | 215200 | 0 | 203187.1568 | 191.0659 | 0
2306 | 4 | 0 | 0 | 0.24988 | 10.22 | 0 | 0 | 0 | 0 | 10.22 | 0 | 215200 | 0 | 203187.1568 | 199.9246 | 0
2307 | 4 | 0 | 0 | 0.28215 | 11.5399 | 0 | 0 | 0 | 0 | 11.5399 | 0 | 215200 | 0 | 203187.1568 | 209.9274 | 0
2308 | 4 | 0 | 0 | 0.23942 | 9.7922 | 0 | 0 | 0 | 0 | 9.7922 | 0 | 215200 | 0 | 203187.1568 | 218.4153 | 0
2309 | 4 | 0 | 0 | 0.25047 | 10.2441 | 0 | 0 | 0 | 0 | 10.2441 | 0 | 215200 | 0 | 203187.1568 | 227.2949 | 0
2310 | 4 | 0 | 0 | 0.28843 | 11.7966 | 0 | 0 | 0 | 0 | 11.7966 | 0 | 215200 | 0 | 203187.1568 | 237.5202 | 0
2311 | 4 | 0 | 0.05303 | 0.26464 | 26.139 | 0 | 0 | 0 | 0 | 26.139 | 0 | 215200 | 0 | 203187.1568 | 260.1775 | 0
2312 | 4 | 1 | 0.32046 | 0.2767 | 103.8667 | 200 | 103.8667 | 96.1333 | 200 | 0 | 0 | 215000 | 200 | 203387.1568 | 164.0442 | 0
2313 | 4 | 1 | 0.64314 | 0.19453 | 193.6952 | 200 | 193.6952 | 6.3048 | 200 | 0 | 0 | 214800 | 200 | 203587.1568 | 157.7394 | 0
2314 | 4 | 0 | 0.9569 | 0.21724 | 285.2369 | 0 | 0 | 0 | 0 | 180 | 105.2369 | 214800 | 105.2369 | 203692.3937 | 313.7634 | 0
2315 | 4 | 0 | 1 | 0.27132 | 299.8971 | 0 | 0 | 0 | 0 | 180 | 119.8971 | 214800 | 119.8971 | 203812.2908 | 469.7874 | 0
2316 | 4 | 0 | 1 | 0.32249 | 301.9898 | 0 | 0 | 0 | 0 | 47.3265 | 200 | 214800 | 200 | 204012.2908 | 510.81 | 54.6634
2317 | 4 | 0 | 1 | 0.33747 | 302.6025 | 0 | 0 | 0 | 0 | 0 | 200 | 214800 | 200 | 204212.2908 | 510.81 | 102.6025
2318 | 4 | 0 | 1 | 0.25198 | 299.1058 | 0 | 0 | 0 | 0 | 0 | 200 | 214800 | 200 | 204412.2908 | 510.81 | 99.1058
2319 | 4 | 0 | 1 | 0.28321 | 300.3835 | 0 | 0 | 0 | 0 | 0 | 200 | 214800 | 200 | 204612.2908 | 510.81 | 100.3835
2320 | 4 | 0 | 0.9569 | 0.21609 | 285.1899 | 0 | 0 | 0 | 0 | 0 | 200 | 214800 | 200 | 204812.2908 | 510.81 | 85.1899
2321 | 4 | 0 | 0.64314 | 0.19301 | 193.6328 | 0 | 0 | 0 | 0 | 0 | 193.6328 | 214800 | 193.6328 | 205005.9236 | 510.81 | 0
2322 | 4 | 0 | 0.32046 | 0.23537 | 102.1762 | 0 | 0 | 0 | 0 | 0 | 102.1762 | 214800 | 102.1762 | 205108.0998 | 510.81 | 0
2323 | 4 | 0 | 0.05303 | 0.22341 | 24.4525 | 0 | 0 | 0 | 0 | 0 | 24.4525 | 214800 | 24.4525 | 205132.5523 | 510.81 | 0
2324 | 4 | 1 | 0 | 0.15957 | 6.5265 | 200 | 6.5265 | 180 | 186.5265 | 0 | 0 | 214600 | 186.5265 | 205319.0787 | 330.81 | 0
2325 | 4 | 1 | 0 | 0.18858 | 7.713 | 200 | 7.713 | 180 | 187.713 | 0 | 0 | 214400 | 187.713 | 205506.7918 | 150.81 | 0
2326 | 4 | 0 | 0 | 0.23965 | 9.8016 | 0 | 0 | 0 | 0 | 9.8016 | 0 | 214400 | 0 | 205506.7918 | 159.306 | 0
2327 | 4 | 0 | 0 | 0.27219 | 11.1325 | 0 | 0 | 0 | 0 | 11.1325 | 0 | 214400 | 0 | 205506.7918 | 168.9557 | 0
2328 | 4 | 0 | 0 | 0.17782 | 7.2726 | 0 | 0 | 0 | 0 | 7.2726 | 0 | 214400 | 0 | 205506.7918 | 175.2596 | 0
2329 | 4 | 0 | 0 | 0.19067 | 7.7982 | 0 | 0 | 0 | 0 | 7.7982 | 0 | 214400 | 0 | 205506.7918 | 182.0191 | 0
2330 | 4 | 0 | 0 | 0.1527 | 6.2453 | 0 | 0 | 0 | 0 | 6.2453 | 0 | 214400 | 0 | 205506.7918 | 187.4326 | 0
2331 | 4 | 0 | 0 | 0.22977 | 9.3975 | 0 | 0 | 0 | 0 | 9.3975 | 0 | 214400 | 0 | 205506.7918 | 195.5783 | 0
2332 | 4 | 0 | 0 | 0.222 | 9.0799 | 0 | 0 | 0 | 0 | 9.0799 | 0 | 214400 | 0 | 205506.7918 | 203.4488 | 0
2333 | 4 | 0 | 0 | 0.18574 | 7.5968 | 0 | 0 | 0 | 0 | 7.5968 | 0 | 214400 | 0 | 205506.7918 | 210.0337 | 0
2334 | 4 | 0 | 0 | 0.20764 | 8.4924 | 0 | 0 | 0 | 0 | 8.4924 | 0 | 214400 | 0 | 205506.7918 | 217.3949 | 0
2335 | 4 | 0 | 0.051099 | 0.23065 | 24.191 | 0 | 0 | 0 | 0 | 24.191 | 0 | 214400 | 0 | 205506.7918 | 238.3636 | 0
2336 | 4 | 1 | 0.30879 | 0.45908 | 107.9561 | 200 | 107.9561 | 92.0439 | 200 | 0 | 0 | 214200 | 200 | 205706.7918 | 146.3197 | 0
2337 | 4 | 1 | 0.61972 | 0.50772 | 199.7414 | 200 | 199.7414 | 0.25862 | 200 | 0 | 0 | 214000 | 200 | 205906.7918 | 146.0611 | 0
2338 | 4 | 0 | 0.92205 | 0.66733 | 293.5829 | 0 | 0 | 0 | 0 | 180 | 113.5829 | 214000 | 113.5829 | 206020.3747 | 302.0851 | 0
2339 | 4 | 0 | 1 | 0.7802 | 320.7103 | 0 | 0 | 0 | 0 | 180 | 140.7103 | 214000 | 140.7103 | 206161.085 | 458.1091 | 0
2340 | 4 | 0 | 1 | 0.47978 | 308.423 | 0 | 0 | 0 | 0 | 60.7994 | 200 | 214000 | 200 | 206361.085 | 510.81 | 47.6236
2341 | 4 | 0 | 1 | 0.5141 | 309.8267 | 0 | 0 | 0 | 0 | 0 | 200 | 214000 | 200 | 206561.085 | 510.81 | 109.8267
2342 | 4 | 0 | 1 | 0.78851 | 321.0499 | 0 | 0 | 0 | 0 | 0 | 200 | 214000 | 200 | 206761.085 | 510.81 | 121.0499
2343 | 4 | 0 | 1 | 0.67054 | 316.2252 | 0 | 0 | 0 | 0 | 0 | 200 | 214000 | 200 | 206961.085 | 510.81 | 116.2252
2344 | 4 | 0 | 0.92205 | 0.53173 | 288.037 | 0 | 0 | 0 | 0 | 0 | 200 | 214000 | 200 | 207161.085 | 510.81 | 88.037
2345 | 4 | 0 | 0.61972 | 0.68894 | 207.1534 | 0 | 0 | 0 | 0 | 0 | 200 | 214000 | 200 | 207361.085 | 510.81 | 7.1534
2346 | 4 | 0 | 0.30879 | 0.64332 | 115.4916 | 0 | 0 | 0 | 0 | 0 | 115.4916 | 214000 | 115.4916 | 207476.5766 | 510.81 | 0
2347 | 4 | 0 | 0.051099 | 0.69442 | 43.1591 | 0 | 0 | 0 | 0 | 0 | 43.1591 | 214000 | 43.1591 | 207519.7357 | 510.81 | 0
2348 | 4 | 1 | 0 | 0.45635 | 18.6648 | 200 | 18.6648 | 180 | 198.6648 | 0 | 0 | 213800 | 198.6648 | 207718.4004 | 330.81 | 0
2349 | 4 | 1 | 0 | 0.4931 | 20.1677 | 200 | 20.1677 | 179.8323 | 200 | 0 | 0 | 213600 | 200 | 207918.4004 | 150.9777 | 0
2350 | 4 | 0 | 0 | 0.35969 | 14.7112 | 0 | 0 | 0 | 0 | 14.7112 | 0 | 213600 | 0 | 207918.4004 | 163.7293 | 0
2351 | 4 | 0 | 0 | 0.35133 | 14.3694 | 0 | 0 | 0 | 0 | 14.3694 | 0 | 213600 | 0 | 207918.4004 | 176.1847 | 0
2352 | 4 | 0 | 0 | 0.29525 | 12.0756 | 0 | 0 | 0 | 0 | 12.0756 | 0 | 213600 | 0 | 207918.4004 | 186.6518 | 0
2353 | 4 | 0 | 0 | 0.27107 | 11.0868 | 0 | 0 | 0 | 0 | 11.0868 | 0 | 213600 | 0 | 207918.4004 | 196.2618 | 0
2354 | 4 | 0 | 0 | 0.28891 | 11.8165 | 0 | 0 | 0 | 0 | 11.8165 | 0 | 213600 | 0 | 207918.4004 | 206.5044 | 0
2355 | 4 | 0 | 0 | 0.2253 | 9.2147 | 0 | 0 | 0 | 0 | 9.2147 | 0 | 213600 | 0 | 207918.4004 | 214.4917 | 0
2356 | 4 | 0 | 0 | 0.25993 | 10.6311 | 0 | 0 | 0 | 0 | 10.6311 | 0 | 213600 | 0 | 207918.4004 | 223.7068 | 0
2357 | 4 | 0 | 0 | 0.36186 | 14.8 | 0 | 0 | 0 | 0 | 14.8 | 0 | 213600 | 0 | 207918.4004 | 236.5354 | 0
2358 | 4 | 0 | 0 | 0.48449 | 19.8156 | 0 | 0 | 0 | 0 | 19.8156 | 0 | 213600 | 0 | 207918.4004 | 253.7115 | 0
2359 | 4 | 0 | 0.050516 | 0.47133 | 33.8664 | 0 | 0 | 0 | 0 | 33.8664 | 0 | 213600 | 0 | 207918.4004 | 283.0669 | 0
2360 | 4 | 1 | 0.30527 | 0.67378 | 115.7191 | 200 | 115.7191 | 84.2809 | 200 | 0 | 0 | 213400 | 200 | 208118.4004 | 198.786 | 0
2361 | 4 | 1 | 0.61265 | 0.76827 | 208.3544 | 200 | 200 | 0 | 200 | 8.3544 | 0 | 213200 | 200 | 208318.4004 | 206.0276 | 0
2362 | 4 | 0 | 0.91153 | 0.55887 | 286.1065 | 0 | 0 | 0 | 0 | 180 | 106.1065 | 213200 | 106.1065 | 208424.5069 | 362.0516 | 0
2363 | 4 | 0 | 1 | 0.39931 | 305.1316 | 0 | 0 | 0 | 0 | 171.618 | 133.5137 | 213200 | 133.5137 | 208558.0206 | 510.81 | 0
2364 | 4 | 0 | 1 | 0.36507 | 303.7312 | 0 | 0 | 0 | 0 | 0 | 200 | 213200 | 200 | 208758.0206 | 510.81 | 103.7312
2365 | 4 | 0 | 1 | 0.32194 | 301.9674 | 0 | 0 | 0 | 0 | 0 | 200 | 213200 | 200 | 208958.0206 | 510.81 | 101.9674
2366 | 4 | 0 | 1 | 0.3258 | 302.1252 | 0 | 0 | 0 | 0 | 0 | 200 | 213200 | 200 | 209158.0206 | 510.81 | 102.1252
2367 | 4 | 0 | 1 | 0.2727 | 299.9533 | 0 | 0 | 0 | 0 | 0 | 200 | 213200 | 200 | 209358.0206 | 510.81 | 99.9533
2368 | 4 | 0 | 0.91153 | 0.37597 | 278.626 | 0 | 0 | 0 | 0 | 0 | 200 | 213200 | 200 | 209558.0206 | 510.81 | 78.626
2369 | 4 | 0 | 0.61265 | 0.51322 | 197.9229 | 0 | 0 | 0 | 0 | 0 | 197.9229 | 213200 | 197.9229 | 209755.9435 | 510.81 | 0
2370 | 4 | 0 | 0.30527 | 0.60429 | 112.8769 | 0 | 0 | 0 | 0 | 0 | 112.8769 | 213200 | 112.8769 | 209868.8204 | 510.81 | 0
2371 | 4 | 0 | 0.050516 | 0.8165 | 47.9837 | 0 | 0 | 0 | 0 | 0 | 47.9837 | 213200 | 47.9837 | 209916.8041 | 510.81 | 0
2372 | 4 | 1 | 0 | 0.88653 | 36.259 | 200 | 36.259 | 163.741 | 200 | 0 | 0 | 213000 | 200 | 210116.8041 | 347.069 | 0
2373 | 4 | 1 | 0 | 0.6103 | 24.9611 | 200 | 24.9611 | 175.0389 | 200 | 0 | 0 | 212800 | 200 | 210316.8041 | 172.03 | 0
2374 | 4 | 0 | 0 | 0.616 | 25.1946 | 0 | 0 | 0 | 0 | 25.1946 | 0 | 212800 | 0 | 210316.8041 | 193.8687 | 0
2375 | 4 | 0 | 0 | 0.65557 | 26.8129 | 0 | 0 | 0 | 0 | 26.8129 | 0 | 212800 | 0 | 210316.8041 | 217.1101 | 0
2376 | 4 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 212800 | 0 | 210316.8041 | 252.5622 | 0
2377 | 4 | 0 | 0 | 0.95296 | 38.9761 | 0 | 0 | 0 | 0 | 38.9761 | 0 | 212800 | 0 | 210316.8041 | 286.3468 | 0
2378 | 4 | 0 | 0 | 0.66288 | 27.112 | 0 | 0 | 0 | 0 | 27.112 | 0 | 212800 | 0 | 210316.8041 | 309.8474 | 0
2379 | 4 | 0 | 0 | 0.39923 | 16.3284 | 0 | 0 | 0 | 0 | 16.3284 | 0 | 212800 | 0 | 210316.8041 | 324.0009 | 0
2380 | 4 | 0 | 0 | 0.40794 | 16.6848 | 0 | 0 | 0 | 0 | 16.6848 | 0 | 212800 | 0 | 210316.8041 | 338.4633 | 0
2381 | 4 | 0 | 0 | 0.37508 | 15.3407 | 0 | 0 | 0 | 0 | 15.3407 | 0 | 212800 | 0 | 210316.8041 | 351.7606 | 0
2382 | 4 | 0 | 0 | 0.34545 | 14.1291 | 0 | 0 | 0 | 0 | 14.1291 | 0 | 212800 | 0 | 210316.8041 | 364.0076 | 0
2383 | 4 | 0 | 0.058348 | 0.27867 | 28.2486 | 0 | 0 | 0 | 0 | 28.2486 | 0 | 212800 | 0 | 210316.8041 | 388.4936 | 0
2384 | 4 | 1 | 0.3526 | 0.23658 | 111.5058 | 200 | 111.5058 | 88.4942 | 200 | 0 | 0 | 212600 | 200 | 210516.8041 | 299.9993 | 0
2385 | 4 | 1 | 0.70763 | 0.18916 | 212.0998 | 200 | 200 | 0 | 200 | 12.0998 | 0 | 212400 | 200 | 210716.8041 | 310.4874 | 0
2386 | 4 | 0 | 1 | 0.29834 | 301.0022 | 0 | 0 | 0 | 0 | 180 | 121.0022 | 212400 | 121.0022 | 210837.8063 | 466.5114 | 0
2387 | 4 | 0 | 1 | 0.39215 | 304.8389 | 0 | 0 | 0 | 0 | 51.1059 | 200 | 212400 | 200 | 211037.8063 | 510.81 | 53.733
2388 | 4 | 0 | 1 | 0.43196 | 306.4673 | 0 | 0 | 0 | 0 | 0 | 200 | 212400 | 200 | 211237.8063 | 510.81 | 106.4673
2389 | 4 | 0 | 1 | 0.31619 | 301.7323 | 0 | 0 | 0 | 0 | 0 | 200 | 212400 | 200 | 211437.8063 | 510.81 | 101.7323
2390 | 4 | 0 | 1 | 0.31198 | 301.56 | 0 | 0 | 0 | 0 | 0 | 200 | 212400 | 200 | 211637.8063 | 510.81 | 101.56
2391 | 4 | 0 | 1 | 0.27107 | 299.8869 | 0 | 0 | 0 | 0 | 0 | 200 | 212400 | 200 | 211837.8063 | 510.81 | 99.8869
2392 | 4 | 0 | 1 | 0.24391 | 298.7761 | 0 | 0 | 0 | 0 | 0 | 200 | 212400 | 200 | 212037.8063 | 510.81 | 98.7761
2393 | 4 | 0 | 0.70763 | 0.14049 | 210.1092 | 0 | 0 | 0 | 0 | 0 | 200 | 212400 | 200 | 212237.8063 | 510.81 | 10.1092
2394 | 4 | 0 | 0.3526 | 0.12138 | 106.7941 | 0 | 0 | 0 | 0 | 0 | 106.7941 | 212400 | 106.7941 | 212344.6004 | 510.81 | 0
2395 | 4 | 0 | 0.058348 | 0.12143 | 21.8172 | 0 | 0 | 0 | 0 | 0 | 21.8172 | 212400 | 21.8172 | 212366.4176 | 510.81 | 0
2396 | 4 | 1 | 0 | 0.11199 | 4.5804 | 200 | 4.5804 | 180 | 184.5804 | 0 | 0 | 212200 | 184.5804 | 212550.998 | 330.81 | 0
2397 | 4 | 1 | 0 | 0.071955 | 2.943 | 200 | 2.943 | 180 | 182.943 | 0 | 0 | 212000 | 182.943 | 212733.941 | 150.81 | 0
2398 | 4 | 0 | 0 | 0.072029 | 2.946 | 0 | 0 | 0 | 0 | 2.946 | 0 | 212000 | 0 | 212733.941 | 153.3636 | 0
2399 | 4 | 0 | 0 | 0.082016 | 3.3545 | 0 | 0 | 0 | 0 | 3.3545 | 0 | 212000 | 0 | 212733.941 | 156.2712 | 0
2400 | 4 | 0 | 0 | 0.094557 | 3.8674 | 0 | 0 | 0 | 0 | 3.8674 | 0 | 212000 | 0 | 212733.941 | 159.6235 | 0
2401 | 4 | 0 | 0 | 0.11742 | 4.8024 | 0 | 0 | 0 | 0 | 4.8024 | 0 | 212000 | 0 | 212733.941 | 163.7862 | 0
2402 | 4 | 0 | 0 | 0.1869 | 7.6442 | 0 | 0 | 0 | 0 | 7.6442 | 0 | 212000 | 0 | 212733.941 | 170.4122 | 0
2403 | 4 | 0 | 0 | 0.26588 | 10.8745 | 0 | 0 | 0 | 0 | 10.8745 | 0 | 212000 | 0 | 212733.941 | 179.8382 | 0
2404 | 4 | 0 | 0 | 0.29943 | 12.2468 | 0 | 0 | 0 | 0 | 12.2468 | 0 | 212000 | 0 | 212733.941 | 190.4537 | 0
2405 | 4 | 0 | 0 | 0.34716 | 14.1989 | 0 | 0 | 0 | 0 | 14.1989 | 0 | 212000 | 0 | 212733.941 | 202.7613 | 0
2406 | 4 | 0 | 0 | 0.45811 | 18.7367 | 0 | 0 | 0 | 0 | 18.7367 | 0 | 212000 | 0 | 212733.941 | 219.0023 | 0
2407 | 4 | 0 | 0.0532 | 0.44245 | 33.4604 | 0 | 0 | 0 | 0 | 33.4604 | 0 | 212000 | 0 | 212733.941 | 248.0057 | 0
2408 | 4 | 1 | 0.32149 | 0.40159 | 109.2706 | 200 | 109.2706 | 90.7294 | 200 | 0 | 0 | 211800 | 200 | 212933.941 | 157.2763 | 0
2409 | 4 | 1 | 0.64519 | 0.45176 | 204.8089 | 200 | 200 | 0 | 200 | 4.8089 | 0 | 211600 | 200 | 213133.941 | 161.4446 | 0
2410 | 4 | 0 | 0.95995 | 0.53623 | 299.1664 | 0 | 0 | 0 | 0 | 180 | 119.1664 | 211600 | 119.1664 | 213253.1074 | 317.4686 | 0
2411 | 4 | 0 | 1 | 0.83834 | 323.0882 | 0 | 0 | 0 | 0 | 180 | 143.0882 | 211600 | 143.0882 | 213396.1956 | 473.4926 | 0
2412 | 4 | 0 | 1 | 0.61108 | 313.793 | 0 | 0 | 0 | 0 | 43.0519 | 200 | 211600 | 200 | 213596.1956 | 510.81 | 70.7411
2413 | 4 | 0 | 1 | 0.36852 | 303.8725 | 0 | 0 | 0 | 0 | 0 | 200 | 211600 | 200 | 213796.1956 | 510.81 | 103.8725
2414 | 4 | 0 | 1 | 0.28769 | 300.5666 | 0 | 0 | 0 | 0 | 0 | 200 | 211600 | 200 | 213996.1956 | 510.81 | 100.5666
2415 | 4 | 0 | 1 | 0.35276 | 303.228 | 0 | 0 | 0 | 0 | 0 | 200 | 211600 | 200 | 214196.1956 | 510.81 | 103.228
2416 | 4 | 0 | 0.95995 | 0.28299 | 288.8091 | 0 | 0 | 0 | 0 | 0 | 200 | 211600 | 200 | 214396.1956 | 510.81 | 88.8091
2417 | 4 | 0 | 0.64519 | 0.25297 | 196.6785 | 0 | 0 | 0 | 0 | 0 | 196.6785 | 211600 | 196.6785 | 214592.8741 | 510.81 | 0
2418 | 4 | 0 | 0.32149 | 0.19443 | 100.7976 | 0 | 0 | 0 | 0 | 0 | 100.7976 | 211600 | 100.7976 | 214693.6717 | 510.81 | 0
2419 | 4 | 0 | 0.0532 | 0.22916 | 24.7368 | 0 | 0 | 0 | 0 | 0 | 24.7368 | 211600 | 24.7368 | 214718.4084 | 510.81 | 0
2420 | 4 | 1 | 0 | 0.24316 | 9.9451 | 200 | 9.9451 | 180 | 189.9451 | 0 | 0 | 211400 | 189.9451 | 214908.3535 | 330.81 | 0
2421 | 4 | 1 | 0 | 0.22191 | 9.0762 | 200 | 9.0762 | 180 | 189.0762 | 0 | 0 | 211200 | 189.0762 | 215097.4298 | 150.81 | 0
2422 | 4 | 0 | 0 | 0.29153 | 11.9235 | 0 | 0 | 0 | 0 | 11.9235 | 0 | 211200 | 0 | 215097.4298 | 161.1453 | 0
2423 | 4 | 0 | 0 | 0.16203 | 6.627 | 0 | 0 | 0 | 0 | 6.627 | 0 | 211200 | 0 | 215097.4298 | 166.8896 | 0
2424 | 4 | 0 | 0 | 0.15278 | 6.2489 | 0 | 0 | 0 | 0 | 6.2489 | 0 | 211200 | 0 | 215097.4298 | 172.3061 | 0
2425 | 4 | 0 | 0 | 0.15107 | 6.1789 | 0 | 0 | 0 | 0 | 6.1789 | 0 | 211200 | 0 | 215097.4298 | 177.662 | 0
2426 | 4 | 0 | 0 | 0.13283 | 5.4327 | 0 | 0 | 0 | 0 | 5.4327 | 0 | 211200 | 0 | 215097.4298 | 182.3711 | 0
2427 | 4 | 0 | 0 | 0.11883 | 4.8603 | 0 | 0 | 0 | 0 | 4.8603 | 0 | 211200 | 0 | 215097.4298 | 186.584 | 0
2428 | 4 | 0 | 0 | 0.10027 | 4.1009 | 0 | 0 | 0 | 0 | 4.1009 | 0 | 211200 | 0 | 215097.4298 | 190.1387 | 0
2429 | 4 | 0 | 0 | 0.14803 | 6.0545 | 0 | 0 | 0 | 0 | 6.0545 | 0 | 211200 | 0 | 215097.4298 | 195.3867 | 0
2430 | 4 | 0 | 0 | 0.18527 | 7.5774 | 0 | 0 | 0 | 0 | 7.5774 | 0 | 211200 | 0 | 215097.4298 | 201.9548 | 0
2431 | 4 | 0 | 0.058389 | 0.2158 | 25.6891 | 0 | 0 | 0 | 0 | 25.6891 | 0 | 211200 | 0 | 215097.4298 | 224.2221 | 0
2432 | 4 | 1 | 0.35285 | 0.24318 | 111.8482 | 200 | 111.8482 | 88.1518 | 200 | 0 | 0 | 211000 | 200 | 215297.4298 | 136.0703 | 0
2433 | 4 | 1 | 0.70813 | 0.27326 | 215.6852 | 200 | 200 | 0 | 200 | 15.6852 | 0 | 210800 | 200 | 215497.4298 | 149.6662 | 0
2434 | 4 | 0 | 1 | 0.29944 | 301.0472 | 0 | 0 | 0 | 0 | 180 | 121.0472 | 210800 | 121.0472 | 215618.477 | 305.6902 | 0
2435 | 4 | 0 | 1 | 0.42887 | 306.3408 | 0 | 0 | 0 | 0 | 180 | 126.3408 | 210800 | 126.3408 | 215744.8178 | 461.7142 | 0
2436 | 4 | 0 | 1 | 0.54819 | 311.2208 | 0 | 0 | 0 | 0 | 56.6403 | 200 | 210800 | 200 | 215944.8178 | 510.81 | 54.5805
2437 | 4 | 0 | 1 | 0.59835 | 313.2724 | 0 | 0 | 0 | 0 | 0 | 200 | 210800 | 200 | 216144.8178 | 510.81 | 113.2724
2438 | 4 | 0 | 1 | 0.97968 | 328.8687 | 0 | 0 | 0 | 0 | 0 | 200 | 210800 | 200 | 216344.8178 | 510.81 | 128.8687
2439 | 4 | 0 | 1 | 0.58923 | 312.8996 | 0 | 0 | 0 | 0 | 0 | 200 | 210800 | 200 | 216544.8178 | 510.81 | 112.8996
2440 | 4 | 0 | 1 | 0.73477 | 318.8522 | 0 | 0 | 0 | 0 | 0 | 200 | 210800 | 200 | 216744.8178 | 510.81 | 118.8522
2441 | 4 | 0 | 0.70813 | 0.74376 | 234.9284 | 0 | 0 | 0 | 0 | 0 | 200 | 210800 | 200 | 216944.8178 | 510.81 | 34.9284
2442 | 4 | 0 | 0.35285 | 0.5066 | 122.622 | 0 | 0 | 0 | 0 | 0 | 122.622 | 210800 | 122.622 | 217067.4398 | 510.81 | 0
2443 | 4 | 0 | 0.058389 | 0.39513 | 33.0234 | 0 | 0 | 0 | 0 | 0 | 33.0234 | 210800 | 33.0234 | 217100.4632 | 510.81 | 0
2444 | 4 | 1 | 0 | 0.31208 | 12.7641 | 200 | 12.7641 | 180 | 192.7641 | 0 | 0 | 210600 | 192.7641 | 217293.2273 | 330.81 | 0
2445 | 4 | 1 | 0 | 0.3192 | 13.0551 | 200 | 13.0551 | 180 | 193.0551 | 0 | 0 | 210400 | 193.0551 | 217486.2825 | 150.81 | 0
2446 | 4 | 0 | 0 | 0.64371 | 26.3278 | 0 | 0 | 0 | 0 | 26.3278 | 0 | 210400 | 0 | 217486.2825 | 173.6309 | 0
2447 | 4 | 0 | 0 | 0.55193 | 22.5739 | 0 | 0 | 0 | 0 | 22.5739 | 0 | 210400 | 0 | 217486.2825 | 193.198 | 0
2448 | 4 | 0 | 0 | 0.47117 | 19.271 | 0 | 0 | 0 | 0 | 19.271 | 0 | 210400 | 0 | 217486.2825 | 209.9021 | 0
2449 | 4 | 0 | 0 | 0.52799 | 21.5949 | 0 | 0 | 0 | 0 | 21.5949 | 0 | 210400 | 0 | 217486.2825 | 228.6206 | 0
2450 | 4 | 0 | 0 | 0.4335 | 17.73 | 0 | 0 | 0 | 0 | 17.73 | 0 | 210400 | 0 | 217486.2825 | 243.9889 | 0
2451 | 4 | 0 | 0 | 0.4273 | 17.4767 | 0 | 0 | 0 | 0 | 17.4767 | 0 | 210400 | 0 | 217486.2825 | 259.1377 | 0
2452 | 4 | 0 | 0 | 0.59119 | 24.1798 | 0 | 0 | 0 | 0 | 24.1798 | 0 | 210400 | 0 | 217486.2825 | 280.0968 | 0
2453 | 4 | 0 | 0 | 0.66492 | 27.1951 | 0 | 0 | 0 | 0 | 27.1951 | 0 | 210400 | 0 | 217486.2825 | 303.6695 | 0
2454 | 4 | 0 | 0 | 0.81341 | 33.2683 | 0 | 0 | 0 | 0 | 33.2683 | 0 | 210400 | 0 | 217486.2825 | 332.5064 | 0
2455 | 4 | 0 | 0.049785 | 1 | 55.2779 | 0 | 0 | 0 | 0 | 55.2779 | 0 | 210400 | 0 | 217486.2825 | 380.4213 | 0
2456 | 4 | 1 | 0.30085 | 0.84639 | 121.5032 | 200 | 121.5032 | 78.4968 | 200 | 0 | 0 | 210200 | 200 | 217686.2825 | 301.9245 | 0
2457 | 4 | 1 | 0.60378 | 0.7629 | 205.5747 | 200 | 200 | 0 | 200 | 5.5747 | 0 | 210000 | 200 | 217886.2825 | 306.7567 | 0
2458 | 4 | 0 | 0.89834 | 0.62848 | 285.1444 | 0 | 0 | 0 | 0 | 180 | 105.1444 | 210000 | 105.1444 | 217991.4269 | 462.7807 | 0
2459 | 4 | 0 | 1 | 0.58758 | 312.8322 | 0 | 0 | 0 | 0 | 55.4099 | 200 | 210000 | 200 | 218191.4269 | 510.81 | 57.4223
2460 | 4 | 0 | 1 | 0.53566 | 310.7086 | 0 | 0 | 0 | 0 | 0 | 200 | 210000 | 200 | 218391.4269 | 510.81 | 110.7086
2461 | 4 | 0 | 1 | 0.48484 | 308.63 | 0 | 0 | 0 | 0 | 0 | 200 | 210000 | 200 | 218591.4269 | 510.81 | 108.63
2462 | 4 | 0 | 1 | 0.33912 | 302.6698 | 0 | 0 | 0 | 0 | 0 | 200 | 210000 | 200 | 218791.4269 | 510.81 | 102.6698
2463 | 4 | 0 | 1 | 0.30572 | 301.304 | 0 | 0 | 0 | 0 | 0 | 200 | 210000 | 200 | 218991.4269 | 510.81 | 101.304
2464 | 4 | 0 | 0.89834 | 0.49752 | 279.7884 | 0 | 0 | 0 | 0 | 0 | 200 | 210000 | 200 | 219191.4269 | 510.81 | 79.7884
2465 | 4 | 0 | 0.60378 | 0.53253 | 196.1526 | 0 | 0 | 0 | 0 | 0 | 196.1526 | 210000 | 196.1526 | 219387.5794 | 510.81 | 0
2466 | 4 | 0 | 0.30085 | 0.83632 | 121.0911 | 0 | 0 | 0 | 0 | 0 | 121.0911 | 210000 | 121.0911 | 219508.6705 | 510.81 | 0
2467 | 4 | 0 | 0.049785 | 0.78791 | 46.6035 | 0 | 0 | 0 | 0 | 0 | 46.6035 | 210000 | 46.6035 | 219555.274 | 510.81 | 0
2468 | 4 | 1 | 0 | 0.67988 | 27.8073 | 200 | 27.8073 | 172.1927 | 200 | 0 | 0 | 209800 | 200 | 219755.274 | 338.6173 | 0
2469 | 4 | 1 | 0 | 0.92658 | 37.897 | 200 | 37.897 | 162.103 | 200 | 0 | 0 | 209600 | 200 | 219955.274 | 176.5143 | 0
2470 | 4 | 0 | 0 | 0.93618 | 38.2899 | 0 | 0 | 0 | 0 | 38.2899 | 0 | 209600 | 0 | 219955.274 | 209.7039 | 0
2471 | 4 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 209600 | 0 | 219955.274 | 245.156 | 0
2472 | 4 | 0 | 0 | 0.94755 | 38.755 | 0 | 0 | 0 | 0 | 38.755 | 0 | 209600 | 0 | 219955.274 | 278.7488 | 0
2473 | 4 | 0 | 0 | 0.84217 | 34.4449 | 0 | 0 | 0 | 0 | 34.4449 | 0 | 209600 | 0 | 219955.274 | 308.6057 | 0
2474 | 4 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 209600 | 0 | 219955.274 | 344.0578 | 0
2475 | 4 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 209600 | 0 | 219955.274 | 379.5099 | 0
2476 | 4 | 0 | 0 | 0.45798 | 18.7314 | 0 | 0 | 0 | 0 | 18.7314 | 0 | 209600 | 0 | 219955.274 | 395.7463 | 0
2477 | 4 | 0 | 0 | 0.40305 | 16.4848 | 0 | 0 | 0 | 0 | 16.4848 | 0 | 209600 | 0 | 219955.274 | 410.0353 | 0
2478 | 4 | 0 | 0 | 0.35706 | 14.6038 | 0 | 0 | 0 | 0 | 14.6038 | 0 | 209600 | 0 | 219955.274 | 422.6939 | 0
2479 | 4 | 0 | 0.058585 | 0.37726 | 32.3494 | 0 | 0 | 0 | 0 | 32.3494 | 0 | 209600 | 0 | 219955.274 | 450.7343 | 0
2480 | 4 | 1 | 0.35403 | 0.44212 | 120.3264 | 200 | 120.3264 | 79.6736 | 200 | 0 | 0 | 209400 | 200 | 220155.274 | 371.0607 | 0
2481 | 4 | 1 | 0.71051 | 0.43422 | 222.9535 | 200 | 200 | 0 | 200 | 22.9535 | 0 | 209200 | 200 | 220355.274 | 390.9568 | 0
2482 | 4 | 0 | 1 | 0.50934 | 309.6318 | 0 | 0 | 0 | 0 | 138.2709 | 171.361 | 209200 | 171.361 | 220526.635 | 510.81 | 0
2483 | 4 | 0 | 1 | 0.3512 | 303.1643 | 0 | 0 | 0 | 0 | 0 | 200 | 209200 | 200 | 220726.635 | 510.81 | 103.1643
2484 | 4 | 0 | 1 | 0.49049 | 308.8609 | 0 | 0 | 0 | 0 | 0 | 200 | 209200 | 200 | 220926.635 | 510.81 | 108.8609
2485 | 4 | 0 | 1 | 0.63027 | 314.5781 | 0 | 0 | 0 | 0 | 0 | 200 | 209200 | 200 | 221126.635 | 510.81 | 114.5781
2486 | 4 | 0 | 1 | 0.34591 | 302.9476 | 0 | 0 | 0 | 0 | 0 | 200 | 209200 | 200 | 221326.635 | 510.81 | 102.9476
2487 | 4 | 0 | 1 | 0.32327 | 302.0217 | 0 | 0 | 0 | 0 | 0 | 200 | 209200 | 200 | 221526.635 | 510.81 | 102.0217
2488 | 4 | 0 | 1 | 0.42319 | 306.1084 | 0 | 0 | 0 | 0 | 0 | 200 | 209200 | 200 | 221726.635 | 510.81 | 106.1084
2489 | 4 | 0 | 0.71051 | 0.60521 | 229.9469 | 0 | 0 | 0 | 0 | 0 | 200 | 209200 | 200 | 221926.635 | 510.81 | 29.9469
2490 | 4 | 0 | 0.35403 | 0.50448 | 122.8767 | 0 | 0 | 0 | 0 | 0 | 122.8767 | 209200 | 122.8767 | 222049.5117 | 510.81 | 0
2491 | 4 | 0 | 0.058585 | 0.30565 | 29.4203 | 0 | 0 | 0 | 0 | 0 | 29.4203 | 209200 | 29.4203 | 222078.932 | 510.81 | 0
2492 | 4 | 1 | 0 | 0.35013 | 14.3204 | 200 | 14.3204 | 180 | 194.3204 | 0 | 0 | 209000 | 194.3204 | 222273.2524 | 330.81 | 0
2493 | 4 | 1 | 0 | 0.27604 | 11.2902 | 200 | 11.2902 | 180 | 191.2902 | 0 | 0 | 208800 | 191.2902 | 222464.5425 | 150.81 | 0
2494 | 4 | 0 | 0 | 0.34203 | 13.9891 | 0 | 0 | 0 | 0 | 13.9891 | 0 | 208800 | 0 | 222464.5425 | 162.9357 | 0
2495 | 4 | 0 | 0 | 0.35884 | 14.6767 | 0 | 0 | 0 | 0 | 14.6767 | 0 | 208800 | 0 | 222464.5425 | 175.6575 | 0
2496 | 4 | 0 | 0 | 0.36828 | 15.0627 | 0 | 0 | 0 | 0 | 15.0627 | 0 | 208800 | 0 | 222464.5425 | 188.7139 | 0
2497 | 4 | 0 | 0 | 0.29102 | 11.9028 | 0 | 0 | 0 | 0 | 11.9028 | 0 | 208800 | 0 | 222464.5425 | 199.0312 | 0
2498 | 4 | 0 | 0 | 0.27171 | 11.1129 | 0 | 0 | 0 | 0 | 11.1129 | 0 | 208800 | 0 | 222464.5425 | 208.6639 | 0
2499 | 4 | 0 | 0 | 0.32947 | 13.4754 | 0 | 0 | 0 | 0 | 13.4754 | 0 | 208800 | 0 | 222464.5425 | 220.3444 | 0
2500 | 4 | 0 | 0 | 0.42084 | 17.2125 | 0 | 0 | 0 | 0 | 17.2125 | 0 | 208800 | 0 | 222464.5425 | 235.2642 | 0
2501 | 4 | 0 | 0 | 0.45728 | 18.7026 | 0 | 0 | 0 | 0 | 18.7026 | 0 | 208800 | 0 | 222464.5425 | 251.4756 | 0
2502 | 4 | 0 | 0 | 0.37134 | 15.1878 | 0 | 0 | 0 | 0 | 15.1878 | 0 | 208800 | 0 | 222464.5425 | 264.6404 | 0
2503 | 4 | 0 | 0.042997 | 0.40601 | 29.0233 | 0 | 0 | 0 | 0 | 29.0233 | 0 | 208800 | 0 | 222464.5425 | 289.7978 | 0
2504 | 4 | 1 | 0.25983 | 0.57097 | 98.3913 | 200 | 98.3913 | 101.6087 | 200 | 0 | 0 | 208600 | 200 | 222664.5425 | 188.1891 | 0
2505 | 4 | 1 | 0.52145 | 0.73874 | 180.8103 | 200 | 180.8103 | 19.1897 | 200 | 0 | 0 | 208400 | 200 | 222864.5425 | 168.9994 | 0
2506 | 4 | 0 | 0.77585 | 0.67441 | 251.6473 | 0 | 0 | 0 | 0 | 180 | 71.6473 | 208400 | 71.6473 | 222936.1898 | 325.0234 | 0
2507 | 4 | 0 | 0.98576 | 0.68378 | 312.654 | 0 | 0 | 0 | 0 | 180 | 132.654 | 208400 | 132.654 | 223068.8439 | 481.0474 | 0
2508 | 4 | 0 | 1 | 0.58894 | 312.8876 | 0 | 0 | 0 | 0 | 34.3362 | 200 | 208400 | 200 | 223268.8439 | 510.81 | 78.5514
2509 | 4 | 0 | 1 | 0.56151 | 311.7657 | 0 | 0 | 0 | 0 | 0 | 200 | 208400 | 200 | 223468.8439 | 510.81 | 111.7657
2510 | 4 | 0 | 1 | 0.63406 | 314.7329 | 0 | 0 | 0 | 0 | 0 | 200 | 208400 | 200 | 223668.8439 | 510.81 | 114.7329
2511 | 4 | 0 | 0.98576 | 0.43469 | 302.4662 | 0 | 0 | 0 | 0 | 0 | 200 | 208400 | 200 | 223868.8439 | 510.81 | 102.4662
2512 | 4 | 0 | 0.77585 | 0.33517 | 237.7724 | 0 | 0 | 0 | 0 | 0 | 200 | 208400 | 200 | 224068.8439 | 510.81 | 37.7724
2513 | 4 | 0 | 0.52145 | 0.55893 | 173.456 | 0 | 0 | 0 | 0 | 0 | 173.456 | 208400 | 173.456 | 224242.2999 | 510.81 | 0
2514 | 4 | 0 | 0.25983 | 0.67779 | 102.7601 | 0 | 0 | 0 | 0 | 0 | 102.7601 | 208400 | 102.7601 | 224345.0599 | 510.81 | 0
2515 | 4 | 0 | 0.042997 | 0.75582 | 43.3305 | 0 | 0 | 0 | 0 | 0 | 43.3305 | 208400 | 43.3305 | 224388.3904 | 510.81 | 0
2516 | 4 | 1 | 0 | 0.68702 | 28.0992 | 200 | 28.0992 | 171.9008 | 200 | 0 | 0 | 208200 | 200 | 224588.3904 | 338.9092 | 0
2517 | 4 | 1 | 0 | 0.59036 | 24.1457 | 200 | 24.1457 | 175.8543 | 200 | 0 | 0 | 208000 | 200 | 224788.3904 | 163.0549 | 0
2518 | 4 | 0 | 0 | 0.39141 | 16.0085 | 0 | 0 | 0 | 0 | 16.0085 | 0 | 208000 | 0 | 224788.3904 | 176.9311 | 0
2519 | 4 | 0 | 0 | 0.23946 | 9.7938 | 0 | 0 | 0 | 0 | 9.7938 | 0 | 208000 | 0 | 224788.3904 | 185.4203 | 0
2520 | 4 | 0 | 0 | 0.28039 | 11.4678 | 0 | 0 | 0 | 0 | 11.4678 | 0 | 208000 | 0 | 224788.3904 | 195.3606 | 0
2521 | 4 | 0 | 0 | 0.30303 | 12.394 | 0 | 0 | 0 | 0 | 12.394 | 0 | 208000 | 0 | 224788.3904 | 206.1038 | 0
2522 | 4 | 0 | 0 | 0.31664 | 12.9506 | 0 | 0 | 0 | 0 | 12.9506 | 0 | 208000 | 0 | 224788.3904 | 217.3293 | 0
2523 | 4 | 0 | 0 | 0.23939 | 9.7912 | 0 | 0 | 0 | 0 | 9.7912 | 0 | 208000 | 0 | 224788.3904 | 225.8163 | 0
2524 | 4 | 0 | 0 | 0.3167 | 12.9528 | 0 | 0 | 0 | 0 | 12.9528 | 0 | 208000 | 0 | 224788.3904 | 237.0438 | 0
2525 | 4 | 0 | 0 | 0.42736 | 17.4791 | 0 | 0 | 0 | 0 | 17.4791 | 0 | 208000 | 0 | 224788.3904 | 252.1947 | 0
2526 | 4 | 0 | 0 | 0.42288 | 17.2956 | 0 | 0 | 0 | 0 | 17.2956 | 0 | 208000 | 0 | 224788.3904 | 267.1866 | 0
2527 | 4 | 0 | 0.050537 | 0.38977 | 30.5366 | 0 | 0 | 0 | 0 | 30.5366 | 0 | 208000 | 0 | 224788.3904 | 293.6557 | 0
2528 | 4 | 1 | 0.30539 | 0.46671 | 107.2858 | 200 | 107.2858 | 92.7142 | 200 | 0 | 0 | 207800 | 200 | 224988.3904 | 200.9415 | 0
2529 | 4 | 1 | 0.6129 | 0.45122 | 195.4597 | 200 | 195.4597 | 4.5403 | 200 | 0 | 0 | 207600 | 200 | 225188.3904 | 196.4012 | 0
2530 | 4 | 0 | 0.9119 | 0.39535 | 279.5265 | 0 | 0 | 0 | 0 | 180 | 99.5265 | 207600 | 99.5265 | 225287.917 | 352.4252 | 0
2531 | 4 | 0 | 1 | 0.39015 | 304.7572 | 0 | 0 | 0 | 0 | 180 | 124.7572 | 207600 | 124.7572 | 225412.6741 | 508.4492 | 0
2532 | 4 | 0 | 1 | 0.33985 | 302.6999 | 0 | 0 | 0 | 0 | 2.7236 | 200 | 207600 | 200 | 225612.6741 | 510.81 | 99.9763
2533 | 4 | 0 | 1 | 0.25039 | 299.0412 | 0 | 0 | 0 | 0 | 0 | 200 | 207600 | 200 | 225812.6741 | 510.81 | 99.0412
2534 | 4 | 0 | 1 | 0.31314 | 301.6075 | 0 | 0 | 0 | 0 | 0 | 200 | 207600 | 200 | 226012.6741 | 510.81 | 101.6075
2535 | 4 | 0 | 1 | 0.30262 | 301.1774 | 0 | 0 | 0 | 0 | 0 | 200 | 207600 | 200 | 226212.6741 | 510.81 | 101.1774
2536 | 4 | 0 | 0.9119 | 0.44586 | 281.5925 | 0 | 0 | 0 | 0 | 0 | 200 | 207600 | 200 | 226412.6741 | 510.81 | 81.5925
2537 | 4 | 0 | 0.6129 | 0.43498 | 194.7954 | 0 | 0 | 0 | 0 | 0 | 194.7954 | 207600 | 194.7954 | 226607.4696 | 510.81 | 0
2538 | 4 | 0 | 0.30539 | 0.4984 | 108.5821 | 0 | 0 | 0 | 0 | 0 | 108.5821 | 207600 | 108.5821 | 226716.0516 | 510.81 | 0
2539 | 4 | 0 | 0.050537 | 0.36916 | 29.6939 | 0 | 0 | 0 | 0 | 0 | 29.6939 | 207600 | 29.6939 | 226745.7455 | 510.81 | 0
2540 | 4 | 1 | 0 | 0.47128 | 19.2752 | 200 | 19.2752 | 180 | 199.2752 | 0 | 0 | 207400 | 199.2752 | 226945.0207 | 330.81 | 0
2541 | 4 | 1 | 0 | 0.25336 | 10.3624 | 200 | 10.3624 | 180 | 190.3624 | 0 | 0 | 207200 | 190.3624 | 227135.3831 | 150.81 | 0
2542 | 4 | 0 | 0 | 0.31374 | 12.8318 | 0 | 0 | 0 | 0 | 12.8318 | 0 | 207200 | 0 | 227135.3831 | 161.9326 | 0
2543 | 4 | 0 | 0 | 0.23143 | 9.4657 | 0 | 0 | 0 | 0 | 9.4657 | 0 | 207200 | 0 | 227135.3831 | 170.1374 | 0
2544 | 4 | 0 | 0 | 0.29001 | 11.8613 | 0 | 0 | 0 | 0 | 11.8613 | 0 | 207200 | 0 | 227135.3831 | 180.4188 | 0
2545 | 4 | 0 | 0 | 0.24377 | 9.97 | 0 | 0 | 0 | 0 | 9.97 | 0 | 207200 | 0 | 227135.3831 | 189.0608 | 0
2546 | 4 | 0 | 0 | 0.25607 | 10.4733 | 0 | 0 | 0 | 0 | 10.4733 | 0 | 207200 | 0 | 227135.3831 | 198.1391 | 0
2547 | 4 | 0 | 0 | 0.18042 | 7.3791 | 0 | 0 | 0 | 0 | 7.3791 | 0 | 207200 | 0 | 227135.3831 | 204.5353 | 0
2548 | 4 | 0 | 0 | 0.14112 | 5.7717 | 0 | 0 | 0 | 0 | 5.7717 | 0 | 207200 | 0 | 227135.3831 | 209.5382 | 0
2549 | 4 | 0 | 0 | 0.098853 | 4.0431 | 0 | 0 | 0 | 0 | 4.0431 | 0 | 207200 | 0 | 227135.3831 | 213.0428 | 0
2550 | 4 | 0 | 0 | 0.12454 | 5.0938 | 0 | 0 | 0 | 0 | 5.0938 | 0 | 207200 | 0 | 227135.3831 | 217.4581 | 0
2551 | 4 | 0 | 0.050359 | 0.10265 | 18.7419 | 0 | 0 | 0 | 0 | 18.7419 | 0 | 207200 | 0 | 227135.3831 | 233.7036 | 0
2552 | 4 | 1 | 0.30432 | 0.071873 | 90.8275 | 200 | 90.8275 | 109.1725 | 200 | 0 | 0 | 207000 | 200 | 227335.3831 | 124.5311 | 0
2553 | 4 | 1 | 0.61074 | 0.068338 | 179.1779 | 200 | 179.1779 | 20.8221 | 200 | 0 | 0 | 206800 | 200 | 227535.3831 | 103.709 | 0
2554 | 4 | 0 | 0.9087 | 0.074436 | 265.4761 | 0 | 0 | 0 | 0 | 180 | 85.4761 | 206800 | 85.4761 | 227620.8592 | 259.733 | 0
2555 | 4 | 0 | 1 | 0.10435 | 293.0678 | 0 | 0 | 0 | 0 | 180 | 113.0678 | 206800 | 113.0678 | 227733.927 | 415.757 | 0
2556 | 4 | 0 | 1 | 0.11343 | 293.4393 | 0 | 0 | 0 | 0 | 109.6597 | 183.7796 | 206800 | 183.7796 | 227917.7066 | 510.81 | 0
2557 | 4 | 0 | 1 | 0.12983 | 294.1102 | 0 | 0 | 0 | 0 | 0 | 200 | 206800 | 200 | 228117.7066 | 510.81 | 94.1102
2558 | 4 | 0 | 1 | 0.1851 | 296.3706 | 0 | 0 | 0 | 0 | 0 | 200 | 206800 | 200 | 228317.7066 | 510.81 | 96.3706
2559 | 4 | 0 | 1 | 0.24656 | 298.8844 | 0 | 0 | 0 | 0 | 0 | 200 | 206800 | 200 | 228517.7066 | 510.81 | 98.8844
2560 | 4 | 0 | 0.9087 | 0.25378 | 272.8112 | 0 | 0 | 0 | 0 | 0 | 200 | 206800 | 200 | 228717.7066 | 510.81 | 72.8112
2561 | 4 | 0 | 0.61074 | 0.30698 | 188.9383 | 0 | 0 | 0 | 0 | 0 | 188.9383 | 206800 | 188.9383 | 228906.6449 | 510.81 | 0
2562 | 4 | 0 | 0.30432 | 0.68683 | 115.9791 | 0 | 0 | 0 | 0 | 0 | 115.9791 | 206800 | 115.9791 | 229022.624 | 510.81 | 0
2563 | 4 | 0 | 0.050359 | 0.49673 | 34.8601 | 0 | 0 | 0 | 0 | 0 | 34.8601 | 206800 | 34.8601 | 229057.4841 | 510.81 | 0
2564 | 4 | 1 | 0 | 0.45043 | 18.4224 | 200 | 18.4224 | 180 | 198.4224 | 0 | 0 | 206600 | 198.4224 | 229255.9066 | 330.81 | 0
2565 | 4 | 1 | 0 | 0.58281 | 23.8371 | 200 | 23.8371 | 176.1629 | 200 | 0 | 0 | 206400 | 200 | 229455.9066 | 154.6471 | 0
2566 | 4 | 0 | 0 | 0.76083 | 31.1179 | 0 | 0 | 0 | 0 | 31.1179 | 0 | 206400 | 0 | 229455.9066 | 181.62 | 0
2567 | 4 | 0 | 0 | 0.68769 | 28.1265 | 0 | 0 | 0 | 0 | 28.1265 | 0 | 206400 | 0 | 229455.9066 | 206.0001 | 0
2568 | 4 | 0 | 0 | 0.40759 | 16.6706 | 0 | 0 | 0 | 0 | 16.6706 | 0 | 206400 | 0 | 229455.9066 | 220.4502 | 0
2569 | 4 | 0 | 0 | 0.34304 | 14.0302 | 0 | 0 | 0 | 0 | 14.0302 | 0 | 206400 | 0 | 229455.9066 | 232.6115 | 0
2570 | 4 | 0 | 0 | 0.25405 | 10.3907 | 0 | 0 | 0 | 0 | 10.3907 | 0 | 206400 | 0 | 229455.9066 | 241.6182 | 0
2571 | 4 | 0 | 0 | 0.21329 | 8.7237 | 0 | 0 | 0 | 0 | 8.7237 | 0 | 206400 | 0 | 229455.9066 | 249.1799 | 0
2572 | 4 | 0 | 0 | 0.25204 | 10.3084 | 0 | 0 | 0 | 0 | 10.3084 | 0 | 206400 | 0 | 229455.9066 | 258.1152 | 0
2573 | 4 | 0 | 0 | 0.33126 | 13.5486 | 0 | 0 | 0 | 0 | 13.5486 | 0 | 206400 | 0 | 229455.9066 | 269.8591 | 0
2574 | 4 | 0 | 0 | 0.59857 | 24.4816 | 0 | 0 | 0 | 0 | 24.4816 | 0 | 206400 | 0 | 229455.9066 | 291.0798 | 0
2575 | 4 | 0 | 0.058964 | 0.53008 | 38.7091 | 0 | 0 | 0 | 0 | 38.7091 | 0 | 206400 | 0 | 229455.9066 | 324.6328 | 0
2576 | 4 | 1 | 0.35632 | 0.40455 | 119.4511 | 200 | 119.4511 | 80.5489 | 200 | 0 | 0 | 206200 | 200 | 229655.9066 | 244.084 | 0
2577 | 4 | 1 | 0.7151 | 0.46137 | 225.392 | 200 | 200 | 0 | 200 | 25.392 | 0 | 206000 | 200 | 229855.9066 | 266.0938 | 0
2578 | 4 | 0 | 1 | 0.36633 | 303.7827 | 0 | 0 | 0 | 0 | 180 | 123.7827 | 206000 | 123.7827 | 229979.6893 | 422.1178 | 0
2579 | 4 | 0 | 1 | 0.33117 | 302.345 | 0 | 0 | 0 | 0 | 102.3215 | 200 | 206000 | 200 | 230179.6893 | 510.81 | 0.023565
2580 | 4 | 0 | 1 | 0.38508 | 304.5499 | 0 | 0 | 0 | 0 | 0 | 200 | 206000 | 200 | 230379.6893 | 510.81 | 104.5499
2581 | 4 | 0 | 1 | 0.39119 | 304.7995 | 0 | 0 | 0 | 0 | 0 | 200 | 206000 | 200 | 230579.6893 | 510.81 | 104.7995
2582 | 4 | 0 | 1 | 0.40679 | 305.4378 | 0 | 0 | 0 | 0 | 0 | 200 | 206000 | 200 | 230779.6893 | 510.81 | 105.4378
2583 | 4 | 0 | 1 | 0.35111 | 303.1602 | 0 | 0 | 0 | 0 | 0 | 200 | 206000 | 200 | 230979.6893 | 510.81 | 103.1602
2584 | 4 | 0 | 1 | 0.39263 | 304.8586 | 0 | 0 | 0 | 0 | 0 | 200 | 206000 | 200 | 231179.6893 | 510.81 | 104.8586
2585 | 4 | 0 | 0.7151 | 0.35728 | 221.1344 | 0 | 0 | 0 | 0 | 0 | 200 | 206000 | 200 | 231379.6893 | 510.81 | 21.1344
2586 | 4 | 0 | 0.35632 | 0.19568 | 110.9085 | 0 | 0 | 0 | 0 | 0 | 110.9085 | 206000 | 110.9085 | 231490.5978 | 510.81 | 0
2587 | 4 | 0 | 0.058964 | 0.31341 | 29.8474 | 0 | 0 | 0 | 0 | 0 | 29.8474 | 206000 | 29.8474 | 231520.4452 | 510.81 | 0
2588 | 4 | 1 | 0 | 0.24382 | 9.9724 | 200 | 9.9724 | 180 | 189.9724 | 0 | 0 | 205800 | 189.9724 | 231710.4177 | 330.81 | 0
2589 | 4 | 1 | 0 | 0.25604 | 10.4721 | 200 | 10.4721 | 180 | 190.4721 | 0 | 0 | 205600 | 190.4721 | 231900.8898 | 150.81 | 0
2590 | 4 | 0 | 0 | 0.34743 | 14.2099 | 0 | 0 | 0 | 0 | 14.2099 | 0 | 205600 | 0 | 231900.8898 | 163.1271 | 0
2591 | 4 | 0 | 0 | 0.20035 | 8.1945 | 0 | 0 | 0 | 0 | 8.1945 | 0 | 205600 | 0 | 231900.8898 | 170.2301 | 0
2592 | 4 | 0 | 0 | 0.15484 | 6.3329 | 0 | 0 | 0 | 0 | 6.3329 | 0 | 205600 | 0 | 231900.8898 | 175.7195 | 0
2593 | 4 | 0 | 0 | 0.16745 | 6.8485 | 0 | 0 | 0 | 0 | 6.8485 | 0 | 205600 | 0 | 231900.8898 | 181.6558 | 0
2594 | 4 | 0 | 0 | 0.1568 | 6.413 | 0 | 0 | 0 | 0 | 6.413 | 0 | 205600 | 0 | 231900.8898 | 187.2145 | 0
2595 | 4 | 0 | 0 | 0.16217 | 6.6328 | 0 | 0 | 0 | 0 | 6.6328 | 0 | 205600 | 0 | 231900.8898 | 192.9638 | 0
2596 | 4 | 0 | 0 | 0.17416 | 7.1232 | 0 | 0 | 0 | 0 | 7.1232 | 0 | 205600 | 0 | 231900.8898 | 199.1382 | 0
2597 | 4 | 0 | 0 | 0.21495 | 8.7915 | 0 | 0 | 0 | 0 | 8.7915 | 0 | 205600 | 0 | 231900.8898 | 206.7587 | 0
2598 | 4 | 0 | 0 | 0.27868 | 11.3978 | 0 | 0 | 0 | 0 | 11.3978 | 0 | 205600 | 0 | 231900.8898 | 216.6383 | 0
2599 | 4 | 0 | 0.047283 | 0.26914 | 24.6633 | 0 | 0 | 0 | 0 | 24.6633 | 0 | 205600 | 0 | 231900.8898 | 238.0165 | 0
2600 | 4 | 1 | 0.28573 | 0.25732 | 93.0433 | 200 | 93.0433 | 106.9567 | 200 | 0 | 0 | 205400 | 200 | 232100.8898 | 131.0598 | 0
2601 | 4 | 1 | 0.57343 | 0.35869 | 180.2782 | 200 | 180.2782 | 19.7218 | 200 | 0 | 0 | 205200 | 200 | 232300.8898 | 111.338 | 0
2602 | 4 | 0 | 0.85318 | 0.38961 | 262.3347 | 0 | 0 | 0 | 0 | 180 | 82.3347 | 205200 | 82.3347 | 232383.2245 | 267.362 | 0
2603 | 4 | 0 | 1 | 0.69341 | 317.1605 | 0 | 0 | 0 | 0 | 180 | 137.1605 | 205200 | 137.1605 | 232520.385 | 423.386 | 0
2604 | 4 | 0 | 1 | 0.47009 | 308.0266 | 0 | 0 | 0 | 0 | 100.8584 | 200 | 205200 | 200 | 232720.385 | 510.81 | 7.1682
2605 | 4 | 0 | 1 | 0.37455 | 304.1189 | 0 | 0 | 0 | 0 | 0 | 200 | 205200 | 200 | 232920.385 | 510.81 | 104.1189
2606 | 4 | 0 | 1 | 0.26528 | 299.65 | 0 | 0 | 0 | 0 | 0 | 200 | 205200 | 200 | 233120.385 | 510.81 | 99.65
2607 | 4 | 0 | 1 | 0.25781 | 299.3445 | 0 | 0 | 0 | 0 | 0 | 200 | 205200 | 200 | 233320.385 | 510.81 | 99.3445
2608 | 4 | 0 | 0.85318 | 0.23954 | 256.1971 | 0 | 0 | 0 | 0 | 0 | 200 | 205200 | 200 | 233520.385 | 510.81 | 56.1971
2609 | 4 | 0 | 0.57343 | 0.27361 | 176.7983 | 0 | 0 | 0 | 0 | 0 | 176.7983 | 205200 | 176.7983 | 233697.1832 | 510.81 | 0
2610 | 4 | 0 | 0.28573 | 0.28413 | 94.1397 | 0 | 0 | 0 | 0 | 0 | 94.1397 | 205200 | 94.1397 | 233791.323 | 510.81 | 0
2611 | 4 | 0 | 0.047283 | 0.17247 | 20.7091 | 0 | 0 | 0 | 0 | 0 | 20.7091 | 205200 | 20.7091 | 233812.0321 | 510.81 | 0
2612 | 4 | 1 | 0 | 0.23602 | 9.6532 | 200 | 9.6532 | 180 | 189.6532 | 0 | 0 | 205000 | 189.6532 | 234001.6853 | 330.81 | 0
2613 | 4 | 1 | 0 | 0.16463 | 6.7334 | 200 | 6.7334 | 180 | 186.7334 | 0 | 0 | 204800 | 186.7334 | 234188.4187 | 150.81 | 0
2614 | 4 | 0 | 0 | 0.19046 | 7.79 | 0 | 0 | 0 | 0 | 7.79 | 0 | 204800 | 0 | 234188.4187 | 157.5624 | 0
2615 | 4 | 0 | 0 | 0.20936 | 8.5626 | 0 | 0 | 0 | 0 | 8.5626 | 0 | 204800 | 0 | 234188.4187 | 164.9844 | 0
2616 | 4 | 0 | 0 | 0.21609 | 8.8381 | 0 | 0 | 0 | 0 | 8.8381 | 0 | 204800 | 0 | 234188.4187 | 172.6453 | 0
2617 | 4 | 0 | 0 | 0.20822 | 8.5164 | 0 | 0 | 0 | 0 | 8.5164 | 0 | 204800 | 0 | 234188.4187 | 180.0273 | 0
2618 | 4 | 0 | 0 | 0.25185 | 10.3008 | 0 | 0 | 0 | 0 | 10.3008 | 0 | 204800 | 0 | 234188.4187 | 188.956 | 0
2619 | 4 | 0 | 0 | 0.16837 | 6.8865 | 0 | 0 | 0 | 0 | 6.8865 | 0 | 204800 | 0 | 234188.4187 | 194.9253 | 0
2620 | 4 | 0 | 0 | 0.31684 | 12.959 | 0 | 0 | 0 | 0 | 12.959 | 0 | 204800 | 0 | 234188.4187 | 206.1581 | 0
2621 | 4 | 0 | 0 | 0.38529 | 15.7584 | 0 | 0 | 0 | 0 | 15.7584 | 0 | 204800 | 0 | 234188.4187 | 219.8174 | 0
2622 | 4 | 0 | 0 | 0.43174 | 17.6582 | 0 | 0 | 0 | 0 | 17.6582 | 0 | 204800 | 0 | 234188.4187 | 235.1236 | 0
2623 | 4 | 0 | 0.059324 | 0.47239 | 36.4536 | 0 | 0 | 0 | 0 | 36.4536 | 0 | 204800 | 0 | 234188.4187 | 266.7216 | 0
2624 | 4 | 1 | 0.3585 | 0.7556 | 134.4383 | 200 | 134.4383 | 65.5617 | 200 | 0 | 0 | 204600 | 200 | 234388.4187 | 201.1599 | 0
2625 | 4 | 1 | 0.71947 | 0.58168 | 231.5744 | 200 | 200 | 0 | 200 | 31.5744 | 0 | 204400 | 200 | 234588.4187 | 228.5285 | 0
2626 | 4 | 0 | 1 | 0.61124 | 313.7997 | 0 | 0 | 0 | 0 | 180 | 133.7997 | 204400 | 133.7997 | 234722.2185 | 384.5525 | 0
2627 | 4 | 0 | 1 | 0.7225 | 318.3502 | 0 | 0 | 0 | 0 | 145.6593 | 172.6909 | 204400 | 172.6909 | 234894.9094 | 510.81 | 0
2628 | 4 | 0 | 1 | 0.64921 | 315.3529 | 0 | 0 | 0 | 0 | 0 | 200 | 204400 | 200 | 235094.9094 | 510.81 | 115.3529
2629 | 4 | 0 | 1 | 0.60962 | 313.7335 | 0 | 0 | 0 | 0 | 0 | 200 | 204400 | 200 | 235294.9094 | 510.81 | 113.7335
2630 | 4 | 0 | 1 | 0.50772 | 309.5655 | 0 | 0 | 0 | 0 | 0 | 200 | 204400 | 200 | 235494.9094 | 510.81 | 109.5655
2631 | 4 | 0 | 1 | 0.29312 | 300.7886 | 0 | 0 | 0 | 0 | 0 | 200 | 204400 | 200 | 235694.9094 | 510.81 | 100.7886
2632 | 4 | 0 | 1 | 0.35823 | 303.4516 | 0 | 0 | 0 | 0 | 0 | 200 | 204400 | 200 | 235894.9094 | 510.81 | 103.4516
2633 | 4 | 0 | 0.71947 | 0.44239 | 225.8776 | 0 | 0 | 0 | 0 | 0 | 200 | 204400 | 200 | 236094.9094 | 510.81 | 25.8776
2634 | 4 | 0 | 0.3585 | 0.25152 | 113.8212 | 0 | 0 | 0 | 0 | 0 | 113.8212 | 204400 | 113.8212 | 236208.7306 | 510.81 | 0
2635 | 4 | 0 | 0.059324 | 0.20561 | 25.542 | 0 | 0 | 0 | 0 | 0 | 25.542 | 204400 | 25.542 | 236234.2726 | 510.81 | 0
2636 | 4 | 1 | 0 | 0.20134 | 8.2348 | 200 | 8.2348 | 180 | 188.2348 | 0 | 0 | 204200 | 188.2348 | 236422.5074 | 330.81 | 0
2637 | 4 | 1 | 0 | 0.15443 | 6.316 | 200 | 6.316 | 180 | 186.316 | 0 | 0 | 204000 | 186.316 | 236608.8235 | 150.81 | 0
2638 | 4 | 0 | 0 | 0.158 | 6.462 | 0 | 0 | 0 | 0 | 6.462 | 0 | 204000 | 0 | 236608.8235 | 156.4113 | 0
2639 | 4 | 0 | 0 | 0.18831 | 7.7019 | 0 | 0 | 0 | 0 | 7.7019 | 0 | 204000 | 0 | 236608.8235 | 163.0873 | 0
2640 | 4 | 0 | 0 | 0.22538 | 9.2179 | 0 | 0 | 0 | 0 | 9.2179 | 0 | 204000 | 0 | 236608.8235 | 171.0774 | 0
2641 | 4 | 0 | 0 | 0.2373 | 9.7056 | 0 | 0 | 0 | 0 | 9.7056 | 0 | 204000 | 0 | 236608.8235 | 179.4902 | 0
2642 | 4 | 0 | 0 | 0.23277 | 9.5203 | 0 | 0 | 0 | 0 | 9.5203 | 0 | 204000 | 0 | 236608.8235 | 187.7424 | 0
2643 | 4 | 0 | 0 | 0.18417 | 7.5327 | 0 | 0 | 0 | 0 | 7.5327 | 0 | 204000 | 0 | 236608.8235 | 194.2718 | 0
2644 | 4 | 0 | 0 | 0.17794 | 7.2778 | 0 | 0 | 0 | 0 | 7.2778 | 0 | 204000 | 0 | 236608.8235 | 200.5802 | 0
2645 | 4 | 0 | 0 | 0.24406 | 9.9821 | 0 | 0 | 0 | 0 | 9.9821 | 0 | 204000 | 0 | 236608.8235 | 209.2327 | 0
2646 | 4 | 0 | 0 | 0.27784 | 11.3638 | 0 | 0 | 0 | 0 | 11.3638 | 0 | 204000 | 0 | 236608.8235 | 219.0828 | 0
2647 | 4 | 0 | 0.054946 | 0.22715 | 25.1589 | 0 | 0 | 0 | 0 | 25.1589 | 0 | 204000 | 0 | 236608.8235 | 240.8906 | 0
2648 | 4 | 1 | 0.33204 | 0.25836 | 106.4593 | 200 | 106.4593 | 93.5407 | 200 | 0 | 0 | 203800 | 200 | 236808.8235 | 147.3499 | 0
2649 | 4 | 1 | 0.66637 | 0.37434 | 207.7577 | 200 | 200 | 0 | 200 | 7.7577 | 0 | 203600 | 200 | 237008.8235 | 154.0742 | 0
2650 | 4 | 0 | 0.99146 | 0.52215 | 307.6887 | 0 | 0 | 0 | 0 | 180 | 127.6887 | 203600 | 127.6887 | 237136.5122 | 310.0982 | 0
2651 | 4 | 0 | 1 | 0.8056 | 321.749 | 0 | 0 | 0 | 0 | 180 | 141.749 | 203600 | 141.749 | 237278.2611 | 466.1222 | 0
2652 | 4 | 0 | 1 | 0.71438 | 318.0181 | 0 | 0 | 0 | 0 | 51.5549 | 200 | 203600 | 200 | 237478.2611 | 510.81 | 66.4632
2653 | 4 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 0 | 200 | 203600 | 200 | 237678.2611 | 510.81 | 129.7
2654 | 4 | 0 | 1 | 0.76939 | 320.2679 | 0 | 0 | 0 | 0 | 0 | 200 | 203600 | 200 | 237878.2611 | 510.81 | 120.2679
2655 | 4 | 0 | 1 | 0.68366 | 316.7617 | 0 | 0 | 0 | 0 | 0 | 200 | 203600 | 200 | 238078.2611 | 510.81 | 116.7617
2656 | 4 | 0 | 0.99146 | 0.49449 | 306.5573 | 0 | 0 | 0 | 0 | 0 | 200 | 203600 | 200 | 238278.2611 | 510.81 | 106.5573
2657 | 4 | 0 | 0.66637 | 0.59902 | 216.9471 | 0 | 0 | 0 | 0 | 0 | 200 | 203600 | 200 | 238478.2611 | 510.81 | 16.9471
2658 | 4 | 0 | 0.33204 | 0.63424 | 121.8327 | 0 | 0 | 0 | 0 | 0 | 121.8327 | 203600 | 121.8327 | 238600.0938 | 510.81 | 0
2659 | 4 | 0 | 0.054946 | 0.39255 | 31.9238 | 0 | 0 | 0 | 0 | 0 | 31.9238 | 203600 | 31.9238 | 238632.0177 | 510.81 | 0
2660 | 4 | 1 | 0 | 0.40885 | 16.7219 | 200 | 16.7219 | 180 | 196.7219 | 0 | 0 | 203400 | 196.7219 | 238828.7396 | 330.81 | 0
2661 | 4 | 1 | 0 | 0.51169 | 20.928 | 200 | 20.928 | 179.072 | 200 | 0 | 0 | 203200 | 200 | 239028.7396 | 151.738 | 0
2662 | 4 | 0 | 0 | 0.34717 | 14.1991 | 0 | 0 | 0 | 0 | 14.1991 | 0 | 203200 | 0 | 239028.7396 | 164.0458 | 0
2663 | 4 | 0 | 0 | 0.29429 | 12.0366 | 0 | 0 | 0 | 0 | 12.0366 | 0 | 203200 | 0 | 239028.7396 | 174.4791 | 0
2664 | 4 | 0 | 0 | 0.34459 | 14.0938 | 0 | 0 | 0 | 0 | 14.0938 | 0 | 203200 | 0 | 239028.7396 | 186.6956 | 0
2665 | 4 | 0 | 0 | 0.32205 | 13.1717 | 0 | 0 | 0 | 0 | 13.1717 | 0 | 203200 | 0 | 239028.7396 | 198.1128 | 0
2666 | 4 | 0 | 0 | 0.38681 | 15.8204 | 0 | 0 | 0 | 0 | 15.8204 | 0 | 203200 | 0 | 239028.7396 | 211.8259 | 0
2667 | 4 | 0 | 0 | 0.2848 | 11.6483 | 0 | 0 | 0 | 0 | 11.6483 | 0 | 203200 | 0 | 239028.7396 | 221.9226 | 0
2668 | 4 | 0 | 0 | 0.32177 | 13.1602 | 0 | 0 | 0 | 0 | 13.1602 | 0 | 203200 | 0 | 239028.7396 | 233.3299 | 0
2669 | 4 | 0 | 0 | 0.34849 | 14.2531 | 0 | 0 | 0 | 0 | 14.2531 | 0 | 203200 | 0 | 239028.7396 | 245.6845 | 0
2670 | 4 | 0 | 0 | 0.31253 | 12.7825 | 0 | 0 | 0 | 0 | 12.7825 | 0 | 203200 | 0 | 239028.7396 | 256.7643 | 0
2671 | 4 | 0 | 0.064696 | 0.35634 | 33.2585 | 0 | 0 | 0 | 0 | 33.2585 | 0 | 203200 | 0 | 239028.7396 | 285.5928 | 0
2672 | 4 | 1 | 0.39096 | 0.45632 | 131.5715 | 200 | 131.5715 | 68.4285 | 200 | 0 | 0 | 203000 | 200 | 239228.7396 | 217.1643 | 0
2673 | 4 | 1 | 0.78461 | 0.57213 | 249.9966 | 200 | 200 | 0 | 200 | 49.9966 | 0 | 202800 | 200 | 239428.7396 | 260.5013 | 0
2674 | 4 | 0 | 1 | 0.6862 | 316.8657 | 0 | 0 | 0 | 0 | 180 | 136.8657 | 202800 | 136.8657 | 239565.6053 | 416.5253 | 0
2675 | 4 | 0 | 1 | 0.69014 | 317.0269 | 0 | 0 | 0 | 0 | 108.7733 | 200 | 202800 | 200 | 239765.6053 | 510.81 | 8.2536
2676 | 4 | 0 | 1 | 0.83902 | 323.1159 | 0 | 0 | 0 | 0 | 0 | 200 | 202800 | 200 | 239965.6053 | 510.81 | 123.1159
2677 | 4 | 0 | 1 | 0.5818 | 312.5957 | 0 | 0 | 0 | 0 | 0 | 200 | 202800 | 200 | 240165.6053 | 510.81 | 112.5957
2678 | 4 | 0 | 1 | 0.93428 | 327.0119 | 0 | 0 | 0 | 0 | 0 | 200 | 202800 | 200 | 240365.6053 | 510.81 | 127.0119
2679 | 4 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 0 | 200 | 202800 | 200 | 240565.6053 | 510.81 | 129.7
2680 | 4 | 0 | 1 | 0.86139 | 324.0309 | 0 | 0 | 0 | 0 | 0 | 200 | 202800 | 200 | 240765.6053 | 510.81 | 124.0309
2681 | 4 | 0 | 0.78461 | 0.78765 | 258.811 | 0 | 0 | 0 | 0 | 0 | 200 | 202800 | 200 | 240965.6053 | 510.81 | 58.811
2682 | 4 | 0 | 0.39096 | 0.55472 | 135.5961 | 0 | 0 | 0 | 0 | 0 | 135.5961 | 202800 | 135.5961 | 241101.2013 | 510.81 | 0
2683 | 4 | 0 | 0.064696 | 0.53418 | 40.5321 | 0 | 0 | 0 | 0 | 0 | 40.5321 | 202800 | 40.5321 | 241141.7334 | 510.81 | 0
2684 | 4 | 1 | 0 | 0.54512 | 22.2956 | 200 | 22.2956 | 177.7044 | 200 | 0 | 0 | 202600 | 200 | 241341.7334 | 333.1056 | 0
2685 | 4 | 1 | 0 | 0.52331 | 21.4033 | 200 | 21.4033 | 178.5967 | 200 | 0 | 0 | 202400 | 200 | 241541.7334 | 154.5089 | 0
2686 | 4 | 0 | 0 | 0.46171 | 18.8839 | 0 | 0 | 0 | 0 | 18.8839 | 0 | 202400 | 0 | 241541.7334 | 170.8774 | 0
2687 | 4 | 0 | 0 | 0.58596 | 23.966 | 0 | 0 | 0 | 0 | 23.966 | 0 | 202400 | 0 | 241541.7334 | 191.6511 | 0
2688 | 4 | 0 | 0 | 0.62826 | 25.6957 | 0 | 0 | 0 | 0 | 25.6957 | 0 | 202400 | 0 | 241541.7334 | 213.9242 | 0
2689 | 4 | 0 | 0 | 0.59573 | 24.3655 | 0 | 0 | 0 | 0 | 24.3655 | 0 | 202400 | 0 | 241541.7334 | 235.0442 | 0
2690 | 4 | 0 | 0 | 0.84706 | 34.6448 | 0 | 0 | 0 | 0 | 34.6448 | 0 | 202400 | 0 | 241541.7334 | 265.0743 | 0
2691 | 4 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 202400 | 0 | 241541.7334 | 300.5264 | 0
2692 | 4 | 0 | 0 | 0.88566 | 36.2235 | 0 | 0 | 0 | 0 | 36.2235 | 0 | 202400 | 0 | 241541.7334 | 331.9249 | 0
2693 | 4 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 202400 | 0 | 241541.7334 | 367.3771 | 0
2694 | 4 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 202400 | 0 | 241541.7334 | 402.8292 | 0
2695 | 4 | 0 | 0.059974 | 0.9133 | 54.6744 | 0 | 0 | 0 | 0 | 54.6744 | 0 | 202400 | 0 | 241541.7334 | 450.221 | 0
2696 | 4 | 1 | 0.36242 | 1 | 145.5669 | 200 | 145.5669 | 54.4331 | 200 | 0 | 0 | 202200 | 200 | 241741.7334 | 395.7879 | 0
2697 | 4 | 1 | 0.72735 | 1 | 250.9572 | 200 | 200 | 0 | 200 | 50.9572 | 0 | 202000 | 200 | 241941.7334 | 439.9576 | 0
2698 | 4 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 81.7402 | 200 | 202000 | 200 | 242141.7334 | 510.81 | 47.9598
2699 | 4 | 0 | 1 | 0.90672 | 325.8849 | 0 | 0 | 0 | 0 | 0 | 200 | 202000 | 200 | 242341.7334 | 510.81 | 125.8849
2700 | 4 | 0 | 1 | 0.75419 | 319.6466 | 0 | 0 | 0 | 0 | 0 | 200 | 202000 | 200 | 242541.7334 | 510.81 | 119.6466
2701 | 4 | 0 | 1 | 0.55395 | 311.4564 | 0 | 0 | 0 | 0 | 0 | 200 | 202000 | 200 | 242741.7334 | 510.81 | 111.4564
2702 | 4 | 0 | 1 | 0.46851 | 307.9622 | 0 | 0 | 0 | 0 | 0 | 200 | 202000 | 200 | 242941.7334 | 510.81 | 107.9622
2703 | 4 | 0 | 1 | 0.47282 | 308.1384 | 0 | 0 | 0 | 0 | 0 | 200 | 202000 | 200 | 243141.7334 | 510.81 | 108.1384
2704 | 4 | 0 | 1 | 0.58549 | 312.7467 | 0 | 0 | 0 | 0 | 0 | 200 | 202000 | 200 | 243341.7334 | 510.81 | 112.7467
2705 | 4 | 0 | 0.72735 | 0.45871 | 228.8185 | 0 | 0 | 0 | 0 | 0 | 200 | 202000 | 200 | 243541.7334 | 510.81 | 28.8185
2706 | 4 | 0 | 0.36242 | 0.49417 | 124.8786 | 0 | 0 | 0 | 0 | 0 | 124.8786 | 202000 | 124.8786 | 243666.6121 | 510.81 | 0
2707 | 4 | 0 | 0.059974 | 0.61996 | 42.6767 | 0 | 0 | 0 | 0 | 0 | 42.6767 | 202000 | 42.6767 | 243709.2887 | 510.81 | 0
2708 | 4 | 1 | 0 | 1 | 40.9 | 200 | 40.9 | 159.1 | 200 | 0 | 0 | 201800 | 200 | 243909.2887 | 351.71 | 0
2709 | 4 | 1 | 0 | 0.63939 | 26.1509 | 200 | 26.1509 | 173.8491 | 200 | 0 | 0 | 201600 | 200 | 244109.2887 | 177.8609 | 0
2710 | 4 | 0 | 0 | 0.53319 | 21.8076 | 0 | 0 | 0 | 0 | 21.8076 | 0 | 201600 | 0 | 244109.2887 | 196.7637 | 0
2711 | 4 | 0 | 0 | 0.39781 | 16.2703 | 0 | 0 | 0 | 0 | 16.2703 | 0 | 201600 | 0 | 244109.2887 | 210.8668 | 0
2712 | 4 | 0 | 0 | 0.48676 | 19.9083 | 0 | 0 | 0 | 0 | 19.9083 | 0 | 201600 | 0 | 244109.2887 | 228.1233 | 0
2713 | 4 | 0 | 0 | 0.68268 | 27.9214 | 0 | 0 | 0 | 0 | 27.9214 | 0 | 201600 | 0 | 244109.2887 | 252.3256 | 0
2714 | 4 | 0 | 0 | 0.56756 | 23.213 | 0 | 0 | 0 | 0 | 23.213 | 0 | 201600 | 0 | 244109.2887 | 272.4467 | 0
2715 | 4 | 0 | 0 | 0.45933 | 18.7868 | 0 | 0 | 0 | 0 | 18.7868 | 0 | 201600 | 0 | 244109.2887 | 288.7311 | 0
2716 | 4 | 0 | 0 | 0.34827 | 14.2442 | 0 | 0 | 0 | 0 | 14.2442 | 0 | 201600 | 0 | 244109.2887 | 301.078 | 0
2717 | 4 | 0 | 0 | 0.25586 | 10.4648 | 0 | 0 | 0 | 0 | 10.4648 | 0 | 201600 | 0 | 244109.2887 | 310.1488 | 0
2718 | 4 | 0 | 0 | 0.24256 | 9.9205 | 0 | 0 | 0 | 0 | 9.9205 | 0 | 201600 | 0 | 244109.2887 | 318.748 | 0
2719 | 4 | 0 | 0.051161 | 0.24693 | 24.8748 | 0 | 0 | 0 | 0 | 24.8748 | 0 | 201600 | 0 | 244109.2887 | 340.3095 | 0
2720 | 4 | 1 | 0.30917 | 0.20278 | 97.5819 | 200 | 97.5819 | 102.4181 | 200 | 0 | 0 | 201400 | 200 | 244309.2887 | 237.8913 | 0
2721 | 4 | 1 | 0.62047 | 0.27664 | 190.5073 | 200 | 190.5073 | 9.4927 | 200 | 0 | 0 | 201200 | 200 | 244509.2887 | 228.3986 | 0
2722 | 4 | 0 | 0.92317 | 0.34059 | 280.5421 | 0 | 0 | 0 | 0 | 180 | 100.5421 | 201200 | 100.5421 | 244609.8309 | 384.4226 | 0
2723 | 4 | 0 | 1 | 0.27676 | 300.1193 | 0 | 0 | 0 | 0 | 145.8091 | 154.3102 | 201200 | 154.3102 | 244764.141 | 510.81 | 0
2724 | 4 | 0 | 1 | 0.49512 | 309.0503 | 0 | 0 | 0 | 0 | 0 | 200 | 201200 | 200 | 244964.141 | 510.81 | 109.0503
2725 | 4 | 0 | 1 | 0.45353 | 307.3495 | 0 | 0 | 0 | 0 | 0 | 200 | 201200 | 200 | 245164.141 | 510.81 | 107.3495
2726 | 4 | 0 | 1 | 0.63357 | 314.7131 | 0 | 0 | 0 | 0 | 0 | 200 | 201200 | 200 | 245364.141 | 510.81 | 114.7131
2727 | 4 | 0 | 1 | 0.75216 | 319.5634 | 0 | 0 | 0 | 0 | 0 | 200 | 201200 | 200 | 245564.141 | 510.81 | 119.5634
2728 | 4 | 0 | 0.92317 | 0.62398 | 292.1328 | 0 | 0 | 0 | 0 | 0 | 200 | 201200 | 200 | 245764.141 | 510.81 | 92.1328
2729 | 4 | 0 | 0.62047 | 0.34415 | 193.2682 | 0 | 0 | 0 | 0 | 0 | 193.2682 | 201200 | 193.2682 | 245957.4093 | 510.81 | 0
2730 | 4 | 0 | 0.30917 | 0.51015 | 110.1531 | 0 | 0 | 0 | 0 | 0 | 110.1531 | 201200 | 110.1531 | 246067.5624 | 510.81 | 0
2731 | 4 | 0 | 0.051161 | 0.48594 | 34.6501 | 0 | 0 | 0 | 0 | 0 | 34.6501 | 201200 | 34.6501 | 246102.2125 | 510.81 | 0
2732 | 4 | 1 | 0 | 0.55425 | 22.6687 | 200 | 22.6687 | 177.3313 | 200 | 0 | 0 | 201000 | 200 | 246302.2125 | 333.4787 | 0
2733 | 4 | 1 | 0 | 0.34744 | 14.2101 | 200 | 14.2101 | 180 | 194.2101 | 0 | 0 | 200800 | 194.2101 | 246496.4226 | 153.4787 | 0
2734 | 4 | 0 | 0 | 0.39486 | 16.1499 | 0 | 0 | 0 | 0 | 16.1499 | 0 | 200800 | 0 | 246496.4226 | 167.4774 | 0
2735 | 4 | 0 | 0 | 0.34784 | 14.2267 | 0 | 0 | 0 | 0 | 14.2267 | 0 | 200800 | 0 | 246496.4226 | 179.8091 | 0
2736 | 4 | 0 | 0 | 0.26017 | 10.6411 | 0 | 0 | 0 | 0 | 10.6411 | 0 | 200800 | 0 | 246496.4226 | 189.0328 | 0
2737 | 4 | 0 | 0 | 0.28169 | 11.5212 | 0 | 0 | 0 | 0 | 11.5212 | 0 | 200800 | 0 | 246496.4226 | 199.0193 | 0
2738 | 4 | 0 | 0 | 0.20021 | 8.1885 | 0 | 0 | 0 | 0 | 8.1885 | 0 | 200800 | 0 | 246496.4226 | 206.1172 | 0
2739 | 4 | 0 | 0 | 0.23252 | 9.51 | 0 | 0 | 0 | 0 | 9.51 | 0 | 200800 | 0 | 246496.4226 | 214.3605 | 0
2740 | 4 | 0 | 0 | 0.17945 | 7.3394 | 0 | 0 | 0 | 0 | 7.3394 | 0 | 200800 | 0 | 246496.4226 | 220.7222 | 0
2741 | 4 | 0 | 0 | 0.15109 | 6.1795 | 0 | 0 | 0 | 0 | 6.1795 | 0 | 200800 | 0 | 246496.4226 | 226.0786 | 0
2742 | 4 | 0 | 0 | 0.17792 | 7.2768 | 0 | 0 | 0 | 0 | 7.2768 | 0 | 200800 | 0 | 246496.4226 | 232.3862 | 0
2743 | 4 | 0 | 0.057126 | 0.17522 | 23.6645 | 0 | 0 | 0 | 0 | 23.6645 | 0 | 200800 | 0 | 246496.4226 | 252.8986 | 0
2744 | 4 | 1 | 0.34521 | 0.20176 | 107.95 | 200 | 107.95 | 92.05 | 200 | 0 | 0 | 200600 | 200 | 246696.4226 | 160.8486 | 0
2745 | 4 | 1 | 0.69281 | 0.35673 | 214.6742 | 200 | 200 | 0 | 200 | 14.6742 | 0 | 200400 | 200 | 246896.4226 | 173.5682 | 0
2746 | 4 | 0 | 1 | 0.28366 | 300.4018 | 0 | 0 | 0 | 0 | 180 | 120.4018 | 200400 | 120.4018 | 247016.8244 | 329.5922 | 0
2747 | 4 | 0 | 1 | 0.31188 | 301.5558 | 0 | 0 | 0 | 0 | 180 | 121.5558 | 200400 | 121.5558 | 247138.3802 | 485.6162 | 0
2748 | 4 | 0 | 1 | 0.28853 | 300.6008 | 0 | 0 | 0 | 0 | 29.0653 | 200 | 200400 | 200 | 247338.3802 | 510.81 | 71.5354
2749 | 4 | 0 | 1 | 0.26285 | 299.5505 | 0 | 0 | 0 | 0 | 0 | 200 | 200400 | 200 | 247538.3802 | 510.81 | 99.5505
2750 | 4 | 0 | 1 | 0.33621 | 302.551 | 0 | 0 | 0 | 0 | 0 | 200 | 200400 | 200 | 247738.3802 | 510.81 | 102.551
2751 | 4 | 0 | 1 | 0.28675 | 300.5279 | 0 | 0 | 0 | 0 | 0 | 200 | 200400 | 200 | 247938.3802 | 510.81 | 100.5279
2752 | 4 | 0 | 1 | 0.28249 | 300.3537 | 0 | 0 | 0 | 0 | 0 | 200 | 200400 | 200 | 248138.3802 | 510.81 | 100.3537
2753 | 4 | 0 | 0.69281 | 0.32582 | 213.4099 | 0 | 0 | 0 | 0 | 0 | 200 | 200400 | 200 | 248338.3802 | 510.81 | 13.4099
2754 | 4 | 0 | 0.34521 | 0.24522 | 109.7273 | 0 | 0 | 0 | 0 | 0 | 109.7273 | 200400 | 109.7273 | 248448.1074 | 510.81 | 0
2755 | 4 | 0 | 0.057126 | 0.22217 | 25.5847 | 0 | 0 | 0 | 0 | 0 | 25.5847 | 200400 | 25.5847 | 248473.6921 | 510.81 | 0
2756 | 4 | 1 | 0 | 0.15691 | 6.4178 | 200 | 6.4178 | 180 | 186.4178 | 0 | 0 | 200200 | 186.4178 | 248660.1099 | 330.81 | 0
2757 | 4 | 1 | 0 | 0.21498 | 8.7928 | 200 | 8.7928 | 180 | 188.7928 | 0 | 0 | 200000 | 188.7928 | 248848.9027 | 150.81 | 0
2758 | 4 | 0 | 0 | 0.2385 | 9.7548 | 0 | 0 | 0 | 0 | 9.7548 | 0 | 200000 | 0 | 248848.9027 | 159.2654 | 0
2759 | 4 | 0 | 0 | 0.25415 | 10.3945 | 0 | 0 | 0 | 0 | 10.3945 | 0 | 200000 | 0 | 248848.9027 | 168.2754 | 0
2760 | 4 | 0 | 0 | 0.32715 | 13.3805 | 0 | 0 | 0 | 0 | 13.3805 | 0 | 200000 | 0 | 248848.9027 | 179.8736 | 0
2761 | 4 | 0 | 0 | 0.29874 | 12.2184 | 0 | 0 | 0 | 0 | 12.2184 | 0 | 200000 | 0 | 248848.9027 | 190.4645 | 0
2762 | 4 | 0 | 0 | 0.299 | 12.2291 | 0 | 0 | 0 | 0 | 12.2291 | 0 | 200000 | 0 | 248848.9027 | 201.0647 | 0
2763 | 4 | 0 | 0 | 0.24583 | 10.0545 | 0 | 0 | 0 | 0 | 10.0545 | 0 | 200000 | 0 | 248848.9027 | 209.78 | 0
2764 | 4 | 0 | 0 | 0.19004 | 7.7727 | 0 | 0 | 0 | 0 | 7.7727 | 0 | 200000 | 0 | 248848.9027 | 216.5174 | 0
2765 | 4 | 0 | 0 | 0.20777 | 8.4977 | 0 | 0 | 0 | 0 | 8.4977 | 0 | 200000 | 0 | 248848.9027 | 223.8832 | 0
2766 | 4 | 0 | 0 | 0.22469 | 9.1899 | 0 | 0 | 0 | 0 | 9.1899 | 0 | 200000 | 0 | 248848.9027 | 231.849 | 0
2767 | 4 | 0 | 0.049577 | 0.23161 | 23.7907 | 0 | 0 | 0 | 0 | 23.7907 | 0 | 200000 | 0 | 248848.9027 | 252.4708 | 0
2768 | 4 | 1 | 0.29959 | 0.51266 | 107.4907 | 200 | 107.4907 | 92.5093 | 200 | 0 | 0 | 199800 | 200 | 249048.9027 | 159.9615 | 0
2769 | 4 | 1 | 0.60126 | 0.54014 | 195.7349 | 200 | 195.7349 | 4.2651 | 200 | 0 | 0 | 199600 | 200 | 249248.9027 | 155.6964 | 0
2770 | 4 | 0 | 0.89458 | 0.30516 | 270.8367 | 0 | 0 | 0 | 0 | 180 | 90.8367 | 199600 | 90.8367 | 249339.7393 | 311.7204 | 0
2771 | 4 | 0 | 1 | 0.40716 | 305.453 | 0 | 0 | 0 | 0 | 180 | 125.453 | 199600 | 125.453 | 249465.1923 | 467.7444 | 0
2772 | 4 | 0 | 1 | 0.34434 | 302.8835 | 0 | 0 | 0 | 0 | 49.6834 | 200 | 199600 | 200 | 249665.1923 | 510.81 | 53.2001
2773 | 4 | 0 | 1 | 0.38658 | 304.611 | 0 | 0 | 0 | 0 | 0 | 200 | 199600 | 200 | 249865.1923 | 510.81 | 104.611
2774 | 4 | 0 | 1 | 0.35918 | 303.4903 | 0 | 0 | 0 | 0 | 0 | 200 | 199600 | 200 | 250065.1923 | 510.81 | 103.4903
2775 | 4 | 0 | 1 | 0.44201 | 306.8782 | 0 | 0 | 0 | 0 | 0 | 200 | 199600 | 200 | 250265.1923 | 510.81 | 106.8782
2776 | 4 | 0 | 0.89458 | 0.34903 | 272.6308 | 0 | 0 | 0 | 0 | 0 | 200 | 199600 | 200 | 250465.1923 | 510.81 | 72.6308
2777 | 4 | 0 | 0.60126 | 0.26854 | 184.6264 | 0 | 0 | 0 | 0 | 0 | 184.6264 | 199600 | 184.6264 | 250649.8188 | 510.81 | 0
2778 | 4 | 0 | 0.29959 | 0.37077 | 101.6873 | 0 | 0 | 0 | 0 | 0 | 101.6873 | 199600 | 101.6873 | 250751.506 | 510.81 | 0
2779 | 4 | 0 | 0.049577 | 0.27758 | 25.6707 | 0 | 0 | 0 | 0 | 0 | 25.6707 | 199600 | 25.6707 | 250777.1768 | 510.81 | 0
2780 | 4 | 1 | 0 | 0.19657 | 8.0395 | 200 | 8.0395 | 180 | 188.0395 | 0 | 0 | 199400 | 188.0395 | 250965.2163 | 330.81 | 0
2781 | 4 | 1 | 0 | 0.144 | 5.8894 | 200 | 5.8894 | 180 | 185.8894 | 0 | 0 | 199200 | 185.8894 | 251151.1057 | 150.81 | 0
2782 | 4 | 0 | 0 | 0.095759 | 3.9165 | 0 | 0 | 0 | 0 | 3.9165 | 0 | 199200 | 0 | 251151.1057 | 154.2049 | 0
2783 | 4 | 0 | 0 | 0.075038 | 3.0691 | 0 | 0 | 0 | 0 | 3.0691 | 0 | 199200 | 0 | 251151.1057 | 156.8651 | 0
2784 | 4 | 0 | 0 | 0.096239 | 3.9362 | 0 | 0 | 0 | 0 | 3.9362 | 0 | 199200 | 0 | 251151.1057 | 160.277 | 0
2785 | 4 | 0 | 0 | 0.084681 | 3.4635 | 0 | 0 | 0 | 0 | 3.4635 | 0 | 199200 | 0 | 251151.1057 | 163.2791 | 0
2786 | 4 | 0 | 0 | 0.074515 | 3.0477 | 0 | 0 | 0 | 0 | 3.0477 | 0 | 199200 | 0 | 251151.1057 | 165.9208 | 0
2787 | 4 | 0 | 0 | 0.12418 | 5.0791 | 0 | 0 | 0 | 0 | 5.0791 | 0 | 199200 | 0 | 251151.1057 | 170.3234 | 0
2788 | 4 | 0 | 0 | 0.16155 | 6.6074 | 0 | 0 | 0 | 0 | 6.6074 | 0 | 199200 | 0 | 251151.1057 | 176.0506 | 0
2789 | 4 | 0 | 0 | 0.16975 | 6.9428 | 0 | 0 | 0 | 0 | 6.9428 | 0 | 199200 | 0 | 251151.1057 | 182.0687 | 0
2790 | 4 | 0 | 0 | 0.15185 | 6.2107 | 0 | 0 | 0 | 0 | 6.2107 | 0 | 199200 | 0 | 251151.1057 | 187.4521 | 0
2791 | 4 | 0 | 0.05096 | 0.12754 | 19.9334 | 0 | 0 | 0 | 0 | 19.9334 | 0 | 199200 | 0 | 251151.1057 | 204.7304 | 0
2792 | 4 | 1 | 0.30795 | 0.12248 | 93.9461 | 200 | 93.9461 | 106.0539 | 200 | 0 | 0 | 199000 | 200 | 251351.1057 | 98.6765 | 0
2793 | 4 | 1 | 0.61803 | 0.13498 | 184.0084 | 200 | 184.0084 | 15.9916 | 200 | 0 | 0 | 198800 | 200 | 251551.1057 | 82.6849 | 0
2794 | 4 | 0 | 0.91954 | 0.11249 | 270.1646 | 0 | 0 | 0 | 0 | 180 | 90.1646 | 198800 | 90.1646 | 251641.2703 | 238.7089 | 0
2795 | 4 | 0 | 1 | 0.099138 | 292.8547 | 0 | 0 | 0 | 0 | 180 | 112.8547 | 198800 | 112.8547 | 251754.125 | 394.7329 | 0
2796 | 4 | 0 | 1 | 0.13922 | 294.4941 | 0 | 0 | 0 | 0 | 133.9145 | 160.5796 | 198800 | 160.5796 | 251914.7046 | 510.81 | 0
2797 | 4 | 0 | 1 | 0.21284 | 297.5052 | 0 | 0 | 0 | 0 | 0 | 200 | 198800 | 200 | 252114.7046 | 510.81 | 97.5052
2798 | 4 | 0 | 1 | 0.18554 | 296.3888 | 0 | 0 | 0 | 0 | 0 | 200 | 198800 | 200 | 252314.7046 | 510.81 | 96.3888
2799 | 4 | 0 | 1 | 0.22058 | 297.8217 | 0 | 0 | 0 | 0 | 0 | 200 | 198800 | 200 | 252514.7046 | 510.81 | 97.8217
2800 | 4 | 0 | 0.91954 | 0.23853 | 275.3195 | 0 | 0 | 0 | 0 | 0 | 200 | 198800 | 200 | 252714.7046 | 510.81 | 75.3195
2801 | 4 | 0 | 0.61803 | 0.21636 | 187.3372 | 0 | 0 | 0 | 0 | 0 | 187.3372 | 198800 | 187.3372 | 252902.0418 | 510.81 | 0
2802 | 4 | 0 | 0.30795 | 0.3338 | 102.5892 | 0 | 0 | 0 | 0 | 0 | 102.5892 | 198800 | 102.5892 | 253004.631 | 510.81 | 0
2803 | 4 | 0 | 0.05096 | 0.28944 | 26.5555 | 0 | 0 | 0 | 0 | 0 | 26.5555 | 198800 | 26.5555 | 253031.1864 | 510.81 | 0
2804 | 4 | 1 | 0 | 0.20295 | 8.3007 | 200 | 8.3007 | 180 | 188.3007 | 0 | 0 | 198600 | 188.3007 | 253219.4871 | 330.81 | 0
2805 | 4 | 1 | 0 | 0.14911 | 6.0986 | 200 | 6.0986 | 180 | 186.0986 | 0 | 0 | 198400 | 186.0986 | 253405.5858 | 150.81 | 0
2806 | 4 | 0 | 0 | 0.13896 | 5.6833 | 0 | 0 | 0 | 0 | 5.6833 | 0 | 198400 | 0 | 253405.5858 | 155.7363 | 0
2807 | 4 | 0 | 0 | 0.12837 | 5.2503 | 0 | 0 | 0 | 0 | 5.2503 | 0 | 198400 | 0 | 253405.5858 | 160.2873 | 0
2808 | 4 | 0 | 0 | 0.14647 | 5.9906 | 0 | 0 | 0 | 0 | 5.9906 | 0 | 198400 | 0 | 253405.5858 | 165.4799 | 0
2809 | 4 | 0 | 0 | 0.1356 | 5.546 | 0 | 0 | 0 | 0 | 5.546 | 0 | 198400 | 0 | 253405.5858 | 170.2871 | 0
2810 | 4 | 0 | 0 | 0.12947 | 5.2953 | 0 | 0 | 0 | 0 | 5.2953 | 0 | 198400 | 0 | 253405.5858 | 174.8771 | 0
2811 | 4 | 0 | 0 | 0.15468 | 6.3262 | 0 | 0 | 0 | 0 | 6.3262 | 0 | 198400 | 0 | 253405.5858 | 180.3607 | 0
2812 | 4 | 0 | 0 | 0.12407 | 5.0744 | 0 | 0 | 0 | 0 | 5.0744 | 0 | 198400 | 0 | 253405.5858 | 184.7591 | 0
2813 | 4 | 0 | 0 | 0.10749 | 4.3965 | 0 | 0 | 0 | 0 | 4.3965 | 0 | 198400 | 0 | 253405.5858 | 188.57 | 0
2814 | 4 | 0 | 0 | 0.1332 | 5.448 | 0 | 0 | 0 | 0 | 5.448 | 0 | 198400 | 0 | 253405.5858 | 193.2923 | 0
2815 | 4 | 0 | 0.056021 | 0.088239 | 19.7878 | 0 | 0 | 0 | 0 | 19.7878 | 0 | 198400 | 0 | 253405.5858 | 210.4444 | 0
2816 | 4 | 1 | 0.33853 | 0.09375 | 101.6027 | 200 | 101.6027 | 98.3973 | 200 | 0 | 0 | 198200 | 200 | 253605.5858 | 112.0471 | 0
2817 | 4 | 1 | 0.67941 | 0.077895 | 199.3981 | 200 | 199.3981 | 0.60193 | 200 | 0 | 0 | 198000 | 200 | 253805.5858 | 111.4452 | 0
2818 | 4 | 0 | 1 | 0.092989 | 292.6033 | 0 | 0 | 0 | 0 | 180 | 112.6033 | 198000 | 112.6033 | 253918.189 | 267.4692 | 0
2819 | 4 | 0 | 1 | 0.1027 | 293.0005 | 0 | 0 | 0 | 0 | 180 | 113.0005 | 198000 | 113.0005 | 254031.1895 | 423.4932 | 0
2820 | 4 | 0 | 1 | 0.14981 | 294.9273 | 0 | 0 | 0 | 0 | 100.7347 | 194.1926 | 198000 | 194.1926 | 254225.3822 | 510.81 | 0
2821 | 4 | 0 | 1 | 0.19929 | 296.9509 | 0 | 0 | 0 | 0 | 0 | 200 | 198000 | 200 | 254425.3822 | 510.81 | 96.9509
2822 | 4 | 0 | 1 | 0.21744 | 297.6934 | 0 | 0 | 0 | 0 | 0 | 200 | 198000 | 200 | 254625.3822 | 510.81 | 97.6934
2823 | 4 | 0 | 1 | 0.21457 | 297.576 | 0 | 0 | 0 | 0 | 0 | 200 | 198000 | 200 | 254825.3822 | 510.81 | 97.576
2824 | 4 | 0 | 1 | 0.17895 | 296.119 | 0 | 0 | 0 | 0 | 0 | 200 | 198000 | 200 | 255025.3822 | 510.81 | 96.119
2825 | 4 | 0 | 0.67941 | 0.17305 | 203.2897 | 0 | 0 | 0 | 0 | 0 | 200 | 198000 | 200 | 255225.3822 | 510.81 | 3.2897
2826 | 4 | 0 | 0.33853 | 0.22642 | 107.029 | 0 | 0 | 0 | 0 | 0 | 107.029 | 198000 | 107.029 | 255332.4112 | 510.81 | 0
2827 | 4 | 0 | 0.056021 | 0.20923 | 24.7365 | 0 | 0 | 0 | 0 | 0 | 24.7365 | 198000 | 24.7365 | 255357.1477 | 510.81 | 0
2828 | 4 | 1 | 0 | 0.18679 | 7.6395 | 200 | 7.6395 | 180 | 187.6395 | 0 | 0 | 197800 | 187.6395 | 255544.7872 | 330.81 | 0
2829 | 4 | 1 | 0 | 0.20372 | 8.3324 | 200 | 8.3324 | 180 | 188.3324 | 0 | 0 | 197600 | 188.3324 | 255733.1196 | 150.81 | 0
2830 | 4 | 0 | 0 | 0.18547 | 7.5858 | 0 | 0 | 0 | 0 | 7.5858 | 0 | 197600 | 0 | 255733.1196 | 157.3854 | 0
2831 | 4 | 0 | 0 | 0.1073 | 4.3886 | 0 | 0 | 0 | 0 | 4.3886 | 0 | 197600 | 0 | 255733.1196 | 161.1894 | 0
2832 | 4 | 0 | 0 | 0.15645 | 6.3987 | 0 | 0 | 0 | 0 | 6.3987 | 0 | 197600 | 0 | 255733.1196 | 166.7358 | 0
2833 | 4 | 0 | 0 | 0.18108 | 7.4061 | 0 | 0 | 0 | 0 | 7.4061 | 0 | 197600 | 0 | 255733.1196 | 173.1554 | 0
2834 | 4 | 0 | 0 | 0.18994 | 7.7687 | 0 | 0 | 0 | 0 | 7.7687 | 0 | 197600 | 0 | 255733.1196 | 179.8893 | 0
2835 | 4 | 0 | 0 | 0.17747 | 7.2584 | 0 | 0 | 0 | 0 | 7.2584 | 0 | 197600 | 0 | 255733.1196 | 186.1809 | 0
2836 | 4 | 0 | 0 | 0.22754 | 9.3066 | 0 | 0 | 0 | 0 | 9.3066 | 0 | 197600 | 0 | 255733.1196 | 194.2478 | 0
2837 | 4 | 0 | 0 | 0.22839 | 9.3413 | 0 | 0 | 0 | 0 | 9.3413 | 0 | 197600 | 0 | 255733.1196 | 202.3449 | 0
2838 | 4 | 0 | 0 | 0.15887 | 6.4978 | 0 | 0 | 0 | 0 | 6.4978 | 0 | 197600 | 0 | 255733.1196 | 207.9771 | 0
2839 | 4 | 0 | 0.054308 | 0.12262 | 20.6992 | 0 | 0 | 0 | 0 | 20.6992 | 0 | 197600 | 0 | 255733.1196 | 225.9192 | 0
2840 | 4 | 1 | 0.32818 | 0.11965 | 99.6726 | 200 | 99.6726 | 100.3274 | 200 | 0 | 0 | 197400 | 200 | 255933.1196 | 125.5918 | 0
2841 | 4 | 1 | 0.65863 | 0.15312 | 196.4757 | 200 | 196.4757 | 3.5243 | 200 | 0 | 0 | 197200 | 200 | 256133.1196 | 122.0675 | 0
2842 | 4 | 0 | 0.97995 | 0.14376 | 288.8886 | 0 | 0 | 0 | 0 | 180 | 108.8886 | 197200 | 108.8886 | 256242.0082 | 278.0915 | 0
2843 | 4 | 0 | 1 | 0.15649 | 295.2006 | 0 | 0 | 0 | 0 | 180 | 115.2006 | 197200 | 115.2006 | 256357.2088 | 434.1155 | 0
2844 | 4 | 0 | 1 | 0.12211 | 293.7943 | 0 | 0 | 0 | 0 | 88.48 | 200 | 197200 | 200 | 256557.2088 | 510.81 | 5.3143
2845 | 4 | 0 | 1 | 0.12351 | 293.8516 | 0 | 0 | 0 | 0 | 0 | 200 | 197200 | 200 | 256757.2088 | 510.81 | 93.8516
2846 | 4 | 0 | 1 | 0.11203 | 293.3821 | 0 | 0 | 0 | 0 | 0 | 200 | 197200 | 200 | 256957.2088 | 510.81 | 93.3821
2847 | 4 | 0 | 1 | 0.080637 | 292.0981 | 0 | 0 | 0 | 0 | 0 | 200 | 197200 | 200 | 257157.2088 | 510.81 | 92.0981
2848 | 4 | 0 | 0.97995 | 0.11433 | 287.6846 | 0 | 0 | 0 | 0 | 0 | 200 | 197200 | 200 | 257357.2088 | 510.81 | 87.6846
2849 | 4 | 0 | 0.65863 | 0.12326 | 195.2545 | 0 | 0 | 0 | 0 | 0 | 195.2545 | 197200 | 195.2545 | 257552.4633 | 510.81 | 0
2850 | 4 | 0 | 0.32818 | 0.10832 | 99.2093 | 0 | 0 | 0 | 0 | 0 | 99.2093 | 197200 | 99.2093 | 257651.6726 | 510.81 | 0
2851 | 4 | 0 | 0.054308 | 0.11942 | 20.5683 | 0 | 0 | 0 | 0 | 0 | 20.5683 | 197200 | 20.5683 | 257672.2409 | 510.81 | 0
2852 | 4 | 1 | 0 | 0.11758 | 4.8091 | 200 | 4.8091 | 180 | 184.8091 | 0 | 0 | 197000 | 184.8091 | 257857.05 | 330.81 | 0
2853 | 4 | 1 | 0 | 0.10556 | 4.3174 | 200 | 4.3174 | 180 | 184.3174 | 0 | 0 | 196800 | 184.3174 | 258041.3674 | 150.81 | 0
2854 | 4 | 0 | 0 | 0.19435 | 7.949 | 0 | 0 | 0 | 0 | 7.949 | 0 | 196800 | 0 | 258041.3674 | 157.7002 | 0
2855 | 4 | 0 | 0 | 0.25033 | 10.2384 | 0 | 0 | 0 | 0 | 10.2384 | 0 | 196800 | 0 | 258041.3674 | 166.5748 | 0
2856 | 4 | 0 | 0 | 0.32712 | 13.3792 | 0 | 0 | 0 | 0 | 13.3792 | 0 | 196800 | 0 | 258041.3674 | 178.1719 | 0
2857 | 4 | 0 | 0 | 0.38522 | 15.7555 | 0 | 0 | 0 | 0 | 15.7555 | 0 | 196800 | 0 | 258041.3674 | 191.8288 | 0
2858 | 4 | 0 | 0 | 0.3638 | 14.8796 | 0 | 0 | 0 | 0 | 14.8796 | 0 | 196800 | 0 | 258041.3674 | 204.7264 | 0
2859 | 4 | 0 | 0 | 0.27024 | 11.053 | 0 | 0 | 0 | 0 | 11.053 | 0 | 196800 | 0 | 258041.3674 | 214.3072 | 0
2860 | 4 | 0 | 0 | 0.30644 | 12.5332 | 0 | 0 | 0 | 0 | 12.5332 | 0 | 196800 | 0 | 258041.3674 | 225.171 | 0
2861 | 4 | 0 | 0 | 0.35656 | 14.5834 | 0 | 0 | 0 | 0 | 14.5834 | 0 | 196800 | 0 | 258041.3674 | 237.8119 | 0
2862 | 4 | 0 | 0 | 0.40404 | 16.5252 | 0 | 0 | 0 | 0 | 16.5252 | 0 | 196800 | 0 | 258041.3674 | 252.1359 | 0
2863 | 4 | 0 | 0.054685 | 0.39349 | 31.8869 | 0 | 0 | 0 | 0 | 31.8869 | 0 | 196800 | 0 | 258041.3674 | 279.7754 | 0
2864 | 4 | 1 | 0.33047 | 0.47133 | 114.7157 | 200 | 114.7157 | 85.2843 | 200 | 0 | 0 | 196600 | 200 | 258241.3674 | 194.4912 | 0
2865 | 4 | 1 | 0.66321 | 0.40419 | 208.0668 | 200 | 200 | 0 | 200 | 8.0668 | 0 | 196400 | 200 | 258441.3674 | 201.4835 | 0
2866 | 4 | 0 | 0.98676 | 0.5407 | 307.0916 | 0 | 0 | 0 | 0 | 180 | 127.0916 | 196400 | 127.0916 | 258568.459 | 357.5075 | 0
2867 | 4 | 0 | 1 | 0.58698 | 312.8077 | 0 | 0 | 0 | 0 | 176.8603 | 135.9474 | 196400 | 135.9474 | 258704.4064 | 510.81 | 0
2868 | 4 | 0 | 1 | 0.6973 | 317.3195 | 0 | 0 | 0 | 0 | 0 | 200 | 196400 | 200 | 258904.4064 | 510.81 | 117.3195
2869 | 4 | 0 | 1 | 0.53612 | 310.7272 | 0 | 0 | 0 | 0 | 0 | 200 | 196400 | 200 | 259104.4064 | 510.81 | 110.7272
2870 | 4 | 0 | 1 | 0.62361 | 314.3058 | 0 | 0 | 0 | 0 | 0 | 200 | 196400 | 200 | 259304.4064 | 510.81 | 114.3058
2871 | 4 | 0 | 1 | 0.63135 | 314.6223 | 0 | 0 | 0 | 0 | 0 | 200 | 196400 | 200 | 259504.4064 | 510.81 | 114.6223
2872 | 4 | 0 | 0.98676 | 0.68773 | 313.1051 | 0 | 0 | 0 | 0 | 0 | 200 | 196400 | 200 | 259704.4064 | 510.81 | 113.1051
2873 | 4 | 0 | 0.66321 | 0.71573 | 220.8089 | 0 | 0 | 0 | 0 | 0 | 200 | 196400 | 200 | 259904.4064 | 510.81 | 20.8089
2874 | 4 | 0 | 0.33047 | 0.78291 | 127.4591 | 0 | 0 | 0 | 0 | 0 | 127.4591 | 196400 | 127.4591 | 260031.8655 | 510.81 | 0
2875 | 4 | 0 | 0.054685 | 0.95232 | 54.743 | 0 | 0 | 0 | 0 | 0 | 54.743 | 196400 | 54.743 | 260086.6085 | 510.81 | 0
2876 | 4 | 1 | 0 | 1 | 40.9 | 200 | 40.9 | 159.1 | 200 | 0 | 0 | 196200 | 200 | 260286.6085 | 351.71 | 0
2877 | 4 | 1 | 0 | 0.80177 | 32.7926 | 200 | 32.7926 | 167.2074 | 200 | 0 | 0 | 196000 | 200 | 260486.6085 | 184.5026 | 0
2878 | 4 | 0 | 0 | 0.68859 | 28.1634 | 0 | 0 | 0 | 0 | 28.1634 | 0 | 196000 | 0 | 260486.6085 | 208.9146 | 0
2879 | 4 | 0 | 0 | 0.74636 | 30.5261 | 0 | 0 | 0 | 0 | 30.5261 | 0 | 196000 | 0 | 260486.6085 | 235.3746 | 0
2880 | 4 | 0 | 0 | 0.56493 | 23.1056 | 0 | 0 | 0 | 0 | 23.1056 | 0 | 196000 | 0 | 260486.6085 | 255.4025 | 0
2881 | 5 | 0 | 0 | 0.46248 | 18.9156 | 0 | 0 | 0 | 0 | 18.9156 | 0 | 196000 | 0 | 260486.6085 | 271.7985 | 0
2882 | 5 | 0 | 0 | 0.51107 | 20.9029 | 0 | 0 | 0 | 0 | 20.9029 | 0 | 196000 | 0 | 260486.6085 | 289.9171 | 0
2883 | 5 | 0 | 0 | 0.47118 | 19.2714 | 0 | 0 | 0 | 0 | 19.2714 | 0 | 196000 | 0 | 260486.6085 | 306.6216 | 0
2884 | 5 | 0 | 0 | 0.50658 | 20.7192 | 0 | 0 | 0 | 0 | 20.7192 | 0 | 196000 | 0 | 260486.6085 | 324.5809 | 0
2885 | 5 | 0 | 0 | 0.85342 | 34.905 | 0 | 0 | 0 | 0 | 34.905 | 0 | 196000 | 0 | 260486.6085 | 354.8366 | 0
2886 | 5 | 0 | 0 | 0.76643 | 31.3468 | 0 | 0 | 0 | 0 | 31.3468 | 0 | 196000 | 0 | 260486.6085 | 382.0081 | 0
2887 | 5 | 0 | 0.12819 | 0.83984 | 71.3718 | 0 | 0 | 0 | 0 | 71.3718 | 0 | 196000 | 0 | 260486.6085 | 443.8731 | 0
2888 | 5 | 1 | 0.43794 | 0.54075 | 148.5948 | 200 | 148.5948 | 51.4052 | 200 | 0 | 0 | 195800 | 200 | 260686.6085 | 392.4679 | 0
2889 | 5 | 1 | 0.78581 | 0.46911 | 246.1278 | 200 | 200 | 0 | 200 | 46.1278 | 0 | 195600 | 200 | 260886.6085 | 432.4515 | 0
2890 | 5 | 0 | 1 | 0.42382 | 306.1344 | 0 | 0 | 0 | 0 | 90.3998 | 200 | 195600 | 200 | 261086.6085 | 510.81 | 15.7346
2891 | 5 | 0 | 1 | 0.45886 | 307.5673 | 0 | 0 | 0 | 0 | 0 | 200 | 195600 | 200 | 261286.6085 | 510.81 | 107.5673
2892 | 5 | 0 | 1 | 0.49877 | 309.1996 | 0 | 0 | 0 | 0 | 0 | 200 | 195600 | 200 | 261486.6085 | 510.81 | 109.1996
2893 | 5 | 0 | 1 | 0.57857 | 312.4635 | 0 | 0 | 0 | 0 | 0 | 200 | 195600 | 200 | 261686.6085 | 510.81 | 112.4635
2894 | 5 | 0 | 1 | 0.45903 | 307.5743 | 0 | 0 | 0 | 0 | 0 | 200 | 195600 | 200 | 261886.6085 | 510.81 | 107.5743
2895 | 5 | 0 | 1 | 0.51922 | 310.0361 | 0 | 0 | 0 | 0 | 0 | 200 | 195600 | 200 | 262086.6085 | 510.81 | 110.0361
2896 | 5 | 0 | 1 | 0.27421 | 300.0151 | 0 | 0 | 0 | 0 | 0 | 200 | 195600 | 200 | 262286.6085 | 510.81 | 100.0151
2897 | 5 | 0 | 0.78581 | 0.21919 | 235.9062 | 0 | 0 | 0 | 0 | 0 | 200 | 195600 | 200 | 262486.6085 | 510.81 | 35.9062
2898 | 5 | 0 | 0.43794 | 0.17887 | 133.7938 | 0 | 0 | 0 | 0 | 0 | 133.7938 | 195600 | 133.7938 | 262620.4024 | 510.81 | 0
2899 | 5 | 0 | 0.12819 | 0.22615 | 46.2718 | 0 | 0 | 0 | 0 | 0 | 46.2718 | 195600 | 46.2718 | 262666.6742 | 510.81 | 0
2900 | 5 | 1 | 0 | 0.21488 | 8.7887 | 200 | 8.7887 | 180 | 188.7887 | 0 | 0 | 195400 | 188.7887 | 262855.4629 | 330.81 | 0
2901 | 5 | 1 | 0 | 0.2217 | 9.0675 | 200 | 9.0675 | 180 | 189.0675 | 0 | 0 | 195200 | 189.0675 | 263044.5304 | 150.81 | 0
2902 | 5 | 0 | 0 | 0.24929 | 10.196 | 0 | 0 | 0 | 0 | 10.196 | 0 | 195200 | 0 | 263044.5304 | 159.6479 | 0
2903 | 5 | 0 | 0 | 0.31739 | 12.9811 | 0 | 0 | 0 | 0 | 12.9811 | 0 | 195200 | 0 | 263044.5304 | 170.8999 | 0
2904 | 5 | 0 | 0 | 0.26578 | 10.8706 | 0 | 0 | 0 | 0 | 10.8706 | 0 | 195200 | 0 | 263044.5304 | 180.3226 | 0
2905 | 5 | 0 | 0 | 0.19696 | 8.0557 | 0 | 0 | 0 | 0 | 8.0557 | 0 | 195200 | 0 | 263044.5304 | 187.3053 | 0
2906 | 5 | 0 | 0 | 0.21082 | 8.6227 | 0 | 0 | 0 | 0 | 8.6227 | 0 | 195200 | 0 | 263044.5304 | 194.7795 | 0
2907 | 5 | 0 | 0 | 0.2265 | 9.2636 | 0 | 0 | 0 | 0 | 9.2636 | 0 | 195200 | 0 | 263044.5304 | 202.8092 | 0
2908 | 5 | 0 | 0 | 0.29628 | 12.1179 | 0 | 0 | 0 | 0 | 12.1179 | 0 | 195200 | 0 | 263044.5304 | 213.3129 | 0
2909 | 5 | 0 | 0 | 0.21785 | 8.9101 | 0 | 0 | 0 | 0 | 8.9101 | 0 | 195200 | 0 | 263044.5304 | 221.0363 | 0
2910 | 5 | 0 | 0 | 0.2078 | 8.4989 | 0 | 0 | 0 | 0 | 8.4989 | 0 | 195200 | 0 | 263044.5304 | 228.4031 | 0
2911 | 5 | 0 | 0.12392 | 0.12344 | 40.8375 | 0 | 0 | 0 | 0 | 40.8375 | 0 | 195200 | 0 | 263044.5304 | 263.801 | 0
2912 | 5 | 1 | 0.42335 | 0.17958 | 129.6096 | 200 | 129.6096 | 70.3904 | 200 | 0 | 0 | 195000 | 200 | 263244.5304 | 193.4106 | 0
2913 | 5 | 1 | 0.75963 | 0.16948 | 226.3128 | 200 | 200 | 0 | 200 | 26.3128 | 0 | 194800 | 200 | 263444.5304 | 216.2185 | 0
2914 | 5 | 0 | 1 | 0.15064 | 294.9611 | 0 | 0 | 0 | 0 | 180 | 114.9611 | 194800 | 114.9611 | 263559.4915 | 372.2425 | 0
2915 | 5 | 0 | 1 | 0.24437 | 298.7949 | 0 | 0 | 0 | 0 | 159.861 | 138.9339 | 194800 | 138.9339 | 263698.4254 | 510.81 | 0
2916 | 5 | 0 | 1 | 0.34162 | 302.7723 | 0 | 0 | 0 | 0 | 0 | 200 | 194800 | 200 | 263898.4254 | 510.81 | 102.7723
2917 | 5 | 0 | 1 | 0.37723 | 304.2288 | 0 | 0 | 0 | 0 | 0 | 200 | 194800 | 200 | 264098.4254 | 510.81 | 104.2288
2918 | 5 | 0 | 1 | 0.32201 | 301.9704 | 0 | 0 | 0 | 0 | 0 | 200 | 194800 | 200 | 264298.4254 | 510.81 | 101.9704
2919 | 5 | 0 | 1 | 0.39976 | 305.1503 | 0 | 0 | 0 | 0 | 0 | 200 | 194800 | 200 | 264498.4254 | 510.81 | 105.1503
2920 | 5 | 0 | 1 | 0.42903 | 306.3473 | 0 | 0 | 0 | 0 | 0 | 200 | 194800 | 200 | 264698.4254 | 510.81 | 106.3473
2921 | 5 | 0 | 0.75963 | 0.33627 | 233.1348 | 0 | 0 | 0 | 0 | 0 | 200 | 194800 | 200 | 264898.4254 | 510.81 | 33.1348
2922 | 5 | 0 | 0.42335 | 0.34722 | 136.4661 | 0 | 0 | 0 | 0 | 0 | 136.4661 | 194800 | 136.4661 | 265034.8915 | 510.81 | 0
2923 | 5 | 0 | 0.12392 | 0.34449 | 49.8782 | 0 | 0 | 0 | 0 | 0 | 49.8782 | 194800 | 49.8782 | 265084.7697 | 510.81 | 0
2924 | 5 | 1 | 0 | 0.20242 | 8.2789 | 200 | 8.2789 | 180 | 188.2789 | 0 | 0 | 194600 | 188.2789 | 265273.0486 | 330.81 | 0
2925 | 5 | 1 | 0 | 0.21342 | 8.729 | 200 | 8.729 | 180 | 188.729 | 0 | 0 | 194400 | 188.729 | 265461.7776 | 150.81 | 0
2926 | 5 | 0 | 0 | 0.22926 | 9.3767 | 0 | 0 | 0 | 0 | 9.3767 | 0 | 194400 | 0 | 265461.7776 | 158.9377 | 0
2927 | 5 | 0 | 0 | 0.29241 | 11.9596 | 0 | 0 | 0 | 0 | 11.9596 | 0 | 194400 | 0 | 265461.7776 | 169.3042 | 0
2928 | 5 | 0 | 0 | 0.27119 | 11.0916 | 0 | 0 | 0 | 0 | 11.0916 | 0 | 194400 | 0 | 265461.7776 | 178.9185 | 0
2929 | 5 | 0 | 0 | 0.35532 | 14.5325 | 0 | 0 | 0 | 0 | 14.5325 | 0 | 194400 | 0 | 265461.7776 | 191.5152 | 0
2930 | 5 | 0 | 0 | 0.54158 | 22.1508 | 0 | 0 | 0 | 0 | 22.1508 | 0 | 194400 | 0 | 265461.7776 | 210.7155 | 0
2931 | 5 | 0 | 0 | 0.53788 | 21.9995 | 0 | 0 | 0 | 0 | 21.9995 | 0 | 194400 | 0 | 265461.7776 | 229.7847 | 0
2932 | 5 | 0 | 0 | 0.57802 | 23.6411 | 0 | 0 | 0 | 0 | 23.6411 | 0 | 194400 | 0 | 265461.7776 | 250.2768 | 0
2933 | 5 | 0 | 0 | 0.38143 | 15.6005 | 0 | 0 | 0 | 0 | 15.6005 | 0 | 194400 | 0 | 265461.7776 | 263.7993 | 0
2934 | 5 | 0 | 0 | 0.44905 | 18.366 | 0 | 0 | 0 | 0 | 18.366 | 0 | 194400 | 0 | 265461.7776 | 279.7189 | 0
2935 | 5 | 0 | 0.11756 | 0.36471 | 48.8667 | 0 | 0 | 0 | 0 | 48.8667 | 0 | 194400 | 0 | 265461.7776 | 322.0766 | 0
2936 | 5 | 1 | 0.4016 | 0.38671 | 131.8001 | 200 | 131.8001 | 68.1999 | 200 | 0 | 0 | 194200 | 200 | 265661.7776 | 253.8767 | 0
2937 | 5 | 1 | 0.7206 | 0.26393 | 218.9051 | 200 | 200 | 0 | 200 | 18.9051 | 0 | 194000 | 200 | 265861.7776 | 270.2636 | 0
2938 | 5 | 0 | 1 | 0.34874 | 303.0634 | 0 | 0 | 0 | 0 | 180 | 123.0634 | 194000 | 123.0634 | 265984.841 | 426.2876 | 0
2939 | 5 | 0 | 1 | 0.25027 | 299.0359 | 0 | 0 | 0 | 0 | 97.5108 | 200 | 194000 | 200 | 266184.841 | 510.81 | 1.5251
2940 | 5 | 0 | 1 | 0.30402 | 301.2346 | 0 | 0 | 0 | 0 | 0 | 200 | 194000 | 200 | 266384.841 | 510.81 | 101.2346
2941 | 5 | 0 | 1 | 0.1839 | 296.3215 | 0 | 0 | 0 | 0 | 0 | 200 | 194000 | 200 | 266584.841 | 510.81 | 96.3215
2942 | 5 | 0 | 1 | 0.14392 | 294.6865 | 0 | 0 | 0 | 0 | 0 | 200 | 194000 | 200 | 266784.841 | 510.81 | 94.6865
2943 | 5 | 0 | 1 | 0.16134 | 295.3988 | 0 | 0 | 0 | 0 | 0 | 200 | 194000 | 200 | 266984.841 | 510.81 | 95.3988
2944 | 5 | 0 | 1 | 0.15407 | 295.1016 | 0 | 0 | 0 | 0 | 0 | 200 | 194000 | 200 | 267184.841 | 510.81 | 95.1016
2945 | 5 | 0 | 0.7206 | 0.19926 | 216.26 | 0 | 0 | 0 | 0 | 0 | 200 | 194000 | 200 | 267384.841 | 510.81 | 16.26
2946 | 5 | 0 | 0.4016 | 0.27728 | 127.3243 | 0 | 0 | 0 | 0 | 0 | 127.3243 | 194000 | 127.3243 | 267512.1653 | 510.81 | 0
2947 | 5 | 0 | 0.11756 | 0.35625 | 48.5203 | 0 | 0 | 0 | 0 | 0 | 48.5203 | 194000 | 48.5203 | 267560.6856 | 510.81 | 0
2948 | 5 | 1 | 0 | 0.3868 | 15.8202 | 200 | 15.8202 | 180 | 195.8202 | 0 | 0 | 193800 | 195.8202 | 267756.5058 | 330.81 | 0
2949 | 5 | 1 | 0 | 0.34539 | 14.1264 | 200 | 14.1264 | 180 | 194.1264 | 0 | 0 | 193600 | 194.1264 | 267950.6322 | 150.81 | 0
2950 | 5 | 0 | 0 | 0.25985 | 10.628 | 0 | 0 | 0 | 0 | 10.628 | 0 | 193600 | 0 | 267950.6322 | 160.0223 | 0
2951 | 5 | 0 | 0 | 0.40292 | 16.4796 | 0 | 0 | 0 | 0 | 16.4796 | 0 | 193600 | 0 | 267950.6322 | 174.3068 | 0
2952 | 5 | 0 | 0 | 0.43701 | 17.8735 | 0 | 0 | 0 | 0 | 17.8735 | 0 | 193600 | 0 | 267950.6322 | 189.7996 | 0
2953 | 5 | 0 | 0 | 0.27399 | 11.2064 | 0 | 0 | 0 | 0 | 11.2064 | 0 | 193600 | 0 | 267950.6322 | 199.5133 | 0
2954 | 5 | 0 | 0 | 0.20763 | 8.4921 | 0 | 0 | 0 | 0 | 8.4921 | 0 | 193600 | 0 | 267950.6322 | 206.8743 | 0
2955 | 5 | 0 | 0 | 0.24761 | 10.1274 | 0 | 0 | 0 | 0 | 10.1274 | 0 | 193600 | 0 | 267950.6322 | 215.6527 | 0
2956 | 5 | 0 | 0 | 0.30054 | 12.292 | 0 | 0 | 0 | 0 | 12.292 | 0 | 193600 | 0 | 267950.6322 | 226.3075 | 0
2957 | 5 | 0 | 0 | 0.33308 | 13.6228 | 0 | 0 | 0 | 0 | 13.6228 | 0 | 193600 | 0 | 267950.6322 | 238.1157 | 0
2958 | 5 | 0 | 0 | 0.37677 | 15.4098 | 0 | 0 | 0 | 0 | 15.4098 | 0 | 193600 | 0 | 267950.6322 | 251.4729 | 0
2959 | 5 | 0 | 0.13876 | 0.4831 | 59.8324 | 0 | 0 | 0 | 0 | 59.8324 | 0 | 193600 | 0 | 267950.6322 | 303.3356 | 0
2960 | 5 | 1 | 0.47404 | 0.77955 | 168.7867 | 200 | 168.7867 | 31.2133 | 200 | 0 | 0 | 193400 | 200 | 268150.6322 | 272.1224 | 0
2961 | 5 | 1 | 0.85058 | 0.55185 | 268.2177 | 200 | 200 | 0 | 200 | 68.2177 | 0 | 193200 | 200 | 268350.6322 | 331.2535 | 0
2962 | 5 | 0 | 1 | 0.544 | 311.0495 | 0 | 0 | 0 | 0 | 180 | 131.0495 | 193200 | 131.0495 | 268481.6817 | 487.2775 | 0
2963 | 5 | 0 | 1 | 0.63212 | 314.6537 | 0 | 0 | 0 | 0 | 27.1487 | 200 | 193200 | 200 | 268681.6817 | 510.81 | 87.505
2964 | 5 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 0 | 200 | 193200 | 200 | 268881.6817 | 510.81 | 129.7
2965 | 5 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 0 | 200 | 193200 | 200 | 269081.6817 | 510.81 | 129.7
2966 | 5 | 0 | 1 | 0.94764 | 327.5584 | 0 | 0 | 0 | 0 | 0 | 200 | 193200 | 200 | 269281.6817 | 510.81 | 127.5584
2967 | 5 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 0 | 200 | 193200 | 200 | 269481.6817 | 510.81 | 129.7
2968 | 5 | 0 | 1 | 0.86803 | 324.3023 | 0 | 0 | 0 | 0 | 0 | 200 | 193200 | 200 | 269681.6817 | 510.81 | 124.3023
2969 | 5 | 0 | 0.85058 | 0.5423 | 267.8272 | 0 | 0 | 0 | 0 | 0 | 200 | 193200 | 200 | 269881.6817 | 510.81 | 67.8272
2970 | 5 | 0 | 0.47404 | 0.62466 | 162.4519 | 0 | 0 | 0 | 0 | 0 | 162.4519 | 193200 | 162.4519 | 270044.1336 | 510.81 | 0
2971 | 5 | 0 | 0.13876 | 0.83208 | 74.1058 | 0 | 0 | 0 | 0 | 0 | 74.1058 | 193200 | 74.1058 | 270118.2394 | 510.81 | 0
2972 | 5 | 1 | 0 | 0.83054 | 33.9691 | 200 | 33.9691 | 166.0309 | 200 | 0 | 0 | 193000 | 200 | 270318.2394 | 344.7791 | 0
2973 | 5 | 1 | 0 | 0.98865 | 40.4358 | 200 | 40.4358 | 159.5642 | 200 | 0 | 0 | 192800 | 200 | 270518.2394 | 185.215 | 0
2974 | 5 | 0 | 0 | 0.95607 | 39.1032 | 0 | 0 | 0 | 0 | 39.1032 | 0 | 192800 | 0 | 270518.2394 | 219.1096 | 0
2975 | 5 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 192800 | 0 | 270518.2394 | 254.5617 | 0
2976 | 5 | 0 | 0 | 0.74144 | 30.3248 | 0 | 0 | 0 | 0 | 30.3248 | 0 | 192800 | 0 | 270518.2394 | 280.8473 | 0
2977 | 5 | 0 | 0 | 0.89055 | 36.4235 | 0 | 0 | 0 | 0 | 36.4235 | 0 | 192800 | 0 | 270518.2394 | 312.4191 | 0
2978 | 5 | 0 | 0 | 0.90703 | 37.0976 | 0 | 0 | 0 | 0 | 37.0976 | 0 | 192800 | 0 | 270518.2394 | 344.5753 | 0
2979 | 5 | 0 | 0 | 0.66984 | 27.3964 | 0 | 0 | 0 | 0 | 27.3964 | 0 | 192800 | 0 | 270518.2394 | 368.3225 | 0
2980 | 5 | 0 | 0 | 0.47518 | 19.4349 | 0 | 0 | 0 | 0 | 19.4349 | 0 | 192800 | 0 | 270518.2394 | 385.1687 | 0
2981 | 5 | 0 | 0 | 0.48898 | 19.9993 | 0 | 0 | 0 | 0 | 19.9993 | 0 | 192800 | 0 | 270518.2394 | 402.5041 | 0
2982 | 5 | 0 | 0 | 0.46771 | 19.1292 | 0 | 0 | 0 | 0 | 19.1292 | 0 | 192800 | 0 | 270518.2394 | 419.0853 | 0
2983 | 5 | 0 | 0.12263 | 0.44589 | 53.6533 | 0 | 0 | 0 | 0 | 53.6533 | 0 | 192800 | 0 | 270518.2394 | 465.5919 | 0
2984 | 5 | 1 | 0.41895 | 0.3878 | 136.8542 | 200 | 136.8542 | 63.1458 | 200 | 0 | 0 | 192600 | 200 | 270718.2394 | 402.4461 | 0
2985 | 5 | 1 | 0.75173 | 0.59913 | 241.6041 | 200 | 200 | 0 | 200 | 41.6041 | 0 | 192400 | 200 | 270918.2394 | 438.5085 | 0
2986 | 5 | 0 | 1 | 0.47991 | 308.4284 | 0 | 0 | 0 | 0 | 83.4119 | 200 | 192400 | 200 | 271118.2394 | 510.81 | 25.0165
2987 | 5 | 0 | 1 | 0.44874 | 307.1533 | 0 | 0 | 0 | 0 | 0 | 200 | 192400 | 200 | 271318.2394 | 510.81 | 107.1533
2988 | 5 | 0 | 1 | 0.36406 | 303.6901 | 0 | 0 | 0 | 0 | 0 | 200 | 192400 | 200 | 271518.2394 | 510.81 | 103.6901
2989 | 5 | 0 | 1 | 0.27675 | 300.1192 | 0 | 0 | 0 | 0 | 0 | 200 | 192400 | 200 | 271718.2394 | 510.81 | 100.1192
2990 | 5 | 0 | 1 | 0.28033 | 300.2657 | 0 | 0 | 0 | 0 | 0 | 200 | 192400 | 200 | 271918.2394 | 510.81 | 100.2657
2991 | 5 | 0 | 1 | 0.31422 | 301.6518 | 0 | 0 | 0 | 0 | 0 | 200 | 192400 | 200 | 272118.2394 | 510.81 | 101.6518
2992 | 5 | 0 | 1 | 0.21666 | 297.6613 | 0 | 0 | 0 | 0 | 0 | 200 | 192400 | 200 | 272318.2394 | 510.81 | 97.6613
2993 | 5 | 0 | 0.75173 | 0.22182 | 226.1719 | 0 | 0 | 0 | 0 | 0 | 200 | 192400 | 200 | 272518.2394 | 510.81 | 26.1719
2994 | 5 | 0 | 0.41895 | 0.16409 | 127.7046 | 0 | 0 | 0 | 0 | 0 | 127.7046 | 192400 | 127.7046 | 272645.9439 | 510.81 | 0
2995 | 5 | 0 | 0.12263 | 0.20336 | 43.7338 | 0 | 0 | 0 | 0 | 0 | 43.7338 | 192400 | 43.7338 | 272689.6777 | 510.81 | 0
2996 | 5 | 1 | 0 | 0.26715 | 10.9266 | 200 | 10.9266 | 180 | 190.9266 | 0 | 0 | 192200 | 190.9266 | 272880.6043 | 330.81 | 0
2997 | 5 | 1 | 0 | 0.19535 | 7.9899 | 200 | 7.9899 | 180 | 187.9899 | 0 | 0 | 192000 | 187.9899 | 273068.5942 | 150.81 | 0
2998 | 5 | 0 | 0 | 0.22435 | 9.1761 | 0 | 0 | 0 | 0 | 9.1761 | 0 | 192000 | 0 | 273068.5942 | 158.7639 | 0
2999 | 5 | 0 | 0 | 0.20235 | 8.2762 | 0 | 0 | 0 | 0 | 8.2762 | 0 | 192000 | 0 | 273068.5942 | 165.9377 | 0
3000 | 5 | 0 | 0 | 0.1807 | 7.3905 | 0 | 0 | 0 | 0 | 7.3905 | 0 | 192000 | 0 | 273068.5942 | 172.3438 | 0
3001 | 5 | 0 | 0 | 0.32471 | 13.2807 | 0 | 0 | 0 | 0 | 13.2807 | 0 | 192000 | 0 | 273068.5942 | 183.8556 | 0
3002 | 5 | 0 | 0 | 0.38842 | 15.8862 | 0 | 0 | 0 | 0 | 15.8862 | 0 | 192000 | 0 | 273068.5942 | 197.6257 | 0
3003 | 5 | 0 | 0 | 0.22043 | 9.0156 | 0 | 0 | 0 | 0 | 9.0156 | 0 | 192000 | 0 | 273068.5942 | 205.4404 | 0
3004 | 5 | 0 | 0 | 0.1698 | 6.945 | 0 | 0 | 0 | 0 | 6.945 | 0 | 192000 | 0 | 273068.5942 | 211.4603 | 0
3005 | 5 | 0 | 0 | 0.23082 | 9.4406 | 0 | 0 | 0 | 0 | 9.4406 | 0 | 192000 | 0 | 273068.5942 | 219.6434 | 0
3006 | 5 | 0 | 0 | 0.23589 | 9.6477 | 0 | 0 | 0 | 0 | 9.6477 | 0 | 192000 | 0 | 273068.5942 | 228.0061 | 0
3007 | 5 | 0 | 0.12469 | 0.22315 | 45.1369 | 0 | 0 | 0 | 0 | 45.1369 | 0 | 192000 | 0 | 273068.5942 | 267.1307 | 0
3008 | 5 | 1 | 0.42598 | 0.23074 | 132.4594 | 200 | 132.4594 | 67.5406 | 200 | 0 | 0 | 191800 | 200 | 273268.5942 | 199.5901 | 0
3009 | 5 | 1 | 0.76433 | 0.21636 | 229.5889 | 200 | 200 | 0 | 200 | 29.5889 | 0 | 191600 | 200 | 273468.5942 | 225.2378 | 0
3010 | 5 | 0 | 1 | 0.22202 | 297.8806 | 0 | 0 | 0 | 0 | 180 | 117.8806 | 191600 | 117.8806 | 273586.4748 | 381.2618 | 0
3011 | 5 | 0 | 1 | 0.30224 | 301.1617 | 0 | 0 | 0 | 0 | 149.4557 | 151.7059 | 191600 | 151.7059 | 273738.1807 | 510.81 | 0
3012 | 5 | 0 | 1 | 0.40414 | 305.3292 | 0 | 0 | 0 | 0 | 0 | 200 | 191600 | 200 | 273938.1807 | 510.81 | 105.3292
3013 | 5 | 0 | 1 | 0.33137 | 302.353 | 0 | 0 | 0 | 0 | 0 | 200 | 191600 | 200 | 274138.1807 | 510.81 | 102.353
3014 | 5 | 0 | 1 | 0.33927 | 302.6763 | 0 | 0 | 0 | 0 | 0 | 200 | 191600 | 200 | 274338.1807 | 510.81 | 102.6763
3015 | 5 | 0 | 1 | 0.47278 | 308.1368 | 0 | 0 | 0 | 0 | 0 | 200 | 191600 | 200 | 274538.1807 | 510.81 | 108.1368
3016 | 5 | 0 | 1 | 0.50985 | 309.6527 | 0 | 0 | 0 | 0 | 0 | 200 | 191600 | 200 | 274738.1807 | 510.81 | 109.6527
3017 | 5 | 0 | 0.76433 | 0.45564 | 239.3755 | 0 | 0 | 0 | 0 | 0 | 200 | 191600 | 200 | 274938.1807 | 510.81 | 39.3755
3018 | 5 | 0 | 0.42598 | 0.54108 | 145.1525 | 0 | 0 | 0 | 0 | 0 | 145.1525 | 191600 | 145.1525 | 275083.3332 | 510.81 | 0
3019 | 5 | 0 | 0.12469 | 0.34829 | 50.2551 | 0 | 0 | 0 | 0 | 0 | 50.2551 | 191600 | 50.2551 | 275133.5883 | 510.81 | 0
3020 | 5 | 1 | 0 | 0.28053 | 11.4739 | 200 | 11.4739 | 180 | 191.4739 | 0 | 0 | 191400 | 191.4739 | 275325.0622 | 330.81 | 0
3021 | 5 | 1 | 0 | 0.37135 | 15.1882 | 200 | 15.1882 | 180 | 195.1882 | 0 | 0 | 191200 | 195.1882 | 275520.2504 | 150.81 | 0
3022 | 5 | 0 | 0 | 0.27817 | 11.377 | 0 | 0 | 0 | 0 | 11.377 | 0 | 191200 | 0 | 275520.2504 | 160.6716 | 0
3023 | 5 | 0 | 0 | 0.27824 | 11.3799 | 0 | 0 | 0 | 0 | 11.3799 | 0 | 191200 | 0 | 275520.2504 | 170.5357 | 0
3024 | 5 | 0 | 0 | 0.29447 | 12.0438 | 0 | 0 | 0 | 0 | 12.0438 | 0 | 191200 | 0 | 275520.2504 | 180.9753 | 0
3025 | 5 | 0 | 0 | 0.2739 | 11.2027 | 0 | 0 | 0 | 0 | 11.2027 | 0 | 191200 | 0 | 275520.2504 | 190.6857 | 0
3026 | 5 | 0 | 0 | 0.35666 | 14.5874 | 0 | 0 | 0 | 0 | 14.5874 | 0 | 191200 | 0 | 275520.2504 | 203.3301 | 0
3027 | 5 | 0 | 0 | 0.34604 | 14.153 | 0 | 0 | 0 | 0 | 14.153 | 0 | 191200 | 0 | 275520.2504 | 215.5979 | 0
3028 | 5 | 0 | 0 | 0.18434 | 7.5396 | 0 | 0 | 0 | 0 | 7.5396 | 0 | 191200 | 0 | 275520.2504 | 222.1332 | 0
3029 | 5 | 0 | 0 | 0.23156 | 9.4708 | 0 | 0 | 0 | 0 | 9.4708 | 0 | 191200 | 0 | 275520.2504 | 230.3425 | 0
3030 | 5 | 0 | 0 | 0.29616 | 12.1129 | 0 | 0 | 0 | 0 | 12.1129 | 0 | 191200 | 0 | 275520.2504 | 240.842 | 0
3031 | 5 | 0 | 0.12298 | 0.4753 | 54.9573 | 0 | 0 | 0 | 0 | 54.9573 | 0 | 191200 | 0 | 275520.2504 | 288.479 | 0
3032 | 5 | 1 | 0.42015 | 0.47211 | 140.6485 | 200 | 140.6485 | 59.3515 | 200 | 0 | 0 | 191000 | 200 | 275720.2504 | 229.1275 | 0
3033 | 5 | 1 | 0.75388 | 0.42504 | 235.1047 | 200 | 200 | 0 | 200 | 35.1047 | 0 | 190800 | 200 | 275920.2504 | 259.5562 | 0
3034 | 5 | 0 | 1 | 0.38838 | 304.6849 | 0 | 0 | 0 | 0 | 180 | 124.6849 | 190800 | 124.6849 | 276044.9354 | 415.5802 | 0
3035 | 5 | 0 | 1 | 0.51805 | 309.9883 | 0 | 0 | 0 | 0 | 109.8636 | 200 | 190800 | 200 | 276244.9354 | 510.81 | 0.12472
3036 | 5 | 0 | 1 | 0.53369 | 310.6279 | 0 | 0 | 0 | 0 | 0 | 200 | 190800 | 200 | 276444.9354 | 510.81 | 110.6279
3037 | 5 | 0 | 1 | 0.56671 | 311.9784 | 0 | 0 | 0 | 0 | 0 | 200 | 190800 | 200 | 276644.9354 | 510.81 | 111.9784
3038 | 5 | 0 | 1 | 0.65509 | 315.5931 | 0 | 0 | 0 | 0 | 0 | 200 | 190800 | 200 | 276844.9354 | 510.81 | 115.5931
3039 | 5 | 0 | 1 | 0.56606 | 311.9518 | 0 | 0 | 0 | 0 | 0 | 200 | 190800 | 200 | 277044.9354 | 510.81 | 111.9518
3040 | 5 | 0 | 1 | 0.80819 | 321.8552 | 0 | 0 | 0 | 0 | 0 | 200 | 190800 | 200 | 277244.9354 | 510.81 | 121.8552
3041 | 5 | 0 | 0.75388 | 1 | 258.6205 | 0 | 0 | 0 | 0 | 0 | 200 | 190800 | 200 | 277444.9354 | 510.81 | 58.6205
3042 | 5 | 0 | 0.42015 | 0.65968 | 148.3203 | 0 | 0 | 0 | 0 | 0 | 148.3203 | 190800 | 148.3203 | 277593.2556 | 510.81 | 0
3043 | 5 | 0 | 0.12298 | 1 | 76.4178 | 0 | 0 | 0 | 0 | 0 | 76.4178 | 190800 | 76.4178 | 277669.6734 | 510.81 | 0
3044 | 5 | 1 | 0 | 0.78739 | 32.2044 | 200 | 32.2044 | 167.7956 | 200 | 0 | 0 | 190600 | 200 | 277869.6734 | 343.0144 | 0
3045 | 5 | 1 | 0 | 0.62445 | 25.5402 | 200 | 25.5402 | 174.4598 | 200 | 0 | 0 | 190400 | 200 | 278069.6734 | 168.5546 | 0
3046 | 5 | 0 | 0 | 0.8486 | 34.7078 | 0 | 0 | 0 | 0 | 34.7078 | 0 | 190400 | 0 | 278069.6734 | 198.6393 | 0
3047 | 5 | 0 | 0 | 0.83881 | 34.3072 | 0 | 0 | 0 | 0 | 34.3072 | 0 | 190400 | 0 | 278069.6734 | 228.3768 | 0
3048 | 5 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 190400 | 0 | 278069.6734 | 263.829 | 0
3049 | 5 | 0 | 0 | 0.94745 | 38.7507 | 0 | 0 | 0 | 0 | 38.7507 | 0 | 190400 | 0 | 278069.6734 | 297.4181 | 0
3050 | 5 | 0 | 0 | 0.83662 | 34.218 | 0 | 0 | 0 | 0 | 34.218 | 0 | 190400 | 0 | 278069.6734 | 327.0782 | 0
3051 | 5 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 190400 | 0 | 278069.6734 | 362.5303 | 0
3052 | 5 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 190400 | 0 | 278069.6734 | 397.9824 | 0
3053 | 5 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 190400 | 0 | 278069.6734 | 433.4346 | 0
3054 | 5 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 190400 | 0 | 278069.6734 | 468.8867 | 0
3055 | 5 | 0 | 0.11272 | 1 | 73.4544 | 0 | 0 | 0 | 0 | 48.3656 | 25.0888 | 190400 | 25.0888 | 278094.7622 | 510.81 | 0
3056 | 5 | 1 | 0.3851 | 0.85319 | 146.1108 | 200 | 146.1108 | 53.8892 | 200 | 0 | 0 | 190200 | 200 | 278294.7622 | 456.9208 | 0
3057 | 5 | 1 | 0.69098 | 0.61436 | 224.6819 | 200 | 200 | 0 | 200 | 24.6819 | 0 | 190000 | 200 | 278494.7622 | 478.3151 | 0
3058 | 5 | 0 | 0.98051 | 0.80451 | 316.0765 | 0 | 0 | 0 | 0 | 37.4884 | 200 | 190000 | 200 | 278694.7622 | 510.81 | 78.5881
3059 | 5 | 0 | 1 | 0.93488 | 327.0365 | 0 | 0 | 0 | 0 | 0 | 200 | 190000 | 200 | 278894.7622 | 510.81 | 127.0365
3060 | 5 | 0 | 1 | 0.96098 | 328.1041 | 0 | 0 | 0 | 0 | 0 | 200 | 190000 | 200 | 279094.7622 | 510.81 | 128.1041
3061 | 5 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 0 | 200 | 190000 | 200 | 279294.7622 | 510.81 | 129.7
3062 | 5 | 0 | 1 | 0.93539 | 327.0576 | 0 | 0 | 0 | 0 | 0 | 200 | 190000 | 200 | 279494.7622 | 510.81 | 127.0576
3063 | 5 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 0 | 200 | 190000 | 200 | 279694.7622 | 510.81 | 129.7
3064 | 5 | 0 | 0.98051 | 0.73165 | 313.0966 | 0 | 0 | 0 | 0 | 0 | 200 | 190000 | 200 | 279894.7622 | 510.81 | 113.0966
3065 | 5 | 0 | 0.69098 | 0.64705 | 226.0191 | 0 | 0 | 0 | 0 | 0 | 200 | 190000 | 200 | 280094.7622 | 510.81 | 26.0191
3066 | 5 | 0 | 0.3851 | 0.7182 | 140.5897 | 0 | 0 | 0 | 0 | 0 | 140.5897 | 190000 | 140.5897 | 280235.3519 | 510.81 | 0
3067 | 5 | 0 | 0.11272 | 0.50416 | 53.1748 | 0 | 0 | 0 | 0 | 0 | 53.1748 | 190000 | 53.1748 | 280288.5266 | 510.81 | 0
3068 | 5 | 1 | 0 | 0.27471 | 11.2356 | 200 | 11.2356 | 180 | 191.2356 | 0 | 0 | 189800 | 191.2356 | 280479.7622 | 330.81 | 0
3069 | 5 | 1 | 0 | 0.23161 | 9.473 | 200 | 9.473 | 180 | 189.473 | 0 | 0 | 189600 | 189.473 | 280669.2352 | 150.81 | 0
3070 | 5 | 0 | 0 | 0.26108 | 10.678 | 0 | 0 | 0 | 0 | 10.678 | 0 | 189600 | 0 | 280669.2352 | 160.0657 | 0
3071 | 5 | 0 | 0 | 0.28165 | 11.5195 | 0 | 0 | 0 | 0 | 11.5195 | 0 | 189600 | 0 | 280669.2352 | 170.0508 | 0
3072 | 5 | 0 | 0 | 0.23041 | 9.4239 | 0 | 0 | 0 | 0 | 9.4239 | 0 | 189600 | 0 | 280669.2352 | 178.2195 | 0
3073 | 5 | 0 | 0 | 0.19638 | 8.0321 | 0 | 0 | 0 | 0 | 8.0321 | 0 | 189600 | 0 | 280669.2352 | 185.1817 | 0
3074 | 5 | 0 | 0 | 0.26192 | 10.7126 | 0 | 0 | 0 | 0 | 10.7126 | 0 | 189600 | 0 | 280669.2352 | 194.4674 | 0
3075 | 5 | 0 | 0 | 0.21869 | 8.9443 | 0 | 0 | 0 | 0 | 8.9443 | 0 | 189600 | 0 | 280669.2352 | 202.2203 | 0
3076 | 5 | 0 | 0 | 0.17938 | 7.3367 | 0 | 0 | 0 | 0 | 7.3367 | 0 | 189600 | 0 | 280669.2352 | 208.5798 | 0
3077 | 5 | 0 | 0 | 0.15027 | 6.1462 | 0 | 0 | 0 | 0 | 6.1462 | 0 | 189600 | 0 | 280669.2352 | 213.9073 | 0
3078 | 5 | 0 | 0 | 0.14305 | 5.8509 | 0 | 0 | 0 | 0 | 5.8509 | 0 | 189600 | 0 | 280669.2352 | 218.9789 | 0
3079 | 5 | 0 | 0.11718 | 0.13464 | 39.3492 | 0 | 0 | 0 | 0 | 39.3492 | 0 | 189600 | 0 | 280669.2352 | 253.0868 | 0
3080 | 5 | 1 | 0.40033 | 0.14324 | 121.474 | 200 | 121.474 | 78.526 | 200 | 0 | 0 | 189400 | 200 | 280869.2352 | 174.5608 | 0
3081 | 5 | 1 | 0.71832 | 0.18339 | 214.9508 | 200 | 200 | 0 | 200 | 14.9508 | 0 | 189200 | 200 | 281069.2352 | 187.5202 | 0
3082 | 5 | 0 | 1 | 0.12391 | 293.8678 | 0 | 0 | 0 | 0 | 180 | 113.8678 | 189200 | 113.8678 | 281183.103 | 343.5442 | 0
3083 | 5 | 0 | 1 | 0.12441 | 293.8882 | 0 | 0 | 0 | 0 | 180 | 113.8882 | 189200 | 113.8882 | 281296.9912 | 499.5682 | 0
3084 | 5 | 0 | 1 | 0.20125 | 297.0313 | 0 | 0 | 0 | 0 | 12.9693 | 200 | 189200 | 200 | 281496.9912 | 510.81 | 84.062
3085 | 5 | 0 | 1 | 0.17208 | 295.8379 | 0 | 0 | 0 | 0 | 0 | 200 | 189200 | 200 | 281696.9912 | 510.81 | 95.8379
3086 | 5 | 0 | 1 | 0.15718 | 295.2289 | 0 | 0 | 0 | 0 | 0 | 200 | 189200 | 200 | 281896.9912 | 510.81 | 95.2289
3087 | 5 | 0 | 1 | 0.19598 | 296.8155 | 0 | 0 | 0 | 0 | 0 | 200 | 189200 | 200 | 282096.9912 | 510.81 | 96.8155
3088 | 5 | 0 | 1 | 0.27598 | 300.0877 | 0 | 0 | 0 | 0 | 0 | 200 | 189200 | 200 | 282296.9912 | 510.81 | 100.0877
3089 | 5 | 0 | 0.71832 | 0.25402 | 217.8398 | 0 | 0 | 0 | 0 | 0 | 200 | 189200 | 200 | 282496.9912 | 510.81 | 17.8398
3090 | 5 | 0 | 0.40033 | 0.4379 | 133.5258 | 0 | 0 | 0 | 0 | 0 | 133.5258 | 189200 | 133.5258 | 282630.517 | 510.81 | 0
3091 | 5 | 0 | 0.11718 | 0.46485 | 52.855 | 0 | 0 | 0 | 0 | 0 | 52.855 | 189200 | 52.855 | 282683.3719 | 510.81 | 0
3092 | 5 | 1 | 0 | 0.5125 | 20.961 | 200 | 20.961 | 179.039 | 200 | 0 | 0 | 189000 | 200 | 282883.3719 | 331.771 | 0
3093 | 5 | 1 | 0 | 0.41009 | 16.7726 | 200 | 16.7726 | 180 | 196.7726 | 0 | 0 | 188800 | 196.7726 | 283080.1446 | 151.771 | 0
3094 | 5 | 0 | 0 | 0.47748 | 19.5289 | 0 | 0 | 0 | 0 | 19.5289 | 0 | 188800 | 0 | 283080.1446 | 168.6987 | 0
3095 | 5 | 0 | 0 | 0.42193 | 17.257 | 0 | 0 | 0 | 0 | 17.257 | 0 | 188800 | 0 | 283080.1446 | 183.657 | 0
3096 | 5 | 0 | 0 | 0.59874 | 24.4885 | 0 | 0 | 0 | 0 | 24.4885 | 0 | 188800 | 0 | 283080.1446 | 204.8837 | 0
3097 | 5 | 0 | 0 | 0.36752 | 15.0317 | 0 | 0 | 0 | 0 | 15.0317 | 0 | 188800 | 0 | 283080.1446 | 217.9132 | 0
3098 | 5 | 0 | 0 | 0.30051 | 12.2908 | 0 | 0 | 0 | 0 | 12.2908 | 0 | 188800 | 0 | 283080.1446 | 228.5669 | 0
3099 | 5 | 0 | 0 | 0.28602 | 11.6984 | 0 | 0 | 0 | 0 | 11.6984 | 0 | 188800 | 0 | 283080.1446 | 238.7071 | 0
3100 | 5 | 0 | 0 | 0.34704 | 14.1938 | 0 | 0 | 0 | 0 | 14.1938 | 0 | 188800 | 0 | 283080.1446 | 251.0102 | 0
3101 | 5 | 0 | 0 | 0.26797 | 10.96 | 0 | 0 | 0 | 0 | 10.96 | 0 | 188800 | 0 | 283080.1446 | 260.5103 | 0
3102 | 5 | 0 | 0 | 0.44193 | 18.0751 | 0 | 0 | 0 | 0 | 18.0751 | 0 | 188800 | 0 | 283080.1446 | 276.1778 | 0
3103 | 5 | 0 | 0.12511 | 0.46676 | 55.2221 | 0 | 0 | 0 | 0 | 55.2221 | 0 | 188800 | 0 | 283080.1446 | 324.0444 | 0
3104 | 5 | 1 | 0.42741 | 0.46181 | 142.3249 | 200 | 142.3249 | 57.6751 | 200 | 0 | 0 | 188600 | 200 | 283280.1446 | 266.3693 | 0
3105 | 5 | 1 | 0.76691 | 0.37959 | 237.0089 | 200 | 200 | 0 | 200 | 37.0089 | 0 | 188400 | 200 | 283480.1446 | 298.4486 | 0
3106 | 5 | 0 | 1 | 0.36812 | 303.8563 | 0 | 0 | 0 | 0 | 180 | 123.8563 | 188400 | 123.8563 | 283604.0009 | 454.4726 | 0
3107 | 5 | 0 | 1 | 0.39094 | 304.7894 | 0 | 0 | 0 | 0 | 64.9947 | 200 | 188400 | 200 | 283804.0009 | 510.81 | 39.7947
3108 | 5 | 0 | 1 | 0.34316 | 302.8352 | 0 | 0 | 0 | 0 | 0 | 200 | 188400 | 200 | 284004.0009 | 510.81 | 102.8352
3109 | 5 | 0 | 1 | 0.26536 | 299.6531 | 0 | 0 | 0 | 0 | 0 | 200 | 188400 | 200 | 284204.0009 | 510.81 | 99.6531
3110 | 5 | 0 | 1 | 0.26642 | 299.6964 | 0 | 0 | 0 | 0 | 0 | 200 | 188400 | 200 | 284404.0009 | 510.81 | 99.6964
3111 | 5 | 0 | 1 | 0.42387 | 306.1362 | 0 | 0 | 0 | 0 | 0 | 200 | 188400 | 200 | 284604.0009 | 510.81 | 106.1362
3112 | 5 | 0 | 1 | 0.52767 | 310.3817 | 0 | 0 | 0 | 0 | 0 | 200 | 188400 | 200 | 284804.0009 | 510.81 | 110.3817
3113 | 5 | 0 | 0.76691 | 0.66348 | 248.6201 | 0 | 0 | 0 | 0 | 0 | 200 | 188400 | 200 | 285004.0009 | 510.81 | 48.6201
3114 | 5 | 0 | 0.42741 | 0.71605 | 152.7234 | 0 | 0 | 0 | 0 | 0 | 152.7234 | 188400 | 152.7234 | 285156.7243 | 510.81 | 0
3115 | 5 | 0 | 0.12511 | 0.51094 | 57.0294 | 0 | 0 | 0 | 0 | 0 | 57.0294 | 188400 | 57.0294 | 285213.7537 | 510.81 | 0
3116 | 5 | 1 | 0 | 0.39545 | 16.1737 | 200 | 16.1737 | 180 | 196.1737 | 0 | 0 | 188200 | 196.1737 | 285409.9274 | 330.81 | 0
3117 | 5 | 1 | 0 | 0.3051 | 12.4787 | 200 | 12.4787 | 180 | 192.4787 | 0 | 0 | 188000 | 192.4787 | 285602.4061 | 150.81 | 0
3118 | 5 | 0 | 0 | 0.43373 | 17.7397 | 0 | 0 | 0 | 0 | 17.7397 | 0 | 188000 | 0 | 285602.4061 | 166.1868 | 0
3119 | 5 | 0 | 0 | 0.5108 | 20.8918 | 0 | 0 | 0 | 0 | 20.8918 | 0 | 188000 | 0 | 285602.4061 | 184.2958 | 0
3120 | 5 | 0 | 0 | 0.2833 | 11.5869 | 0 | 0 | 0 | 0 | 11.5869 | 0 | 188000 | 0 | 285602.4061 | 194.3394 | 0
3121 | 5 | 0 | 0 | 0.3224 | 13.1862 | 0 | 0 | 0 | 0 | 13.1862 | 0 | 188000 | 0 | 285602.4061 | 205.7692 | 0
3122 | 5 | 0 | 0 | 0.29626 | 12.1172 | 0 | 0 | 0 | 0 | 12.1172 | 0 | 188000 | 0 | 285602.4061 | 216.2723 | 0
3123 | 5 | 0 | 0 | 0.25012 | 10.23 | 0 | 0 | 0 | 0 | 10.23 | 0 | 188000 | 0 | 285602.4061 | 225.1397 | 0
3124 | 5 | 0 | 0 | 0.44565 | 18.2272 | 0 | 0 | 0 | 0 | 18.2272 | 0 | 188000 | 0 | 285602.4061 | 240.9391 | 0
3125 | 5 | 0 | 0 | 0.33868 | 13.8521 | 0 | 0 | 0 | 0 | 13.8521 | 0 | 188000 | 0 | 285602.4061 | 252.9461 | 0
3126 | 5 | 0 | 0 | 0.22102 | 9.0397 | 0 | 0 | 0 | 0 | 9.0397 | 0 | 188000 | 0 | 285602.4061 | 260.7817 | 0
3127 | 5 | 0 | 0.12202 | 0.31432 | 48.0949 | 0 | 0 | 0 | 0 | 48.0949 | 0 | 188000 | 0 | 285602.4061 | 302.4703 | 0
3128 | 5 | 1 | 0.41685 | 0.45283 | 138.9086 | 200 | 138.9086 | 61.0914 | 200 | 0 | 0 | 187800 | 200 | 285802.4061 | 241.3789 | 0
3129 | 5 | 1 | 0.74797 | 0.53967 | 238.0854 | 200 | 200 | 0 | 200 | 38.0854 | 0 | 187600 | 200 | 286002.4061 | 274.3913 | 0
3130 | 5 | 0 | 1 | 0.89884 | 325.5625 | 0 | 0 | 0 | 0 | 180 | 145.5625 | 187600 | 145.5625 | 286147.9686 | 430.4153 | 0
3131 | 5 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 92.7488 | 200 | 187600 | 200 | 286347.9686 | 510.81 | 36.9512
3132 | 5 | 0 | 1 | 0.85981 | 323.9662 | 0 | 0 | 0 | 0 | 0 | 200 | 187600 | 200 | 286547.9686 | 510.81 | 123.9662
3133 | 5 | 0 | 1 | 0.77223 | 320.3842 | 0 | 0 | 0 | 0 | 0 | 200 | 187600 | 200 | 286747.9686 | 510.81 | 120.3842
3134 | 5 | 0 | 1 | 0.69191 | 317.099 | 0 | 0 | 0 | 0 | 0 | 200 | 187600 | 200 | 286947.9686 | 510.81 | 117.099
3135 | 5 | 0 | 1 | 0.67404 | 316.3684 | 0 | 0 | 0 | 0 | 0 | 200 | 187600 | 200 | 287147.9686 | 510.81 | 116.3684
3136 | 5 | 0 | 1 | 0.8485 | 323.5036 | 0 | 0 | 0 | 0 | 0 | 200 | 187600 | 200 | 287347.9686 | 510.81 | 123.5036
3137 | 5 | 0 | 0.74797 | 0.80548 | 248.9569 | 0 | 0 | 0 | 0 | 0 | 200 | 187600 | 200 | 287547.9686 | 510.81 | 48.9569
3138 | 5 | 0 | 0.41685 | 0.93811 | 158.7565 | 0 | 0 | 0 | 0 | 0 | 158.7565 | 187600 | 158.7565 | 287706.7252 | 510.81 | 0
3139 | 5 | 0 | 0.12202 | 0.80273 | 68.0707 | 0 | 0 | 0 | 0 | 0 | 68.0707 | 187600 | 68.0707 | 287774.7959 | 510.81 | 0
3140 | 5 | 1 | 0 | 1 | 40.9 | 200 | 40.9 | 159.1 | 200 | 0 | 0 | 187400 | 200 | 287974.7959 | 351.71 | 0
3141 | 5 | 1 | 0 | 0.92748 | 37.934 | 200 | 37.934 | 162.066 | 200 | 0 | 0 | 187200 | 200 | 288174.7959 | 189.644 | 0
3142 | 5 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 187200 | 0 | 288174.7959 | 225.0961 | 0
3143 | 5 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 187200 | 0 | 288174.7959 | 260.5482 | 0
3144 | 5 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 187200 | 0 | 288174.7959 | 296.0003 | 0
3145 | 5 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 187200 | 0 | 288174.7959 | 331.4525 | 0
3146 | 5 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 187200 | 0 | 288174.7959 | 366.9046 | 0
3147 | 5 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 187200 | 0 | 288174.7959 | 402.3567 | 0
3148 | 5 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 187200 | 0 | 288174.7959 | 437.8088 | 0
3149 | 5 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 187200 | 0 | 288174.7959 | 473.2609 | 0
3150 | 5 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 187200 | 0 | 288174.7959 | 508.7131 | 0
3151 | 5 | 0 | 0.11847 | 1 | 75.113 | 0 | 0 | 0 | 0 | 2.4192 | 72.6938 | 187200 | 72.6938 | 288247.4897 | 510.81 | 0
3152 | 5 | 1 | 0.40472 | 1 | 157.7823 | 200 | 157.7823 | 42.2177 | 200 | 0 | 0 | 187000 | 200 | 288447.4897 | 468.5923 | 0
3153 | 5 | 1 | 0.72619 | 0.77785 | 241.5375 | 200 | 200 | 0 | 200 | 41.5375 | 0 | 186800 | 200 | 288647.4897 | 504.597 | 0
3154 | 5 | 0 | 1 | 0.57514 | 312.3231 | 0 | 0 | 0 | 0 | 7.1677 | 200 | 186800 | 200 | 288847.4897 | 510.81 | 105.1553
3155 | 5 | 0 | 1 | 0.56241 | 311.8024 | 0 | 0 | 0 | 0 | 0 | 200 | 186800 | 200 | 289047.4897 | 510.81 | 111.8024
3156 | 5 | 0 | 1 | 0.57386 | 312.2709 | 0 | 0 | 0 | 0 | 0 | 200 | 186800 | 200 | 289247.4897 | 510.81 | 112.2709
3157 | 5 | 0 | 1 | 0.51877 | 310.0175 | 0 | 0 | 0 | 0 | 0 | 200 | 186800 | 200 | 289447.4897 | 510.81 | 110.0175
3158 | 5 | 0 | 1 | 0.52929 | 310.4478 | 0 | 0 | 0 | 0 | 0 | 200 | 186800 | 200 | 289647.4897 | 510.81 | 110.4478
3159 | 5 | 0 | 1 | 0.68226 | 316.7045 | 0 | 0 | 0 | 0 | 0 | 200 | 186800 | 200 | 289847.4897 | 510.81 | 116.7045
3160 | 5 | 0 | 1 | 0.79273 | 321.2228 | 0 | 0 | 0 | 0 | 0 | 200 | 186800 | 200 | 290047.4897 | 510.81 | 121.2228
3161 | 5 | 0 | 0.72619 | 0.54942 | 232.1945 | 0 | 0 | 0 | 0 | 0 | 200 | 186800 | 200 | 290247.4897 | 510.81 | 32.1945
3162 | 5 | 0 | 0.40472 | 0.41442 | 133.832 | 0 | 0 | 0 | 0 | 0 | 133.832 | 186800 | 133.832 | 290381.3217 | 510.81 | 0
3163 | 5 | 0 | 0.11847 | 0.37657 | 49.6147 | 0 | 0 | 0 | 0 | 0 | 49.6147 | 186800 | 49.6147 | 290430.9363 | 510.81 | 0
3164 | 5 | 1 | 0 | 0.31455 | 12.8651 | 200 | 12.8651 | 180 | 192.8651 | 0 | 0 | 186600 | 192.8651 | 290623.8014 | 330.81 | 0
3165 | 5 | 1 | 0 | 0.28304 | 11.5762 | 200 | 11.5762 | 180 | 191.5762 | 0 | 0 | 186400 | 191.5762 | 290815.3776 | 150.81 | 0
3166 | 5 | 0 | 0 | 0.30036 | 12.2847 | 0 | 0 | 0 | 0 | 12.2847 | 0 | 186400 | 0 | 290815.3776 | 161.4584 | 0
3167 | 5 | 0 | 0 | 0.46644 | 19.0775 | 0 | 0 | 0 | 0 | 19.0775 | 0 | 186400 | 0 | 290815.3776 | 177.9948 | 0
3168 | 5 | 0 | 0 | 0.4345 | 17.771 | 0 | 0 | 0 | 0 | 17.771 | 0 | 186400 | 0 | 290815.3776 | 193.3987 | 0
3169 | 5 | 0 | 0 | 0.61042 | 24.9664 | 0 | 0 | 0 | 0 | 24.9664 | 0 | 186400 | 0 | 290815.3776 | 215.0395 | 0
3170 | 5 | 0 | 0 | 0.54295 | 22.2067 | 0 | 0 | 0 | 0 | 22.2067 | 0 | 186400 | 0 | 290815.3776 | 234.2883 | 0
3171 | 5 | 0 | 0 | 0.62469 | 25.5496 | 0 | 0 | 0 | 0 | 25.5496 | 0 | 186400 | 0 | 290815.3776 | 256.4347 | 0
3172 | 5 | 0 | 0 | 0.59469 | 24.3227 | 0 | 0 | 0 | 0 | 24.3227 | 0 | 186400 | 0 | 290815.3776 | 277.5176 | 0
3173 | 5 | 0 | 0 | 0.50544 | 20.6723 | 0 | 0 | 0 | 0 | 20.6723 | 0 | 186400 | 0 | 290815.3776 | 295.4364 | 0
3174 | 5 | 0 | 0 | 0.48515 | 19.8426 | 0 | 0 | 0 | 0 | 19.8426 | 0 | 186400 | 0 | 290815.3776 | 312.6359 | 0
3175 | 5 | 0 | 0.12093 | 0.4586 | 53.6812 | 0 | 0 | 0 | 0 | 53.6812 | 0 | 186400 | 0 | 290815.3776 | 359.1667 | 0
3176 | 5 | 1 | 0.41313 | 0.74367 | 149.7285 | 200 | 149.7285 | 50.2715 | 200 | 0 | 0 | 186200 | 200 | 291015.3776 | 308.8952 | 0
3177 | 5 | 1 | 0.74128 | 0.485 | 233.9194 | 200 | 200 | 0 | 200 | 33.9194 | 0 | 186000 | 200 | 291215.3776 | 338.2966 | 0
3178 | 5 | 0 | 1 | 0.54774 | 311.2024 | 0 | 0 | 0 | 0 | 180 | 131.2024 | 186000 | 131.2024 | 291346.58 | 494.3206 | 0
3179 | 5 | 0 | 1 | 0.66623 | 316.049 | 0 | 0 | 0 | 0 | 19.0233 | 200 | 186000 | 200 | 291546.58 | 510.81 | 97.0257
3180 | 5 | 0 | 1 | 0.74937 | 319.4491 | 0 | 0 | 0 | 0 | 0 | 200 | 186000 | 200 | 291746.58 | 510.81 | 119.4491
3181 | 5 | 0 | 1 | 0.99024 | 329.3007 | 0 | 0 | 0 | 0 | 0 | 200 | 186000 | 200 | 291946.58 | 510.81 | 129.3007
3182 | 5 | 0 | 1 | 0.9032 | 325.741 | 0 | 0 | 0 | 0 | 0 | 200 | 186000 | 200 | 292146.58 | 510.81 | 125.741
3183 | 5 | 0 | 1 | 0.9271 | 326.7183 | 0 | 0 | 0 | 0 | 0 | 200 | 186000 | 200 | 292346.58 | 510.81 | 126.7183
3184 | 5 | 0 | 1 | 0.77525 | 320.5076 | 0 | 0 | 0 | 0 | 0 | 200 | 186000 | 200 | 292546.58 | 510.81 | 120.5076
3185 | 5 | 0 | 0.74128 | 0.92285 | 251.8277 | 0 | 0 | 0 | 0 | 0 | 200 | 186000 | 200 | 292746.58 | 510.81 | 51.8277
3186 | 5 | 0 | 0.41313 | 0.553 | 141.9298 | 0 | 0 | 0 | 0 | 0 | 141.9298 | 186000 | 141.9298 | 292888.5098 | 510.81 | 0
3187 | 5 | 0 | 0.12093 | 0.48516 | 54.7672 | 0 | 0 | 0 | 0 | 0 | 54.7672 | 186000 | 54.7672 | 292943.277 | 510.81 | 0
3188 | 5 | 1 | 0 | 0.4212 | 17.2272 | 200 | 17.2272 | 180 | 197.2272 | 0 | 0 | 185800 | 197.2272 | 293140.5042 | 330.81 | 0
3189 | 5 | 1 | 0 | 0.31141 | 12.7368 | 200 | 12.7368 | 180 | 192.7368 | 0 | 0 | 185600 | 192.7368 | 293333.241 | 150.81 | 0
3190 | 5 | 0 | 0 | 0.40953 | 16.75 | 0 | 0 | 0 | 0 | 16.75 | 0 | 185600 | 0 | 293333.241 | 165.3289 | 0
3191 | 5 | 0 | 0 | 0.22888 | 9.3614 | 0 | 0 | 0 | 0 | 9.3614 | 0 | 185600 | 0 | 293333.241 | 173.4433 | 0
3192 | 5 | 0 | 0 | 0.37762 | 15.4449 | 0 | 0 | 0 | 0 | 15.4449 | 0 | 185600 | 0 | 293333.241 | 186.8309 | 0
3193 | 5 | 0 | 0 | 0.31009 | 12.6827 | 0 | 0 | 0 | 0 | 12.6827 | 0 | 185600 | 0 | 293333.241 | 197.8243 | 0
3194 | 5 | 0 | 0 | 0.41358 | 16.9153 | 0 | 0 | 0 | 0 | 16.9153 | 0 | 185600 | 0 | 293333.241 | 212.4865 | 0
3195 | 5 | 0 | 0 | 0.47773 | 19.5391 | 0 | 0 | 0 | 0 | 19.5391 | 0 | 185600 | 0 | 293333.241 | 229.423 | 0
3196 | 5 | 0 | 0 | 0.36755 | 15.0327 | 0 | 0 | 0 | 0 | 15.0327 | 0 | 185600 | 0 | 293333.241 | 242.4534 | 0
3197 | 5 | 0 | 0 | 0.35603 | 14.5616 | 0 | 0 | 0 | 0 | 14.5616 | 0 | 185600 | 0 | 293333.241 | 255.0754 | 0
3198 | 5 | 0 | 0 | 0.43643 | 17.8502 | 0 | 0 | 0 | 0 | 17.8502 | 0 | 185600 | 0 | 293333.241 | 270.5479 | 0
3199 | 5 | 0 | 0.1334 | 0.48954 | 58.548 | 0 | 0 | 0 | 0 | 58.548 | 0 | 185600 | 0 | 293333.241 | 321.2973 | 0
3200 | 5 | 1 | 0.45574 | 0.64204 | 157.876 | 200 | 157.876 | 42.124 | 200 | 0 | 0 | 185400 | 200 | 293533.241 | 279.1732 | 0
3201 | 5 | 1 | 0.81773 | 0.68597 | 264.217 | 200 | 200 | 0 | 200 | 64.217 | 0 | 185200 | 200 | 293733.241 | 334.8365 | 0
3202 | 5 | 0 | 1 | 0.67323 | 316.335 | 0 | 0 | 0 | 0 | 180 | 136.335 | 185200 | 136.335 | 293869.576 | 490.8605 | 0
3203 | 5 | 0 | 1 | 0.77113 | 320.3391 | 0 | 0 | 0 | 0 | 23.0151 | 200 | 185200 | 200 | 294069.576 | 510.81 | 97.3239
3204 | 5 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 0 | 200 | 185200 | 200 | 294269.576 | 510.81 | 129.7
3205 | 5 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 0 | 200 | 185200 | 200 | 294469.576 | 510.81 | 129.7
3206 | 5 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 0 | 200 | 185200 | 200 | 294669.576 | 510.81 | 129.7
3207 | 5 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 0 | 200 | 185200 | 200 | 294869.576 | 510.81 | 129.7
3208 | 5 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 0 | 200 | 185200 | 200 | 295069.576 | 510.81 | 129.7
3209 | 5 | 0 | 0.81773 | 1 | 277.061 | 0 | 0 | 0 | 0 | 0 | 200 | 185200 | 200 | 295269.576 | 510.81 | 77.061
3210 | 5 | 0 | 0.45574 | 1 | 172.5166 | 0 | 0 | 0 | 0 | 0 | 172.5166 | 185200 | 172.5166 | 295442.0925 | 510.81 | 0
3211 | 5 | 0 | 0.1334 | 1 | 79.4259 | 0 | 0 | 0 | 0 | 0 | 79.4259 | 185200 | 79.4259 | 295521.5185 | 510.81 | 0
3212 | 5 | 1 | 0 | 1 | 40.9 | 200 | 40.9 | 159.1 | 200 | 0 | 0 | 185000 | 200 | 295721.5185 | 351.71 | 0
3213 | 5 | 1 | 0 | 1 | 40.9 | 200 | 40.9 | 159.1 | 200 | 0 | 0 | 184800 | 200 | 295921.5185 | 192.61 | 0
3214 | 5 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 184800 | 0 | 295921.5185 | 228.0621 | 0
3215 | 5 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 184800 | 0 | 295921.5185 | 263.5142 | 0
3216 | 5 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 184800 | 0 | 295921.5185 | 298.9664 | 0
3217 | 5 | 0 | 0 | 0.82611 | 33.7878 | 0 | 0 | 0 | 0 | 33.7878 | 0 | 184800 | 0 | 295921.5185 | 328.2536 | 0
3218 | 5 | 0 | 0 | 0.46734 | 19.1141 | 0 | 0 | 0 | 0 | 19.1141 | 0 | 184800 | 0 | 295921.5185 | 344.8218 | 0
3219 | 5 | 0 | 0 | 0.48324 | 19.7646 | 0 | 0 | 0 | 0 | 19.7646 | 0 | 184800 | 0 | 295921.5185 | 361.9537 | 0
3220 | 5 | 0 | 0 | 0.49881 | 20.4014 | 0 | 0 | 0 | 0 | 20.4014 | 0 | 184800 | 0 | 295921.5185 | 379.6377 | 0
3221 | 5 | 0 | 0 | 0.75331 | 30.8103 | 0 | 0 | 0 | 0 | 30.8103 | 0 | 184800 | 0 | 295921.5185 | 406.344 | 0
3222 | 5 | 0 | 0 | 0.4462 | 18.2497 | 0 | 0 | 0 | 0 | 18.2497 | 0 | 184800 | 0 | 295921.5185 | 422.1628 | 0
3223 | 5 | 0 | 0.093522 | 0.55035 | 49.5186 | 0 | 0 | 0 | 0 | 49.5186 | 0 | 184800 | 0 | 295921.5185 | 465.0855 | 0
3224 | 5 | 1 | 0.3195 | 0.41445 | 109.2219 | 200 | 109.2219 | 90.7781 | 200 | 0 | 0 | 184600 | 200 | 296121.5185 | 374.3075 | 0
3225 | 5 | 1 | 0.57328 | 0.35662 | 180.1487 | 200 | 180.1487 | 19.8513 | 200 | 0 | 0 | 184400 | 200 | 296321.5185 | 354.4561 | 0
3226 | 5 | 0 | 0.81349 | 0.48164 | 254.6361 | 0 | 0 | 0 | 0 | 180 | 74.6361 | 184400 | 74.6361 | 296396.1545 | 510.4801 | 0
3227 | 5 | 0 | 1 | 0.61702 | 314.0361 | 0 | 0 | 0 | 0 | 0.38055 | 200 | 184400 | 200 | 296596.1545 | 510.81 | 113.6555
3228 | 5 | 0 | 1 | 0.34904 | 303.0757 | 0 | 0 | 0 | 0 | 0 | 200 | 184400 | 200 | 296796.1545 | 510.81 | 103.0757
3229 | 5 | 0 | 1 | 0.29802 | 300.9892 | 0 | 0 | 0 | 0 | 0 | 200 | 184400 | 200 | 296996.1545 | 510.81 | 100.9892
3230 | 5 | 0 | 1 | 0.30977 | 301.4695 | 0 | 0 | 0 | 0 | 0 | 200 | 184400 | 200 | 297196.1545 | 510.81 | 101.4695
3231 | 5 | 0 | 1 | 0.28027 | 300.2629 | 0 | 0 | 0 | 0 | 0 | 200 | 184400 | 200 | 297396.1545 | 510.81 | 100.2629
3232 | 5 | 0 | 0.81349 | 0.31419 | 247.7874 | 0 | 0 | 0 | 0 | 0 | 200 | 184400 | 200 | 297596.1545 | 510.81 | 47.7874
3233 | 5 | 0 | 0.57328 | 0.36659 | 180.5565 | 0 | 0 | 0 | 0 | 0 | 180.5565 | 184400 | 180.5565 | 297776.711 | 510.81 | 0
3234 | 5 | 0 | 0.3195 | 0.33398 | 105.9308 | 0 | 0 | 0 | 0 | 0 | 105.9308 | 184400 | 105.9308 | 297882.6418 | 510.81 | 0
3235 | 5 | 0 | 0.093522 | 0.39251 | 43.0628 | 0 | 0 | 0 | 0 | 0 | 43.0628 | 184400 | 43.0628 | 297925.7046 | 510.81 | 0
3236 | 5 | 1 | 0 | 0.23808 | 9.7375 | 200 | 9.7375 | 180 | 189.7375 | 0 | 0 | 184200 | 189.7375 | 298115.4421 | 330.81 | 0
3237 | 5 | 1 | 0 | 0.22549 | 9.2224 | 200 | 9.2224 | 180 | 189.2224 | 0 | 0 | 184000 | 189.2224 | 298304.6645 | 150.81 | 0
3238 | 5 | 0 | 0 | 0.25186 | 10.301 | 0 | 0 | 0 | 0 | 10.301 | 0 | 184000 | 0 | 298304.6645 | 159.7389 | 0
3239 | 5 | 0 | 0 | 0.22337 | 9.1358 | 0 | 0 | 0 | 0 | 9.1358 | 0 | 184000 | 0 | 298304.6645 | 167.6578 | 0
3240 | 5 | 0 | 0 | 0.2176 | 8.9 | 0 | 0 | 0 | 0 | 8.9 | 0 | 184000 | 0 | 298304.6645 | 175.3723 | 0
3241 | 5 | 0 | 0 | 0.21425 | 8.7629 | 0 | 0 | 0 | 0 | 8.7629 | 0 | 184000 | 0 | 298304.6645 | 182.968 | 0
3242 | 5 | 0 | 0 | 0.17849 | 7.3002 | 0 | 0 | 0 | 0 | 7.3002 | 0 | 184000 | 0 | 298304.6645 | 189.2958 | 0
3243 | 5 | 0 | 0 | 0.16303 | 6.6678 | 0 | 0 | 0 | 0 | 6.6678 | 0 | 184000 | 0 | 298304.6645 | 195.0754 | 0
3244 | 5 | 0 | 0 | 0.17604 | 7.2002 | 0 | 0 | 0 | 0 | 7.2002 | 0 | 184000 | 0 | 298304.6645 | 201.3165 | 0
3245 | 5 | 0 | 0 | 0.22371 | 9.1497 | 0 | 0 | 0 | 0 | 9.1497 | 0 | 184000 | 0 | 298304.6645 | 209.2475 | 0
3246 | 5 | 0 | 0 | 0.25361 | 10.3725 | 0 | 0 | 0 | 0 | 10.3725 | 0 | 184000 | 0 | 298304.6645 | 218.2383 | 0
3247 | 5 | 0 | 0.12647 | 0.27436 | 47.7448 | 0 | 0 | 0 | 0 | 47.7448 | 0 | 184000 | 0 | 298304.6645 | 259.6236 | 0
3248 | 5 | 1 | 0.43205 | 0.22987 | 134.177 | 200 | 134.177 | 65.823 | 200 | 0 | 0 | 183800 | 200 | 298504.6645 | 193.8006 | 0
3249 | 5 | 1 | 0.77523 | 0.21858 | 232.8258 | 200 | 200 | 0 | 200 | 32.8258 | 0 | 183600 | 200 | 298704.6645 | 222.254 | 0
3250 | 5 | 0 | 1 | 0.25564 | 299.2558 | 0 | 0 | 0 | 0 | 180 | 119.2558 | 183600 | 119.2558 | 298823.9203 | 378.278 | 0
3251 | 5 | 0 | 1 | 0.35917 | 303.49 | 0 | 0 | 0 | 0 | 152.8981 | 150.5919 | 183600 | 150.5919 | 298974.5122 | 510.81 | 0
3252 | 5 | 0 | 1 | 0.45095 | 307.2438 | 0 | 0 | 0 | 0 | 0 | 200 | 183600 | 200 | 299174.5122 | 510.81 | 107.2438
3253 | 5 | 0 | 1 | 0.34124 | 302.7569 | 0 | 0 | 0 | 0 | 0 | 200 | 183600 | 200 | 299374.5122 | 510.81 | 102.7569
3254 | 5 | 0 | 1 | 0.32664 | 302.1595 | 0 | 0 | 0 | 0 | 0 | 200 | 183600 | 200 | 299574.5122 | 510.81 | 102.1595
3255 | 5 | 0 | 1 | 0.50155 | 309.3134 | 0 | 0 | 0 | 0 | 0 | 200 | 183600 | 200 | 299774.5122 | 510.81 | 109.3134
3256 | 5 | 0 | 1 | 0.45783 | 307.5254 | 0 | 0 | 0 | 0 | 0 | 200 | 183600 | 200 | 299974.5122 | 510.81 | 107.5254
3257 | 5 | 0 | 0.77523 | 0.50894 | 244.7013 | 0 | 0 | 0 | 0 | 0 | 200 | 183600 | 200 | 300174.5122 | 510.81 | 44.7013
3258 | 5 | 0 | 0.43205 | 0.46911 | 143.9621 | 0 | 0 | 0 | 0 | 0 | 143.9621 | 183600 | 143.9621 | 300318.4743 | 510.81 | 0
3259 | 5 | 0 | 0.12647 | 0.63888 | 62.6536 | 0 | 0 | 0 | 0 | 0 | 62.6536 | 183600 | 62.6536 | 300381.1279 | 510.81 | 0
3260 | 5 | 1 | 0 | 0.70988 | 29.034 | 200 | 29.034 | 170.966 | 200 | 0 | 0 | 183400 | 200 | 300581.1279 | 339.844 | 0
3261 | 5 | 1 | 0 | 0.65687 | 26.8661 | 200 | 26.8661 | 173.1339 | 200 | 0 | 0 | 183200 | 200 | 300781.1279 | 166.7101 | 0
3262 | 5 | 0 | 0 | 0.6044 | 24.72 | 0 | 0 | 0 | 0 | 24.72 | 0 | 183200 | 0 | 300781.1279 | 188.1374 | 0
3263 | 5 | 0 | 0 | 0.44086 | 18.0312 | 0 | 0 | 0 | 0 | 18.0312 | 0 | 183200 | 0 | 300781.1279 | 203.7668 | 0
3264 | 5 | 0 | 0 | 0.53451 | 21.8614 | 0 | 0 | 0 | 0 | 21.8614 | 0 | 183200 | 0 | 300781.1279 | 222.7163 | 0
3265 | 5 | 0 | 0 | 0.5065 | 20.7159 | 0 | 0 | 0 | 0 | 20.7159 | 0 | 183200 | 0 | 300781.1279 | 240.6729 | 0
3266 | 5 | 0 | 0 | 0.70663 | 28.9012 | 0 | 0 | 0 | 0 | 28.9012 | 0 | 183200 | 0 | 300781.1279 | 265.7245 | 0
3267 | 5 | 0 | 0 | 0.5828 | 23.8364 | 0 | 0 | 0 | 0 | 23.8364 | 0 | 183200 | 0 | 300781.1279 | 286.3859 | 0
3268 | 5 | 0 | 0 | 0.61578 | 25.1852 | 0 | 0 | 0 | 0 | 25.1852 | 0 | 183200 | 0 | 300781.1279 | 308.2164 | 0
3269 | 5 | 0 | 0 | 0.71464 | 29.2288 | 0 | 0 | 0 | 0 | 29.2288 | 0 | 183200 | 0 | 300781.1279 | 333.552 | 0
3270 | 5 | 0 | 0 | 0.53648 | 21.9418 | 0 | 0 | 0 | 0 | 21.9418 | 0 | 183200 | 0 | 300781.1279 | 352.5711 | 0
3271 | 5 | 0 | 0.12354 | 0.45485 | 54.2825 | 0 | 0 | 0 | 0 | 54.2825 | 0 | 183200 | 0 | 300781.1279 | 399.6232 | 0
3272 | 5 | 1 | 0.42206 | 0.78336 | 153.9294 | 200 | 153.9294 | 46.0706 | 200 | 0 | 0 | 183000 | 200 | 300981.1279 | 353.5525 | 0
3273 | 5 | 1 | 0.7573 | 0.88617 | 254.9526 | 200 | 200 | 0 | 200 | 54.9526 | 0 | 182800 | 200 | 301181.1279 | 401.1855 | 0
3274 | 5 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 126.4704 | 200 | 182800 | 200 | 301381.1279 | 510.81 | 3.2296
3275 | 5 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 0 | 200 | 182800 | 200 | 301581.1279 | 510.81 | 129.7
3276 | 5 | 0 | 1 | 0.85469 | 323.7567 | 0 | 0 | 0 | 0 | 0 | 200 | 182800 | 200 | 301781.1279 | 510.81 | 123.7567
3277 | 5 | 0 | 1 | 0.92166 | 326.496 | 0 | 0 | 0 | 0 | 0 | 200 | 182800 | 200 | 301981.1279 | 510.81 | 126.496
3278 | 5 | 0 | 1 | 0.94622 | 327.5004 | 0 | 0 | 0 | 0 | 0 | 200 | 182800 | 200 | 302181.1279 | 510.81 | 127.5004
3279 | 5 | 0 | 1 | 0.74422 | 319.2384 | 0 | 0 | 0 | 0 | 0 | 200 | 182800 | 200 | 302381.1279 | 510.81 | 119.2384
3280 | 5 | 0 | 1 | 0.40324 | 305.2926 | 0 | 0 | 0 | 0 | 0 | 200 | 182800 | 200 | 302581.1279 | 510.81 | 105.2926
3281 | 5 | 0 | 0.7573 | 0.33806 | 232.535 | 0 | 0 | 0 | 0 | 0 | 200 | 182800 | 200 | 302781.1279 | 510.81 | 32.535
3282 | 5 | 0 | 0.42206 | 0.49495 | 142.1337 | 0 | 0 | 0 | 0 | 0 | 142.1337 | 182800 | 142.1337 | 302923.2616 | 510.81 | 0
3283 | 5 | 0 | 0.12354 | 0.29166 | 47.6078 | 0 | 0 | 0 | 0 | 0 | 47.6078 | 182800 | 47.6078 | 302970.8694 | 510.81 | 0
3284 | 5 | 1 | 0 | 0.33539 | 13.7176 | 200 | 13.7176 | 180 | 193.7176 | 0 | 0 | 182600 | 193.7176 | 303164.5869 | 330.81 | 0
3285 | 5 | 1 | 0 | 0.38506 | 15.749 | 200 | 15.749 | 180 | 195.749 | 0 | 0 | 182400 | 195.749 | 303360.336 | 150.81 | 0
3286 | 5 | 0 | 0 | 0.42311 | 17.3051 | 0 | 0 | 0 | 0 | 17.3051 | 0 | 182400 | 0 | 303360.336 | 165.8101 | 0
3287 | 5 | 0 | 0 | 0.36671 | 14.9982 | 0 | 0 | 0 | 0 | 14.9982 | 0 | 182400 | 0 | 303360.336 | 178.8105 | 0
3288 | 5 | 0 | 0 | 0.28852 | 11.8005 | 0 | 0 | 0 | 0 | 11.8005 | 0 | 182400 | 0 | 303360.336 | 189.0392 | 0
3289 | 5 | 0 | 0 | 0.29798 | 12.1874 | 0 | 0 | 0 | 0 | 12.1874 | 0 | 182400 | 0 | 303360.336 | 199.6032 | 0
3290 | 5 | 0 | 0 | 0.29874 | 12.2184 | 0 | 0 | 0 | 0 | 12.2184 | 0 | 182400 | 0 | 303360.336 | 210.1941 | 0
3291 | 5 | 0 | 0 | 0.22069 | 9.0263 | 0 | 0 | 0 | 0 | 9.0263 | 0 | 182400 | 0 | 303360.336 | 218.0181 | 0
3292 | 5 | 0 | 0 | 0.25295 | 10.3457 | 0 | 0 | 0 | 0 | 10.3457 | 0 | 182400 | 0 | 303360.336 | 226.9858 | 0
3293 | 5 | 0 | 0 | 0.37859 | 15.4844 | 0 | 0 | 0 | 0 | 15.4844 | 0 | 182400 | 0 | 303360.336 | 240.4077 | 0
3294 | 5 | 0 | 0 | 0.43769 | 17.9016 | 0 | 0 | 0 | 0 | 17.9016 | 0 | 182400 | 0 | 303360.336 | 255.9248 | 0
3295 | 5 | 0 | 0.10977 | 0.60573 | 56.4744 | 0 | 0 | 0 | 0 | 56.4744 | 0 | 182400 | 0 | 303360.336 | 304.8768 | 0
3296 | 5 | 1 | 0.37499 | 0.78848 | 140.5457 | 200 | 140.5457 | 59.4543 | 200 | 0 | 0 | 182200 | 200 | 303560.336 | 245.4225 | 0
3297 | 5 | 1 | 0.67285 | 0.92102 | 231.9879 | 200 | 200 | 0 | 200 | 31.9879 | 0 | 182000 | 200 | 303760.336 | 273.1497 | 0
3298 | 5 | 0 | 0.95478 | 0.95748 | 314.9022 | 0 | 0 | 0 | 0 | 180 | 134.9022 | 182000 | 134.9022 | 303895.2382 | 429.1737 | 0
3299 | 5 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 94.1813 | 200 | 182000 | 200 | 304095.2382 | 510.81 | 35.5187
3300 | 5 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 0 | 200 | 182000 | 200 | 304295.2382 | 510.81 | 129.7
3301 | 5 | 0 | 1 | 0.91227 | 326.112 | 0 | 0 | 0 | 0 | 0 | 200 | 182000 | 200 | 304495.2382 | 510.81 | 126.112
3302 | 5 | 0 | 1 | 0.91345 | 326.1602 | 0 | 0 | 0 | 0 | 0 | 200 | 182000 | 200 | 304695.2382 | 510.81 | 126.1602
3303 | 5 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 0 | 200 | 182000 | 200 | 304895.2382 | 510.81 | 129.7
3304 | 5 | 0 | 0.95478 | 1 | 316.6413 | 0 | 0 | 0 | 0 | 0 | 200 | 182000 | 200 | 305095.2382 | 510.81 | 116.6413
3305 | 5 | 0 | 0.67285 | 1 | 235.2182 | 0 | 0 | 0 | 0 | 0 | 200 | 182000 | 200 | 305295.2382 | 510.81 | 35.2182
3306 | 5 | 0 | 0.37499 | 1 | 149.1968 | 0 | 0 | 0 | 0 | 0 | 149.1968 | 182000 | 149.1968 | 305444.435 | 510.81 | 0
3307 | 5 | 0 | 0.10977 | 1 | 72.6001 | 0 | 0 | 0 | 0 | 0 | 72.6001 | 182000 | 72.6001 | 305517.0351 | 510.81 | 0
3308 | 5 | 1 | 0 | 1 | 40.9 | 200 | 40.9 | 159.1 | 200 | 0 | 0 | 181800 | 200 | 305717.0351 | 351.71 | 0
3309 | 5 | 1 | 0 | 0.94189 | 38.5233 | 200 | 38.5233 | 161.4767 | 200 | 0 | 0 | 181600 | 200 | 305917.0351 | 190.2333 | 0
3310 | 5 | 0 | 0 | 0.79198 | 32.3921 | 0 | 0 | 0 | 0 | 32.3921 | 0 | 181600 | 0 | 305917.0351 | 218.3107 | 0
3311 | 5 | 0 | 0 | 0.73272 | 29.9682 | 0 | 0 | 0 | 0 | 29.9682 | 0 | 181600 | 0 | 305917.0351 | 244.2872 | 0
3312 | 5 | 0 | 0 | 0.56948 | 23.2918 | 0 | 0 | 0 | 0 | 23.2918 | 0 | 181600 | 0 | 305917.0351 | 264.4765 | 0
3313 | 5 | 0 | 0 | 0.79338 | 32.4492 | 0 | 0 | 0 | 0 | 32.4492 | 0 | 181600 | 0 | 305917.0351 | 292.6035 | 0
3314 | 5 | 0 | 0 | 0.75328 | 30.8094 | 0 | 0 | 0 | 0 | 30.8094 | 0 | 181600 | 0 | 305917.0351 | 319.309 | 0
3315 | 5 | 0 | 0 | 0.69305 | 28.3458 | 0 | 0 | 0 | 0 | 28.3458 | 0 | 181600 | 0 | 305917.0351 | 343.8792 | 0
3316 | 5 | 0 | 0 | 0.61248 | 25.0503 | 0 | 0 | 0 | 0 | 25.0503 | 0 | 181600 | 0 | 305917.0351 | 365.5928 | 0
3317 | 5 | 0 | 0 | 0.52979 | 21.6684 | 0 | 0 | 0 | 0 | 21.6684 | 0 | 181600 | 0 | 305917.0351 | 384.3749 | 0
3318 | 5 | 0 | 0 | 0.5927 | 24.2416 | 0 | 0 | 0 | 0 | 24.2416 | 0 | 181600 | 0 | 305917.0351 | 405.3875 | 0
3319 | 5 | 0 | 0.11506 | 0.7646 | 64.5021 | 0 | 0 | 0 | 0 | 64.5021 | 0 | 181600 | 0 | 305917.0351 | 461.298 | 0
3320 | 5 | 1 | 0.39309 | 0.75871 | 144.5542 | 200 | 144.5542 | 55.4458 | 200 | 0 | 0 | 181400 | 200 | 306117.0351 | 405.8522 | 0
3321 | 5 | 1 | 0.70532 | 0.62596 | 229.2971 | 200 | 200 | 0 | 200 | 29.2971 | 0 | 181200 | 200 | 306317.0351 | 431.2469 | 0
3322 | 5 | 0 | 1 | 0.95031 | 327.6678 | 0 | 0 | 0 | 0 | 91.7894 | 200 | 181200 | 200 | 306517.0351 | 510.81 | 35.8784
3323 | 5 | 0 | 1 | 0.78375 | 320.8553 | 0 | 0 | 0 | 0 | 0 | 200 | 181200 | 200 | 306717.0351 | 510.81 | 120.8553
3324 | 5 | 0 | 1 | 0.96492 | 328.2652 | 0 | 0 | 0 | 0 | 0 | 200 | 181200 | 200 | 306917.0351 | 510.81 | 128.2652
3325 | 5 | 0 | 1 | 0.90009 | 325.6135 | 0 | 0 | 0 | 0 | 0 | 200 | 181200 | 200 | 307117.0351 | 510.81 | 125.6135
3326 | 5 | 0 | 1 | 0.79514 | 321.3213 | 0 | 0 | 0 | 0 | 0 | 200 | 181200 | 200 | 307317.0351 | 510.81 | 121.3213
3327 | 5 | 0 | 1 | 0.64308 | 315.102 | 0 | 0 | 0 | 0 | 0 | 200 | 181200 | 200 | 307517.0351 | 510.81 | 115.102
3328 | 5 | 0 | 1 | 0.67714 | 316.4952 | 0 | 0 | 0 | 0 | 0 | 200 | 181200 | 200 | 307717.0351 | 510.81 | 116.4952
3329 | 5 | 0 | 0.70532 | 0.57118 | 227.0567 | 0 | 0 | 0 | 0 | 0 | 200 | 181200 | 200 | 307917.0351 | 510.81 | 27.0567
3330 | 5 | 0 | 0.39309 | 0.31604 | 126.4491 | 0 | 0 | 0 | 0 | 0 | 126.4491 | 181200 | 126.4491 | 308043.4842 | 510.81 | 0
3331 | 5 | 0 | 0.11506 | 0.24434 | 43.2234 | 0 | 0 | 0 | 0 | 0 | 43.2234 | 181200 | 43.2234 | 308086.7076 | 510.81 | 0
3332 | 5 | 1 | 0 | 0.30928 | 12.6494 | 200 | 12.6494 | 180 | 192.6494 | 0 | 0 | 181000 | 192.6494 | 308279.3571 | 330.81 | 0
3333 | 5 | 1 | 0 | 0.24265 | 9.9243 | 200 | 9.9243 | 180 | 189.9243 | 0 | 0 | 180800 | 189.9243 | 308469.2813 | 150.81 | 0
3334 | 5 | 0 | 0 | 0.20796 | 8.5056 | 0 | 0 | 0 | 0 | 8.5056 | 0 | 180800 | 0 | 308469.2813 | 158.1827 | 0
3335 | 5 | 0 | 0 | 0.15987 | 6.5386 | 0 | 0 | 0 | 0 | 6.5386 | 0 | 180800 | 0 | 308469.2813 | 163.8503 | 0
3336 | 5 | 0 | 0 | 0.15508 | 6.3426 | 0 | 0 | 0 | 0 | 6.3426 | 0 | 180800 | 0 | 308469.2813 | 169.3481 | 0
3337 | 5 | 0 | 0 | 0.22409 | 9.1655 | 0 | 0 | 0 | 0 | 9.1655 | 0 | 180800 | 0 | 308469.2813 | 177.2927 | 0
3338 | 5 | 0 | 0 | 0.19633 | 8.0299 | 0 | 0 | 0 | 0 | 8.0299 | 0 | 180800 | 0 | 308469.2813 | 184.2531 | 0
3339 | 5 | 0 | 0 | 0.25534 | 10.4433 | 0 | 0 | 0 | 0 | 10.4433 | 0 | 180800 | 0 | 308469.2813 | 193.3053 | 0
3340 | 5 | 0 | 0 | 0.32331 | 13.2232 | 0 | 0 | 0 | 0 | 13.2232 | 0 | 180800 | 0 | 308469.2813 | 204.7672 | 0
3341 | 5 | 0 | 0 | 0.28178 | 11.5248 | 0 | 0 | 0 | 0 | 11.5248 | 0 | 180800 | 0 | 308469.2813 | 214.7569 | 0
3342 | 5 | 0 | 0 | 0.36156 | 14.7876 | 0 | 0 | 0 | 0 | 14.7876 | 0 | 180800 | 0 | 308469.2813 | 227.5748 | 0
3343 | 5 | 0 | 0.11049 | 0.55505 | 54.6109 | 0 | 0 | 0 | 0 | 54.6109 | 0 | 180800 | 0 | 308469.2813 | 274.9115 | 0
3344 | 5 | 1 | 0.37747 | 0.39851 | 125.3119 | 200 | 125.3119 | 74.6881 | 200 | 0 | 0 | 180600 | 200 | 308669.2813 | 200.2234 | 0
3345 | 5 | 1 | 0.67729 | 0.4488 | 213.9586 | 200 | 200 | 0 | 200 | 13.9586 | 0 | 180400 | 200 | 308869.2813 | 212.3226 | 0
3346 | 5 | 0 | 0.9611 | 0.64625 | 303.9958 | 0 | 0 | 0 | 0 | 180 | 123.9958 | 180400 | 123.9958 | 308993.2771 | 368.3466 | 0
3347 | 5 | 0 | 1 | 0.71874 | 318.1965 | 0 | 0 | 0 | 0 | 164.3555 | 153.841 | 180400 | 153.841 | 309147.1182 | 510.81 | 0
3348 | 5 | 0 | 1 | 0.73482 | 318.854 | 0 | 0 | 0 | 0 | 0 | 200 | 180400 | 200 | 309347.1182 | 510.81 | 118.854
3349 | 5 | 0 | 1 | 0.75255 | 319.5791 | 0 | 0 | 0 | 0 | 0 | 200 | 180400 | 200 | 309547.1182 | 510.81 | 119.5791
3350 | 5 | 0 | 1 | 0.82456 | 322.5246 | 0 | 0 | 0 | 0 | 0 | 200 | 180400 | 200 | 309747.1182 | 510.81 | 122.5246
3351 | 5 | 0 | 1 | 0.65193 | 315.4641 | 0 | 0 | 0 | 0 | 0 | 200 | 180400 | 200 | 309947.1182 | 510.81 | 115.4641
3352 | 5 | 0 | 0.9611 | 0.62181 | 302.9962 | 0 | 0 | 0 | 0 | 0 | 200 | 180400 | 200 | 310147.1182 | 510.81 | 102.9962
3353 | 5 | 0 | 0.67729 | 0.4042 | 212.1346 | 0 | 0 | 0 | 0 | 0 | 200 | 180400 | 200 | 310347.1182 | 510.81 | 12.1346
3354 | 5 | 0 | 0.37747 | 0.25376 | 119.3914 | 0 | 0 | 0 | 0 | 0 | 119.3914 | 180400 | 119.3914 | 310466.5096 | 510.81 | 0
3355 | 5 | 0 | 0.11049 | 0.25011 | 42.1392 | 0 | 0 | 0 | 0 | 0 | 42.1392 | 180400 | 42.1392 | 310508.6487 | 510.81 | 0
3356 | 5 | 1 | 0 | 0.14254 | 5.83 | 200 | 5.83 | 180 | 185.83 | 0 | 0 | 180200 | 185.83 | 310694.4788 | 330.81 | 0
3357 | 5 | 1 | 0 | 0.17484 | 7.151 | 200 | 7.151 | 180 | 187.151 | 0 | 0 | 180000 | 187.151 | 310881.6297 | 150.81 | 0
3358 | 5 | 0 | 0 | 0.10045 | 4.1085 | 0 | 0 | 0 | 0 | 4.1085 | 0 | 180000 | 0 | 310881.6297 | 154.3712 | 0
3359 | 5 | 0 | 0 | 0.099705 | 4.0779 | 0 | 0 | 0 | 0 | 4.0779 | 0 | 180000 | 0 | 310881.6297 | 157.906 | 0
3360 | 5 | 0 | 0 | 0.079745 | 3.2616 | 0 | 0 | 0 | 0 | 3.2616 | 0 | 180000 | 0 | 310881.6297 | 160.7331 | 0
3361 | 5 | 0 | 0 | 0.10043 | 4.1077 | 0 | 0 | 0 | 0 | 4.1077 | 0 | 180000 | 0 | 310881.6297 | 164.2936 | 0
3362 | 5 | 0 | 0 | 0.12575 | 5.143 | 0 | 0 | 0 | 0 | 5.143 | 0 | 180000 | 0 | 310881.6297 | 168.7516 | 0
3363 | 5 | 0 | 0 | 0.11828 | 4.8376 | 0 | 0 | 0 | 0 | 4.8376 | 0 | 180000 | 0 | 310881.6297 | 172.9448 | 0
3364 | 5 | 0 | 0 | 0.10692 | 4.3729 | 0 | 0 | 0 | 0 | 4.3729 | 0 | 180000 | 0 | 310881.6297 | 176.7352 | 0
3365 | 5 | 0 | 0 | 0.12817 | 5.2423 | 0 | 0 | 0 | 0 | 5.2423 | 0 | 180000 | 0 | 310881.6297 | 181.2792 | 0
3366 | 5 | 0 | 0 | 0.12093 | 4.9462 | 0 | 0 | 0 | 0 | 4.9462 | 0 | 180000 | 0 | 310881.6297 | 185.5665 | 0
3367 | 5 | 0 | 0.13224 | 0.12157 | 43.163 | 0 | 0 | 0 | 0 | 43.163 | 0 | 180000 | 0 | 310881.6297 | 222.9802 | 0
3368 | 5 | 1 | 0.45177 | 0.19696 | 138.5275 | 200 | 138.5275 | 61.4725 | 200 | 0 | 0 | 179800 | 200 | 311081.6297 | 161.5077 | 0
3369 | 5 | 1 | 0.81062 | 0.30776 | 246.6946 | 200 | 200 | 0 | 200 | 46.6946 | 0 | 179600 | 200 | 311281.6297 | 201.9827 | 0
3370 | 5 | 0 | 1 | 0.40222 | 305.251 | 0 | 0 | 0 | 0 | 180 | 125.251 | 179600 | 125.251 | 311406.8807 | 358.0067 | 0
3371 | 5 | 0 | 1 | 0.3632 | 303.6548 | 0 | 0 | 0 | 0 | 176.2844 | 127.3704 | 179600 | 127.3704 | 311534.2511 | 510.81 | 0
3372 | 5 | 0 | 1 | 0.34329 | 302.8405 | 0 | 0 | 0 | 0 | 0 | 200 | 179600 | 200 | 311734.2511 | 510.81 | 102.8405
3373 | 5 | 0 | 1 | 0.41995 | 305.9761 | 0 | 0 | 0 | 0 | 0 | 200 | 179600 | 200 | 311934.2511 | 510.81 | 105.9761
3374 | 5 | 0 | 1 | 0.51431 | 309.8352 | 0 | 0 | 0 | 0 | 0 | 200 | 179600 | 200 | 312134.2511 | 510.81 | 109.8352
3375 | 5 | 0 | 1 | 0.39505 | 304.9577 | 0 | 0 | 0 | 0 | 0 | 200 | 179600 | 200 | 312334.2511 | 510.81 | 104.9577
3376 | 5 | 0 | 1 | 0.34525 | 302.9208 | 0 | 0 | 0 | 0 | 0 | 200 | 179600 | 200 | 312534.2511 | 510.81 | 102.9208
3377 | 5 | 0 | 0.81062 | 0.44685 | 252.3835 | 0 | 0 | 0 | 0 | 0 | 200 | 179600 | 200 | 312734.2511 | 510.81 | 52.3835
3378 | 5 | 0 | 0.45177 | 0.76189 | 161.6335 | 0 | 0 | 0 | 0 | 0 | 161.6335 | 179600 | 161.6335 | 312895.8846 | 510.81 | 0
3379 | 5 | 0 | 0.13224 | 0.51668 | 59.323 | 0 | 0 | 0 | 0 | 0 | 59.323 | 179600 | 59.323 | 312955.2076 | 510.81 | 0
3380 | 5 | 1 | 0 | 0.67073 | 27.4331 | 200 | 27.4331 | 172.5669 | 200 | 0 | 0 | 179400 | 200 | 313155.2076 | 338.2431 | 0
3381 | 5 | 1 | 0 | 0.88714 | 36.284 | 200 | 36.284 | 163.716 | 200 | 0 | 0 | 179200 | 200 | 313355.2076 | 174.527 | 0
3382 | 5 | 0 | 0 | 0.81251 | 33.2315 | 0 | 0 | 0 | 0 | 33.2315 | 0 | 179200 | 0 | 313355.2076 | 203.3321 | 0
3383 | 5 | 0 | 0 | 0.65216 | 26.6732 | 0 | 0 | 0 | 0 | 26.6732 | 0 | 179200 | 0 | 313355.2076 | 226.4525 | 0
3384 | 5 | 0 | 0 | 0.51709 | 21.1488 | 0 | 0 | 0 | 0 | 21.1488 | 0 | 179200 | 0 | 313355.2076 | 244.7842 | 0
3385 | 5 | 0 | 0 | 0.38027 | 15.5529 | 0 | 0 | 0 | 0 | 15.5529 | 0 | 179200 | 0 | 313355.2076 | 258.2655 | 0
3386 | 5 | 0 | 0 | 0.40331 | 16.4954 | 0 | 0 | 0 | 0 | 16.4954 | 0 | 179200 | 0 | 313355.2076 | 272.5637 | 0
3387 | 5 | 0 | 0 | 0.33689 | 13.7789 | 0 | 0 | 0 | 0 | 13.7789 | 0 | 179200 | 0 | 313355.2076 | 284.5072 | 0
3388 | 5 | 0 | 0 | 0.33473 | 13.6905 | 0 | 0 | 0 | 0 | 13.6905 | 0 | 179200 | 0 | 313355.2076 | 296.3741 | 0
3389 | 5 | 0 | 0 | 0.28752 | 11.7594 | 0 | 0 | 0 | 0 | 11.7594 | 0 | 179200 | 0 | 313355.2076 | 306.5672 | 0
3390 | 5 | 0 | 0 | 0.29902 | 12.23 | 0 | 0 | 0 | 0 | 12.23 | 0 | 179200 | 0 | 313355.2076 | 317.1682 | 0
3391 | 5 | 0 | 0.097312 | 0.25065 | 38.3552 | 0 | 0 | 0 | 0 | 38.3552 | 0 | 179200 | 0 | 313355.2076 | 350.4144 | 0
3392 | 5 | 1 | 0.33245 | 0.21748 | 104.9057 | 200 | 104.9057 | 95.0943 | 200 | 0 | 0 | 179000 | 200 | 313555.2076 | 255.3201 | 0
3393 | 5 | 1 | 0.59651 | 0.32958 | 185.7529 | 200 | 185.7529 | 14.2471 | 200 | 0 | 0 | 178800 | 200 | 313755.2076 | 241.073 | 0
3394 | 5 | 0 | 0.84646 | 0.44364 | 262.6032 | 0 | 0 | 0 | 0 | 180 | 82.6032 | 178800 | 82.6032 | 313837.8109 | 397.097 | 0
3395 | 5 | 0 | 1 | 0.34079 | 302.7384 | 0 | 0 | 0 | 0 | 131.1871 | 171.5513 | 178800 | 171.5513 | 314009.3622 | 510.81 | 0
3396 | 5 | 0 | 1 | 0.41006 | 305.5714 | 0 | 0 | 0 | 0 | 0 | 200 | 178800 | 200 | 314209.3622 | 510.81 | 105.5714
3397 | 5 | 0 | 1 | 0.33231 | 302.3914 | 0 | 0 | 0 | 0 | 0 | 200 | 178800 | 200 | 314409.3622 | 510.81 | 102.3914
3398 | 5 | 0 | 1 | 0.45685 | 307.4853 | 0 | 0 | 0 | 0 | 0 | 200 | 178800 | 200 | 314609.3622 | 510.81 | 107.4853
3399 | 5 | 0 | 1 | 0.47656 | 308.2911 | 0 | 0 | 0 | 0 | 0 | 200 | 178800 | 200 | 314809.3622 | 510.81 | 108.2911
3400 | 5 | 0 | 0.84646 | 0.57515 | 267.9821 | 0 | 0 | 0 | 0 | 0 | 200 | 178800 | 200 | 315009.3622 | 510.81 | 67.9821
3401 | 5 | 0 | 0.59651 | 0.44371 | 190.4208 | 0 | 0 | 0 | 0 | 0 | 190.4208 | 178800 | 190.4208 | 315199.7829 | 510.81 | 0
3402 | 5 | 0 | 0.33245 | 0.43354 | 113.7426 | 0 | 0 | 0 | 0 | 0 | 113.7426 | 178800 | 113.7426 | 315313.5255 | 510.81 | 0
3403 | 5 | 0 | 0.097312 | 0.36012 | 42.8327 | 0 | 0 | 0 | 0 | 0 | 42.8327 | 178800 | 42.8327 | 315356.3582 | 510.81 | 0
3404 | 5 | 1 | 0 | 0.40162 | 16.4263 | 200 | 16.4263 | 180 | 196.4263 | 0 | 0 | 178600 | 196.4263 | 315552.7845 | 330.81 | 0
3405 | 5 | 1 | 0 | 0.38067 | 15.5693 | 200 | 15.5693 | 180 | 195.5693 | 0 | 0 | 178400 | 195.5693 | 315748.3539 | 150.81 | 0
3406 | 5 | 0 | 0 | 0.25677 | 10.5018 | 0 | 0 | 0 | 0 | 10.5018 | 0 | 178400 | 0 | 315748.3539 | 159.913 | 0
3407 | 5 | 0 | 0 | 0.20405 | 8.3456 | 0 | 0 | 0 | 0 | 8.3456 | 0 | 178400 | 0 | 315748.3539 | 167.147 | 0
3408 | 5 | 0 | 0 | 0.19239 | 7.8689 | 0 | 0 | 0 | 0 | 7.8689 | 0 | 178400 | 0 | 315748.3539 | 173.9678 | 0
3409 | 5 | 0 | 0 | 0.21062 | 8.6145 | 0 | 0 | 0 | 0 | 8.6145 | 0 | 178400 | 0 | 315748.3539 | 181.4348 | 0
3410 | 5 | 0 | 0 | 0.23425 | 9.5808 | 0 | 0 | 0 | 0 | 9.5808 | 0 | 178400 | 0 | 315748.3539 | 189.7394 | 0
3411 | 5 | 0 | 0 | 0.27159 | 11.1081 | 0 | 0 | 0 | 0 | 11.1081 | 0 | 178400 | 0 | 315748.3539 | 199.3679 | 0
3412 | 5 | 0 | 0 | 0.21634 | 8.8484 | 0 | 0 | 0 | 0 | 8.8484 | 0 | 178400 | 0 | 315748.3539 | 207.0377 | 0
3413 | 5 | 0 | 0 | 0.19561 | 8.0005 | 0 | 0 | 0 | 0 | 8.0005 | 0 | 178400 | 0 | 315748.3539 | 213.9726 | 0
3414 | 5 | 0 | 0 | 0.19547 | 7.9946 | 0 | 0 | 0 | 0 | 7.9946 | 0 | 178400 | 0 | 315748.3539 | 220.9023 | 0
3415 | 5 | 0 | 0.11135 | 0.25089 | 42.4196 | 0 | 0 | 0 | 0 | 42.4196 | 0 | 178400 | 0 | 315748.3539 | 257.6716 | 0
3416 | 5 | 1 | 0.38041 | 0.29721 | 122.018 | 200 | 122.018 | 77.982 | 200 | 0 | 0 | 178200 | 200 | 315948.3539 | 179.6896 | 0
3417 | 5 | 1 | 0.68257 | 0.17887 | 204.4425 | 200 | 200 | 0 | 200 | 4.4425 | 0 | 178000 | 200 | 316148.3539 | 183.5404 | 0
3418 | 5 | 0 | 0.96858 | 0.1666 | 286.5408 | 0 | 0 | 0 | 0 | 180 | 106.5408 | 178000 | 106.5408 | 316254.8946 | 339.5644 | 0
3419 | 5 | 0 | 1 | 0.25877 | 299.3837 | 0 | 0 | 0 | 0 | 180 | 119.3837 | 178000 | 119.3837 | 316374.2783 | 495.5884 | 0
3420 | 5 | 0 | 1 | 0.45163 | 307.2715 | 0 | 0 | 0 | 0 | 17.5607 | 200 | 178000 | 200 | 316574.2783 | 510.81 | 89.7108
3421 | 5 | 0 | 1 | 0.51501 | 309.8638 | 0 | 0 | 0 | 0 | 0 | 200 | 178000 | 200 | 316774.2783 | 510.81 | 109.8638
3422 | 5 | 0 | 1 | 0.46611 | 307.864 | 0 | 0 | 0 | 0 | 0 | 200 | 178000 | 200 | 316974.2783 | 510.81 | 107.864
3423 | 5 | 0 | 1 | 0.48183 | 308.507 | 0 | 0 | 0 | 0 | 0 | 200 | 178000 | 200 | 317174.2783 | 510.81 | 108.507
3424 | 5 | 0 | 0.96858 | 0.73747 | 309.8891 | 0 | 0 | 0 | 0 | 0 | 200 | 178000 | 200 | 317374.2783 | 510.81 | 109.8891
3425 | 5 | 0 | 0.68257 | 0.96632 | 236.6491 | 0 | 0 | 0 | 0 | 0 | 200 | 178000 | 200 | 317574.2783 | 510.81 | 36.6491
3426 | 5 | 0 | 0.38041 | 0.87355 | 145.5902 | 0 | 0 | 0 | 0 | 0 | 145.5902 | 178000 | 145.5902 | 317719.8685 | 510.81 | 0
3427 | 5 | 0 | 0.11135 | 0.52745 | 53.7308 | 0 | 0 | 0 | 0 | 0 | 53.7308 | 178000 | 53.7308 | 317773.5993 | 510.81 | 0
3428 | 5 | 1 | 0 | 0.62334 | 25.4944 | 200 | 25.4944 | 174.5056 | 200 | 0 | 0 | 177800 | 200 | 317973.5993 | 336.3044 | 0
3429 | 5 | 1 | 0 | 0.54075 | 22.1165 | 200 | 22.1165 | 177.8835 | 200 | 0 | 0 | 177600 | 200 | 318173.5993 | 158.4209 | 0
3430 | 5 | 0 | 0 | 0.49508 | 20.2487 | 0 | 0 | 0 | 0 | 20.2487 | 0 | 177600 | 0 | 318173.5993 | 175.9725 | 0
3431 | 5 | 0 | 0 | 0.47835 | 19.5646 | 0 | 0 | 0 | 0 | 19.5646 | 0 | 177600 | 0 | 318173.5993 | 192.9311 | 0
3432 | 5 | 0 | 0 | 0.41141 | 16.8268 | 0 | 0 | 0 | 0 | 16.8268 | 0 | 177600 | 0 | 318173.5993 | 207.5165 | 0
3433 | 5 | 0 | 0 | 0.46089 | 18.8502 | 0 | 0 | 0 | 0 | 18.8502 | 0 | 177600 | 0 | 318173.5993 | 223.8559 | 0
3434 | 5 | 0 | 0 | 0.27417 | 11.2134 | 0 | 0 | 0 | 0 | 11.2134 | 0 | 177600 | 0 | 318173.5993 | 233.5757 | 0
3435 | 5 | 0 | 0 | 0.27119 | 11.0915 | 0 | 0 | 0 | 0 | 11.0915 | 0 | 177600 | 0 | 318173.5993 | 243.1898 | 0
3436 | 5 | 0 | 0 | 0.34874 | 14.2633 | 0 | 0 | 0 | 0 | 14.2633 | 0 | 177600 | 0 | 318173.5993 | 255.5533 | 0
3437 | 5 | 0 | 0 | 0.53561 | 21.9064 | 0 | 0 | 0 | 0 | 21.9064 | 0 | 177600 | 0 | 318173.5993 | 274.5417 | 0
3438 | 5 | 0 | 0 | 0.41532 | 16.9867 | 0 | 0 | 0 | 0 | 16.9867 | 0 | 177600 | 0 | 318173.5993 | 289.2658 | 0
3439 | 5 | 0 | 0.11994 | 0.62582 | 60.2348 | 0 | 0 | 0 | 0 | 60.2348 | 0 | 177600 | 0 | 318173.5993 | 341.4772 | 0
3440 | 5 | 1 | 0.40975 | 0.69064 | 146.5831 | 200 | 146.5831 | 53.4169 | 200 | 0 | 0 | 177400 | 200 | 318373.5993 | 288.0604 | 0
3441 | 5 | 1 | 0.73522 | 0.61844 | 237.6257 | 200 | 200 | 0 | 200 | 37.6257 | 0 | 177200 | 200 | 318573.5993 | 320.6743 | 0
3442 | 5 | 0 | 1 | 0.63406 | 314.7329 | 0 | 0 | 0 | 0 | 180 | 134.7329 | 177200 | 134.7329 | 318708.3322 | 476.6983 | 0
3443 | 5 | 0 | 1 | 0.60484 | 313.5379 | 0 | 0 | 0 | 0 | 39.3536 | 200 | 177200 | 200 | 318908.3322 | 510.81 | 74.1843
3444 | 5 | 0 | 1 | 0.78025 | 320.7121 | 0 | 0 | 0 | 0 | 0 | 200 | 177200 | 200 | 319108.3322 | 510.81 | 120.7121
3445 | 5 | 0 | 1 | 0.90162 | 325.6761 | 0 | 0 | 0 | 0 | 0 | 200 | 177200 | 200 | 319308.3322 | 510.81 | 125.6761
3446 | 5 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 0 | 200 | 177200 | 200 | 319508.3322 | 510.81 | 129.7
3447 | 5 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 0 | 200 | 177200 | 200 | 319708.3322 | 510.81 | 129.7
3448 | 5 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 0 | 200 | 177200 | 200 | 319908.3322 | 510.81 | 129.7
3449 | 5 | 0 | 0.73522 | 0.77609 | 244.0737 | 0 | 0 | 0 | 0 | 0 | 200 | 177200 | 200 | 320108.3322 | 510.81 | 44.0737
3450 | 5 | 0 | 0.40975 | 0.67844 | 146.0844 | 0 | 0 | 0 | 0 | 0 | 146.0844 | 177200 | 146.0844 | 320254.4167 | 510.81 | 0
3451 | 5 | 0 | 0.11994 | 0.5157 | 55.731 | 0 | 0 | 0 | 0 | 0 | 55.731 | 177200 | 55.731 | 320310.1477 | 510.81 | 0
3452 | 5 | 1 | 0 | 0.58063 | 23.7479 | 200 | 23.7479 | 176.2521 | 200 | 0 | 0 | 177000 | 200 | 320510.1477 | 334.5579 | 0
3453 | 5 | 1 | 0 | 0.55437 | 22.6739 | 200 | 22.6739 | 177.3261 | 200 | 0 | 0 | 176800 | 200 | 320710.1477 | 157.2317 | 0
3454 | 5 | 0 | 0 | 0.71125 | 29.0903 | 0 | 0 | 0 | 0 | 29.0903 | 0 | 176800 | 0 | 320710.1477 | 182.4472 | 0
3455 | 5 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 176800 | 0 | 320710.1477 | 217.8993 | 0
3456 | 5 | 0 | 0 | 0.89705 | 36.6892 | 0 | 0 | 0 | 0 | 36.6892 | 0 | 176800 | 0 | 320710.1477 | 249.7015 | 0
3457 | 5 | 0 | 0 | 0.78898 | 32.2692 | 0 | 0 | 0 | 0 | 32.2692 | 0 | 176800 | 0 | 320710.1477 | 277.6725 | 0
3458 | 5 | 0 | 0 | 0.92783 | 37.9483 | 0 | 0 | 0 | 0 | 37.9483 | 0 | 176800 | 0 | 320710.1477 | 310.5661 | 0
3459 | 5 | 0 | 0 | 0.83756 | 34.2563 | 0 | 0 | 0 | 0 | 34.2563 | 0 | 176800 | 0 | 320710.1477 | 340.2595 | 0
3460 | 5 | 0 | 0 | 0.55968 | 22.891 | 0 | 0 | 0 | 0 | 22.891 | 0 | 176800 | 0 | 320710.1477 | 360.1014 | 0
3461 | 5 | 0 | 0 | 0.61456 | 25.1355 | 0 | 0 | 0 | 0 | 25.1355 | 0 | 176800 | 0 | 320710.1477 | 381.8888 | 0
3462 | 5 | 0 | 0 | 0.61846 | 25.2951 | 0 | 0 | 0 | 0 | 25.2951 | 0 | 176800 | 0 | 320710.1477 | 403.8146 | 0
3463 | 5 | 0 | 0.12224 | 0.66507 | 62.5032 | 0 | 0 | 0 | 0 | 62.5032 | 0 | 176800 | 0 | 320710.1477 | 457.9923 | 0
3464 | 5 | 1 | 0.4176 | 0.56714 | 143.7979 | 200 | 143.7979 | 56.2021 | 200 | 0 | 0 | 176600 | 200 | 320910.1477 | 401.7903 | 0
3465 | 5 | 1 | 0.7493 | 0.70151 | 245.0889 | 200 | 200 | 0 | 200 | 45.0889 | 0 | 176400 | 200 | 321110.1477 | 440.8733 | 0
3466 | 5 | 0 | 1 | 0.61354 | 313.8937 | 0 | 0 | 0 | 0 | 80.6838 | 200 | 176400 | 200 | 321310.1477 | 510.81 | 33.2099
3467 | 5 | 0 | 1 | 0.55493 | 311.4965 | 0 | 0 | 0 | 0 | 0 | 200 | 176400 | 200 | 321510.1477 | 510.81 | 111.4965
3468 | 5 | 0 | 1 | 0.4286 | 306.3299 | 0 | 0 | 0 | 0 | 0 | 200 | 176400 | 200 | 321710.1477 | 510.81 | 106.3299
3469 | 5 | 0 | 1 | 0.45855 | 307.5548 | 0 | 0 | 0 | 0 | 0 | 200 | 176400 | 200 | 321910.1477 | 510.81 | 107.5548
3470 | 5 | 0 | 1 | 0.63522 | 314.7803 | 0 | 0 | 0 | 0 | 0 | 200 | 176400 | 200 | 322110.1477 | 510.81 | 114.7803
3471 | 5 | 0 | 1 | 0.60062 | 313.3652 | 0 | 0 | 0 | 0 | 0 | 200 | 176400 | 200 | 322310.1477 | 510.81 | 113.3652
3472 | 5 | 0 | 1 | 0.61605 | 313.9964 | 0 | 0 | 0 | 0 | 0 | 200 | 176400 | 200 | 322510.1477 | 510.81 | 113.9964
3473 | 5 | 0 | 0.7493 | 1 | 257.297 | 0 | 0 | 0 | 0 | 0 | 200 | 176400 | 200 | 322710.1477 | 510.81 | 57.297
3474 | 5 | 0 | 0.4176 | 0.79243 | 153.0123 | 0 | 0 | 0 | 0 | 0 | 153.0123 | 176400 | 153.0123 | 322863.1599 | 510.81 | 0
3475 | 5 | 0 | 0.12224 | 0.66762 | 62.6073 | 0 | 0 | 0 | 0 | 0 | 62.6073 | 176400 | 62.6073 | 322925.7672 | 510.81 | 0
3476 | 5 | 1 | 0 | 0.66083 | 27.0279 | 200 | 27.0279 | 172.9721 | 200 | 0 | 0 | 176200 | 200 | 323125.7672 | 337.8379 | 0
3477 | 5 | 1 | 0 | 0.62447 | 25.541 | 200 | 25.541 | 174.459 | 200 | 0 | 0 | 176000 | 200 | 323325.7672 | 163.3789 | 0
3478 | 5 | 0 | 0 | 0.83921 | 34.3235 | 0 | 0 | 0 | 0 | 34.3235 | 0 | 176000 | 0 | 323325.7672 | 193.1305 | 0
3479 | 5 | 0 | 0 | 0.75048 | 30.6948 | 0 | 0 | 0 | 0 | 30.6948 | 0 | 176000 | 0 | 323325.7672 | 219.7367 | 0
3480 | 5 | 0 | 0 | 0.65933 | 26.9666 | 0 | 0 | 0 | 0 | 26.9666 | 0 | 176000 | 0 | 323325.7672 | 243.1113 | 0
3481 | 5 | 0 | 0 | 0.56107 | 22.9476 | 0 | 0 | 0 | 0 | 22.9476 | 0 | 176000 | 0 | 323325.7672 | 263.0023 | 0
3482 | 5 | 0 | 0 | 0.37611 | 15.3828 | 0 | 0 | 0 | 0 | 15.3828 | 0 | 176000 | 0 | 323325.7672 | 276.336 | 0
3483 | 5 | 0 | 0 | 0.3307 | 13.5258 | 0 | 0 | 0 | 0 | 13.5258 | 0 | 176000 | 0 | 323325.7672 | 288.0602 | 0
3484 | 5 | 0 | 0 | 0.35433 | 14.4919 | 0 | 0 | 0 | 0 | 14.4919 | 0 | 176000 | 0 | 323325.7672 | 300.6217 | 0
3485 | 5 | 0 | 0 | 0.34427 | 14.0805 | 0 | 0 | 0 | 0 | 14.0805 | 0 | 176000 | 0 | 323325.7672 | 312.8267 | 0
3486 | 5 | 0 | 0 | 0.32954 | 13.4784 | 0 | 0 | 0 | 0 | 13.4784 | 0 | 176000 | 0 | 323325.7672 | 324.5098 | 0
3487 | 5 | 0 | 0.10104 | 0.36754 | 44.2137 | 0 | 0 | 0 | 0 | 44.2137 | 0 | 176000 | 0 | 323325.7672 | 362.8342 | 0
3488 | 5 | 1 | 0.34519 | 0.33811 | 113.5212 | 200 | 113.5212 | 86.4788 | 200 | 0 | 0 | 175800 | 200 | 323525.7672 | 276.3554 | 0
3489 | 5 | 1 | 0.61939 | 0.27869 | 190.2777 | 200 | 190.2777 | 9.7223 | 200 | 0 | 0 | 175600 | 200 | 323725.7672 | 266.6331 | 0
3490 | 5 | 0 | 0.87892 | 0.23433 | 263.4172 | 0 | 0 | 0 | 0 | 180 | 83.4172 | 175600 | 83.4172 | 323809.1844 | 422.6571 | 0
3491 | 5 | 0 | 1 | 0.19726 | 296.8678 | 0 | 0 | 0 | 0 | 101.6992 | 195.1686 | 175600 | 195.1686 | 324004.353 | 510.81 | 0
3492 | 5 | 0 | 1 | 0.26188 | 299.5107 | 0 | 0 | 0 | 0 | 0 | 200 | 175600 | 200 | 324204.353 | 510.81 | 99.5107
3493 | 5 | 0 | 1 | 0.17484 | 295.9509 | 0 | 0 | 0 | 0 | 0 | 200 | 175600 | 200 | 324404.353 | 510.81 | 95.9509
3494 | 5 | 0 | 1 | 0.18218 | 296.2512 | 0 | 0 | 0 | 0 | 0 | 200 | 175600 | 200 | 324604.353 | 510.81 | 96.2512
3495 | 5 | 0 | 1 | 0.22205 | 297.8819 | 0 | 0 | 0 | 0 | 0 | 200 | 175600 | 200 | 324804.353 | 510.81 | 97.8819
3496 | 5 | 0 | 0.87892 | 0.27454 | 265.0618 | 0 | 0 | 0 | 0 | 0 | 200 | 175600 | 200 | 325004.353 | 510.81 | 65.0618
3497 | 5 | 0 | 0.61939 | 0.22057 | 187.9008 | 0 | 0 | 0 | 0 | 0 | 187.9008 | 175600 | 187.9008 | 325192.2537 | 510.81 | 0
3498 | 5 | 0 | 0.34519 | 0.33438 | 113.3685 | 0 | 0 | 0 | 0 | 0 | 113.3685 | 175600 | 113.3685 | 325305.6223 | 510.81 | 0
3499 | 5 | 0 | 0.10104 | 0.29927 | 41.4218 | 0 | 0 | 0 | 0 | 0 | 41.4218 | 175600 | 41.4218 | 325347.0441 | 510.81 | 0
3500 | 5 | 1 | 0 | 0.27677 | 11.3199 | 200 | 11.3199 | 180 | 191.3199 | 0 | 0 | 175400 | 191.3199 | 325538.364 | 330.81 | 0
3501 | 5 | 1 | 0 | 0.32175 | 13.1597 | 200 | 13.1597 | 180 | 193.1597 | 0 | 0 | 175200 | 193.1597 | 325731.5237 | 150.81 | 0
3502 | 5 | 0 | 0 | 0.23023 | 9.4166 | 0 | 0 | 0 | 0 | 9.4166 | 0 | 175200 | 0 | 325731.5237 | 158.9723 | 0
3503 | 5 | 0 | 0 | 0.29346 | 12.0026 | 0 | 0 | 0 | 0 | 12.0026 | 0 | 175200 | 0 | 325731.5237 | 169.3762 | 0
3504 | 5 | 0 | 0 | 0.2345 | 9.5908 | 0 | 0 | 0 | 0 | 9.5908 | 0 | 175200 | 0 | 325731.5237 | 177.6895 | 0
3505 | 5 | 0 | 0 | 0.21043 | 8.6067 | 0 | 0 | 0 | 0 | 8.6067 | 0 | 175200 | 0 | 325731.5237 | 185.1498 | 0
3506 | 5 | 0 | 0 | 0.14466 | 5.9167 | 0 | 0 | 0 | 0 | 5.9167 | 0 | 175200 | 0 | 325731.5237 | 190.2784 | 0
3507 | 5 | 0 | 0 | 0.088527 | 3.6208 | 0 | 0 | 0 | 0 | 3.6208 | 0 | 175200 | 0 | 325731.5237 | 193.4169 | 0
3508 | 5 | 0 | 0 | 0.13267 | 5.4263 | 0 | 0 | 0 | 0 | 5.4263 | 0 | 175200 | 0 | 325731.5237 | 198.1204 | 0
3509 | 5 | 0 | 0 | 0.1227 | 5.0183 | 0 | 0 | 0 | 0 | 5.0183 | 0 | 175200 | 0 | 325731.5237 | 202.4703 | 0
3510 | 5 | 0 | 0 | 0.10168 | 4.1586 | 0 | 0 | 0 | 0 | 4.1586 | 0 | 175200 | 0 | 325731.5237 | 206.0749 | 0
3511 | 5 | 0 | 0.10472 | 0.11408 | 34.9083 | 0 | 0 | 0 | 0 | 34.9083 | 0 | 175200 | 0 | 325731.5237 | 236.3334 | 0
3512 | 5 | 1 | 0.35775 | 0.14378 | 109.1976 | 200 | 109.1976 | 90.8024 | 200 | 0 | 0 | 175000 | 200 | 325931.5237 | 145.531 | 0
3513 | 5 | 1 | 0.64191 | 0.22223 | 194.4723 | 200 | 194.4723 | 5.5277 | 200 | 0 | 0 | 174800 | 200 | 326131.5237 | 140.0033 | 0
3514 | 5 | 0 | 0.91088 | 0.20925 | 271.6203 | 0 | 0 | 0 | 0 | 180 | 91.6203 | 174800 | 91.6203 | 326223.144 | 296.0273 | 0
3515 | 5 | 0 | 1 | 0.3189 | 301.8432 | 0 | 0 | 0 | 0 | 180 | 121.8432 | 174800 | 121.8432 | 326344.9873 | 452.0513 | 0
3516 | 5 | 0 | 1 | 0.3674 | 303.8268 | 0 | 0 | 0 | 0 | 67.7881 | 200 | 174800 | 200 | 326544.9873 | 510.81 | 36.0387
3517 | 5 | 0 | 1 | 0.36705 | 303.8122 | 0 | 0 | 0 | 0 | 0 | 200 | 174800 | 200 | 326744.9873 | 510.81 | 103.8122
3518 | 5 | 0 | 1 | 0.32355 | 302.033 | 0 | 0 | 0 | 0 | 0 | 200 | 174800 | 200 | 326944.9873 | 510.81 | 102.033
3519 | 5 | 0 | 1 | 0.22398 | 297.961 | 0 | 0 | 0 | 0 | 0 | 200 | 174800 | 200 | 327144.9873 | 510.81 | 97.961
3520 | 5 | 0 | 0.91088 | 0.32601 | 276.3958 | 0 | 0 | 0 | 0 | 0 | 200 | 174800 | 200 | 327344.9873 | 510.81 | 76.3958
3521 | 5 | 0 | 0.64191 | 0.431 | 203.0108 | 0 | 0 | 0 | 0 | 0 | 200 | 174800 | 200 | 327544.9873 | 510.81 | 3.0108
3522 | 5 | 0 | 0.35775 | 0.58509 | 127.2472 | 0 | 0 | 0 | 0 | 0 | 127.2472 | 174800 | 127.2472 | 327672.2344 | 510.81 | 0
3523 | 5 | 0 | 0.10472 | 0.65893 | 57.1926 | 0 | 0 | 0 | 0 | 0 | 57.1926 | 174800 | 57.1926 | 327729.4271 | 510.81 | 0
3524 | 5 | 1 | 0 | 0.64363 | 26.3243 | 200 | 26.3243 | 173.6757 | 200 | 0 | 0 | 174600 | 200 | 327929.4271 | 337.1343 | 0
3525 | 5 | 1 | 0 | 0.69846 | 28.5669 | 200 | 28.5669 | 171.4331 | 200 | 0 | 0 | 174400 | 200 | 328129.4271 | 165.7012 | 0
3526 | 5 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 174400 | 0 | 328129.4271 | 201.1533 | 0
3527 | 5 | 0 | 0 | 0.86043 | 35.1915 | 0 | 0 | 0 | 0 | 35.1915 | 0 | 174400 | 0 | 328129.4271 | 231.6573 | 0
3528 | 5 | 0 | 0 | 0.604 | 24.7036 | 0 | 0 | 0 | 0 | 24.7036 | 0 | 174400 | 0 | 328129.4271 | 253.0704 | 0
3529 | 5 | 0 | 0 | 0.52426 | 21.4424 | 0 | 0 | 0 | 0 | 21.4424 | 0 | 174400 | 0 | 328129.4271 | 271.6567 | 0
3530 | 5 | 0 | 0 | 0.59678 | 24.4081 | 0 | 0 | 0 | 0 | 24.4081 | 0 | 174400 | 0 | 328129.4271 | 292.8136 | 0
3531 | 5 | 0 | 0 | 0.65246 | 26.6857 | 0 | 0 | 0 | 0 | 26.6857 | 0 | 174400 | 0 | 328129.4271 | 315.9448 | 0
3532 | 5 | 0 | 0 | 0.53542 | 21.8986 | 0 | 0 | 0 | 0 | 21.8986 | 0 | 174400 | 0 | 328129.4271 | 334.9265 | 0
3533 | 5 | 0 | 0 | 0.47734 | 19.5231 | 0 | 0 | 0 | 0 | 19.5231 | 0 | 174400 | 0 | 328129.4271 | 351.8491 | 0
3534 | 5 | 0 | 0 | 0.51745 | 21.1637 | 0 | 0 | 0 | 0 | 21.1637 | 0 | 174400 | 0 | 328129.4271 | 370.1938 | 0
3535 | 5 | 0 | 0.10377 | 0.49167 | 50.0792 | 0 | 0 | 0 | 0 | 50.0792 | 0 | 174400 | 0 | 328129.4271 | 413.6025 | 0
3536 | 5 | 1 | 0.35452 | 0.60439 | 127.1062 | 200 | 127.1062 | 72.8938 | 200 | 0 | 0 | 174200 | 200 | 328329.4271 | 340.7087 | 0
3537 | 5 | 1 | 0.63613 | 0.53282 | 205.5062 | 200 | 200 | 0 | 200 | 5.5062 | 0 | 174000 | 200 | 328529.4271 | 345.4815 | 0
3538 | 5 | 0 | 0.90268 | 0.65507 | 287.4857 | 0 | 0 | 0 | 0 | 180 | 107.4857 | 174000 | 107.4857 | 328636.9128 | 501.5055 | 0
3539 | 5 | 0 | 1 | 0.56135 | 311.7592 | 0 | 0 | 0 | 0 | 10.7343 | 200 | 174000 | 200 | 328836.9128 | 510.81 | 101.0249
3540 | 5 | 0 | 1 | 0.65256 | 315.4899 | 0 | 0 | 0 | 0 | 0 | 200 | 174000 | 200 | 329036.9128 | 510.81 | 115.4899
3541 | 5 | 0 | 1 | 0.51658 | 309.9279 | 0 | 0 | 0 | 0 | 0 | 200 | 174000 | 200 | 329236.9128 | 510.81 | 109.9279
3542 | 5 | 0 | 1 | 0.58257 | 312.6273 | 0 | 0 | 0 | 0 | 0 | 200 | 174000 | 200 | 329436.9128 | 510.81 | 112.6273
3543 | 5 | 0 | 1 | 0.51576 | 309.8947 | 0 | 0 | 0 | 0 | 0 | 200 | 174000 | 200 | 329636.9128 | 510.81 | 109.8947
3544 | 5 | 0 | 0.90268 | 0.56458 | 283.7849 | 0 | 0 | 0 | 0 | 0 | 200 | 174000 | 200 | 329836.9128 | 510.81 | 83.7849
3545 | 5 | 0 | 0.63613 | 0.53813 | 205.7233 | 0 | 0 | 0 | 0 | 0 | 200 | 174000 | 200 | 330036.9128 | 510.81 | 5.7233
3546 | 5 | 0 | 0.35452 | 0.62194 | 127.8243 | 0 | 0 | 0 | 0 | 0 | 127.8243 | 174000 | 127.8243 | 330164.7371 | 510.81 | 0
3547 | 5 | 0 | 0.10377 | 0.59528 | 54.3171 | 0 | 0 | 0 | 0 | 0 | 54.3171 | 174000 | 54.3171 | 330219.0542 | 510.81 | 0
3548 | 5 | 1 | 0 | 0.71663 | 29.31 | 200 | 29.31 | 170.69 | 200 | 0 | 0 | 173800 | 200 | 330419.0542 | 340.12 | 0
3549 | 5 | 1 | 0 | 0.69546 | 28.4443 | 200 | 28.4443 | 171.5557 | 200 | 0 | 0 | 173600 | 200 | 330619.0542 | 168.5644 | 0
3550 | 5 | 0 | 0 | 0.95489 | 39.055 | 0 | 0 | 0 | 0 | 39.055 | 0 | 173600 | 0 | 330619.0542 | 202.4172 | 0
3551 | 5 | 0 | 0 | 0.91814 | 37.5517 | 0 | 0 | 0 | 0 | 37.5517 | 0 | 173600 | 0 | 330619.0542 | 234.9671 | 0
3552 | 5 | 0 | 0 | 0.70687 | 28.911 | 0 | 0 | 0 | 0 | 28.911 | 0 | 173600 | 0 | 330619.0542 | 260.0271 | 0
3553 | 5 | 0 | 0 | 0.55618 | 22.7479 | 0 | 0 | 0 | 0 | 22.7479 | 0 | 173600 | 0 | 330619.0542 | 279.745 | 0
3554 | 5 | 0 | 0 | 0.49858 | 20.3918 | 0 | 0 | 0 | 0 | 20.3918 | 0 | 173600 | 0 | 330619.0542 | 297.4207 | 0
3555 | 5 | 0 | 0 | 0.39842 | 16.2955 | 0 | 0 | 0 | 0 | 16.2955 | 0 | 173600 | 0 | 330619.0542 | 311.5456 | 0
3556 | 5 | 0 | 0 | 0.34596 | 14.1496 | 0 | 0 | 0 | 0 | 14.1496 | 0 | 173600 | 0 | 330619.0542 | 323.8104 | 0
3557 | 5 | 0 | 0 | 0.34003 | 13.9074 | 0 | 0 | 0 | 0 | 13.9074 | 0 | 173600 | 0 | 330619.0542 | 335.8654 | 0
3558 | 5 | 0 | 0 | 0.41416 | 16.9393 | 0 | 0 | 0 | 0 | 16.9393 | 0 | 173600 | 0 | 330619.0542 | 350.5483 | 0
3559 | 5 | 0 | 0.13381 | 0.33904 | 52.5118 | 0 | 0 | 0 | 0 | 52.5118 | 0 | 173600 | 0 | 330619.0542 | 396.0656 | 0
3560 | 5 | 1 | 0.45714 | 0.30957 | 144.6847 | 200 | 144.6847 | 55.3153 | 200 | 0 | 0 | 173400 | 200 | 330819.0542 | 340.7503 | 0
3561 | 5 | 1 | 0.82026 | 0.38319 | 252.5629 | 200 | 200 | 0 | 200 | 52.5629 | 0 | 173200 | 200 | 331019.0542 | 386.3118 | 0
3562 | 5 | 0 | 1 | 0.44126 | 306.8476 | 0 | 0 | 0 | 0 | 143.6297 | 163.2179 | 173200 | 163.2179 | 331182.2721 | 510.81 | 0
3563 | 5 | 0 | 1 | 0.36946 | 303.9111 | 0 | 0 | 0 | 0 | 0 | 200 | 173200 | 200 | 331382.2721 | 510.81 | 103.9111
3564 | 5 | 0 | 1 | 0.46077 | 307.6457 | 0 | 0 | 0 | 0 | 0 | 200 | 173200 | 200 | 331582.2721 | 510.81 | 107.6457
3565 | 5 | 0 | 1 | 0.35978 | 303.5151 | 0 | 0 | 0 | 0 | 0 | 200 | 173200 | 200 | 331782.2721 | 510.81 | 103.5151
3566 | 5 | 0 | 1 | 0.32655 | 302.1559 | 0 | 0 | 0 | 0 | 0 | 200 | 173200 | 200 | 331982.2721 | 510.81 | 102.1559
3567 | 5 | 0 | 1 | 0.35072 | 303.1444 | 0 | 0 | 0 | 0 | 0 | 200 | 173200 | 200 | 332182.2721 | 510.81 | 103.1444
3568 | 5 | 0 | 1 | 0.39652 | 305.0178 | 0 | 0 | 0 | 0 | 0 | 200 | 173200 | 200 | 332382.2721 | 510.81 | 105.0178
3569 | 5 | 0 | 0.82026 | 0.51031 | 257.7621 | 0 | 0 | 0 | 0 | 0 | 200 | 173200 | 200 | 332582.2721 | 510.81 | 57.7621
3570 | 5 | 0 | 0.45714 | 0.48816 | 151.9891 | 0 | 0 | 0 | 0 | 0 | 151.9891 | 173200 | 151.9891 | 332734.2611 | 510.81 | 0
3571 | 5 | 0 | 0.13381 | 0.52257 | 60.0181 | 0 | 0 | 0 | 0 | 0 | 60.0181 | 173200 | 60.0181 | 332794.2792 | 510.81 | 0
3572 | 5 | 1 | 0 | 0.47299 | 19.3454 | 200 | 19.3454 | 180 | 199.3454 | 0 | 0 | 173000 | 199.3454 | 332993.6246 | 330.81 | 0
3573 | 5 | 1 | 0 | 0.33976 | 13.8964 | 200 | 13.8964 | 180 | 193.8964 | 0 | 0 | 172800 | 193.8964 | 333187.521 | 150.81 | 0
3574 | 5 | 0 | 0 | 0.40156 | 16.4238 | 0 | 0 | 0 | 0 | 16.4238 | 0 | 172800 | 0 | 333187.521 | 165.0462 | 0
3575 | 5 | 0 | 0 | 0.34802 | 14.2338 | 0 | 0 | 0 | 0 | 14.2338 | 0 | 172800 | 0 | 333187.521 | 177.384 | 0
3576 | 5 | 0 | 0 | 0.33792 | 13.8208 | 0 | 0 | 0 | 0 | 13.8208 | 0 | 172800 | 0 | 333187.521 | 189.3639 | 0
3577 | 5 | 0 | 0 | 0.31953 | 13.0688 | 0 | 0 | 0 | 0 | 13.0688 | 0 | 172800 | 0 | 333187.521 | 200.6919 | 0
3578 | 5 | 0 | 0 | 0.28259 | 11.5579 | 0 | 0 | 0 | 0 | 11.5579 | 0 | 172800 | 0 | 333187.521 | 210.7104 | 0
3579 | 5 | 0 | 0 | 0.30563 | 12.5002 | 0 | 0 | 0 | 0 | 12.5002 | 0 | 172800 | 0 | 333187.521 | 221.5456 | 0
3580 | 5 | 0 | 0 | 0.39851 | 16.2992 | 0 | 0 | 0 | 0 | 16.2992 | 0 | 172800 | 0 | 333187.521 | 235.6737 | 0
3581 | 5 | 0 | 0 | 0.46753 | 19.122 | 0 | 0 | 0 | 0 | 19.122 | 0 | 172800 | 0 | 333187.521 | 252.2487 | 0
3582 | 5 | 0 | 0 | 0.50521 | 20.6632 | 0 | 0 | 0 | 0 | 20.6632 | 0 | 172800 | 0 | 333187.521 | 270.1595 | 0
3583 | 5 | 0 | 0.10608 | 0.60064 | 55.2029 | 0 | 0 | 0 | 0 | 55.2029 | 0 | 172800 | 0 | 333187.521 | 318.0094 | 0
3584 | 5 | 1 | 0.36241 | 0.51272 | 125.635 | 200 | 125.635 | 74.365 | 200 | 0 | 0 | 172600 | 200 | 333387.521 | 243.6444 | 0
3585 | 5 | 1 | 0.65028 | 0.40577 | 204.3971 | 200 | 200 | 0 | 200 | 4.3971 | 0 | 172400 | 200 | 333587.521 | 247.4559 | 0
3586 | 5 | 0 | 0.92276 | 0.33099 | 280.0311 | 0 | 0 | 0 | 0 | 180 | 100.0311 | 172400 | 100.0311 | 333687.5521 | 403.4799 | 0
3587 | 5 | 0 | 1 | 0.35082 | 303.1487 | 0 | 0 | 0 | 0 | 123.8234 | 179.3253 | 172400 | 179.3253 | 333866.8774 | 510.81 | 0
3588 | 5 | 0 | 1 | 0.23891 | 298.5716 | 0 | 0 | 0 | 0 | 0 | 200 | 172400 | 200 | 334066.8774 | 510.81 | 98.5716
3589 | 5 | 0 | 1 | 0.14461 | 294.7145 | 0 | 0 | 0 | 0 | 0 | 200 | 172400 | 200 | 334266.8774 | 510.81 | 94.7145
3590 | 5 | 0 | 1 | 0.10451 | 293.0746 | 0 | 0 | 0 | 0 | 0 | 200 | 172400 | 200 | 334466.8774 | 510.81 | 93.0746
3591 | 5 | 0 | 1 | 0.1243 | 293.8839 | 0 | 0 | 0 | 0 | 0 | 200 | 172400 | 200 | 334666.8774 | 510.81 | 93.8839
3592 | 5 | 0 | 0.92276 | 0.14149 | 272.2804 | 0 | 0 | 0 | 0 | 0 | 200 | 172400 | 200 | 334866.8774 | 510.81 | 72.2804
3593 | 5 | 0 | 0.65028 | 0.13483 | 193.3155 | 0 | 0 | 0 | 0 | 0 | 193.3155 | 172400 | 193.3155 | 335060.1929 | 510.81 | 0
3594 | 5 | 0 | 0.36241 | 0.14058 | 110.4144 | 0 | 0 | 0 | 0 | 0 | 110.4144 | 172400 | 110.4144 | 335170.6073 | 510.81 | 0
3595 | 5 | 0 | 0.10608 | 0.13748 | 36.2598 | 0 | 0 | 0 | 0 | 0 | 36.2598 | 172400 | 36.2598 | 335206.8672 | 510.81 | 0
3596 | 5 | 1 | 0 | 0.16284 | 6.66 | 200 | 6.66 | 180 | 186.66 | 0 | 0 | 172200 | 186.66 | 335393.5272 | 330.81 | 0
3597 | 5 | 1 | 0 | 0.19599 | 8.0158 | 200 | 8.0158 | 180 | 188.0158 | 0 | 0 | 172000 | 188.0158 | 335581.543 | 150.81 | 0
3598 | 5 | 0 | 0 | 0.24229 | 9.9097 | 0 | 0 | 0 | 0 | 9.9097 | 0 | 172000 | 0 | 335581.543 | 159.3997 | 0
3599 | 5 | 0 | 0 | 0.29389 | 12.0199 | 0 | 0 | 0 | 0 | 12.0199 | 0 | 172000 | 0 | 335581.543 | 169.8186 | 0
3600 | 5 | 0 | 0 | 0.1811 | 7.4069 | 0 | 0 | 0 | 0 | 7.4069 | 0 | 172000 | 0 | 335581.543 | 176.2389 | 0
3601 | 5 | 0 | 0 | 0.1769 | 7.2354 | 0 | 0 | 0 | 0 | 7.2354 | 0 | 172000 | 0 | 335581.543 | 182.5105 | 0
3602 | 5 | 0 | 0 | 0.1082 | 4.4254 | 0 | 0 | 0 | 0 | 4.4254 | 0 | 172000 | 0 | 335581.543 | 186.3465 | 0
3603 | 5 | 0 | 0 | 0.071817 | 2.9373 | 0 | 0 | 0 | 0 | 2.9373 | 0 | 172000 | 0 | 335581.543 | 188.8925 | 0
3604 | 5 | 0 | 0 | 0.11004 | 4.5005 | 0 | 0 | 0 | 0 | 4.5005 | 0 | 172000 | 0 | 335581.543 | 192.7936 | 0
3605 | 5 | 0 | 0 | 0.20808 | 8.5104 | 0 | 0 | 0 | 0 | 8.5104 | 0 | 172000 | 0 | 335581.543 | 200.1704 | 0
3606 | 5 | 0 | 0 | 0.20384 | 8.3371 | 0 | 0 | 0 | 0 | 8.3371 | 0 | 172000 | 0 | 335581.543 | 207.397 | 0
3607 | 5 | 0 | 0.12057 | 0.24365 | 44.785 | 0 | 0 | 0 | 0 | 44.785 | 0 | 172000 | 0 | 335581.543 | 246.2167 | 0
3608 | 5 | 1 | 0.41189 | 0.25038 | 129.1949 | 200 | 129.1949 | 70.8051 | 200 | 0 | 0 | 171800 | 200 | 335781.543 | 175.4115 | 0
3609 | 5 | 1 | 0.73906 | 0.33971 | 227.3354 | 200 | 200 | 0 | 200 | 27.3354 | 0 | 171600 | 200 | 335981.543 | 199.1059 | 0
3610 | 5 | 0 | 1 | 0.41242 | 305.668 | 0 | 0 | 0 | 0 | 180 | 125.668 | 171600 | 125.668 | 336107.211 | 355.1299 | 0
3611 | 5 | 0 | 1 | 0.4376 | 306.6979 | 0 | 0 | 0 | 0 | 179.6033 | 127.0946 | 171600 | 127.0946 | 336234.3057 | 510.81 | 0
3612 | 5 | 0 | 1 | 0.62072 | 314.1874 | 0 | 0 | 0 | 0 | 0 | 200 | 171600 | 200 | 336434.3057 | 510.81 | 114.1874
3613 | 5 | 0 | 1 | 0.68577 | 316.8481 | 0 | 0 | 0 | 0 | 0 | 200 | 171600 | 200 | 336634.3057 | 510.81 | 116.8481
3614 | 5 | 0 | 1 | 0.78254 | 320.806 | 0 | 0 | 0 | 0 | 0 | 200 | 171600 | 200 | 336834.3057 | 510.81 | 120.806
3615 | 5 | 0 | 1 | 0.85694 | 323.8489 | 0 | 0 | 0 | 0 | 0 | 200 | 171600 | 200 | 337034.3057 | 510.81 | 123.8489
3616 | 5 | 0 | 1 | 0.95239 | 327.7528 | 0 | 0 | 0 | 0 | 0 | 200 | 171600 | 200 | 337234.3057 | 510.81 | 127.7528
3617 | 5 | 0 | 0.73906 | 1 | 254.3411 | 0 | 0 | 0 | 0 | 0 | 200 | 171600 | 200 | 337434.3057 | 510.81 | 54.3411
3618 | 5 | 0 | 0.41189 | 1 | 159.8544 | 0 | 0 | 0 | 0 | 0 | 159.8544 | 171600 | 159.8544 | 337594.1601 | 510.81 | 0
3619 | 5 | 0 | 0.12057 | 0.7032 | 63.5808 | 0 | 0 | 0 | 0 | 0 | 63.5808 | 171600 | 63.5808 | 337657.7409 | 510.81 | 0
3620 | 5 | 1 | 0 | 0.56519 | 23.1164 | 200 | 23.1164 | 176.8836 | 200 | 0 | 0 | 171400 | 200 | 337857.7409 | 333.9264 | 0
3621 | 5 | 1 | 0 | 0.59471 | 24.3236 | 200 | 24.3236 | 175.6764 | 200 | 0 | 0 | 171200 | 200 | 338057.7409 | 158.25 | 0
3622 | 5 | 0 | 0 | 0.32948 | 13.4756 | 0 | 0 | 0 | 0 | 13.4756 | 0 | 171200 | 0 | 338057.7409 | 169.9306 | 0
3623 | 5 | 0 | 0 | 0.37748 | 15.4389 | 0 | 0 | 0 | 0 | 15.4389 | 0 | 171200 | 0 | 338057.7409 | 183.313 | 0
3624 | 5 | 0 | 0 | 0.33267 | 13.6063 | 0 | 0 | 0 | 0 | 13.6063 | 0 | 171200 | 0 | 338057.7409 | 195.107 | 0
3625 | 6 | 0 | 0 | 0.38342 | 15.6817 | 0 | 0 | 0 | 0 | 15.6817 | 0 | 171200 | 0 | 338057.7409 | 208.6999 | 0
3626 | 6 | 0 | 0 | 0.41487 | 16.9682 | 0 | 0 | 0 | 0 | 16.9682 | 0 | 171200 | 0 | 338057.7409 | 223.4079 | 0
3627 | 6 | 0 | 0 | 0.32257 | 13.193 | 0 | 0 | 0 | 0 | 13.193 | 0 | 171200 | 0 | 338057.7409 | 234.8436 | 0
3628 | 6 | 0 | 0 | 0.21475 | 8.7832 | 0 | 0 | 0 | 0 | 8.7832 | 0 | 171200 | 0 | 338057.7409 | 242.4569 | 0
3629 | 6 | 0 | 0 | 0.29741 | 12.1642 | 0 | 0 | 0 | 0 | 12.1642 | 0 | 171200 | 0 | 338057.7409 | 253.0008 | 0
3630 | 6 | 0 | 0 | 0.35654 | 14.5826 | 0 | 0 | 0 | 0 | 14.5826 | 0 | 171200 | 0 | 338057.7409 | 265.641 | 0
3631 | 6 | 0 | 0.10467 | 0.24042 | 40.0615 | 0 | 0 | 0 | 0 | 40.0615 | 0 | 171200 | 0 | 338057.7409 | 300.3663 | 0
3632 | 6 | 1 | 0.30312 | 0.29641 | 99.6632 | 200 | 99.6632 | 100.3368 | 200 | 0 | 0 | 171000 | 200 | 338257.7409 | 200.0296 | 0
3633 | 6 | 1 | 0.52021 | 0.27585 | 161.52 | 200 | 161.52 | 38.48 | 200 | 0 | 0 | 170800 | 200 | 338457.7409 | 161.5496 | 0
3634 | 6 | 0 | 0.72338 | 0.37179 | 224.1175 | 0 | 0 | 0 | 0 | 180 | 44.1175 | 170800 | 44.1175 | 338501.8584 | 317.5736 | 0
3635 | 6 | 0 | 0.88752 | 0.41973 | 273.4821 | 0 | 0 | 0 | 0 | 180 | 93.4821 | 170800 | 93.4821 | 338595.3404 | 473.5976 | 0
3636 | 6 | 0 | 0.99386 | 0.43933 | 304.9957 | 0 | 0 | 0 | 0 | 42.9308 | 200 | 170800 | 200 | 338795.3404 | 510.81 | 62.0648
3637 | 6 | 0 | 1 | 0.40179 | 305.233 | 0 | 0 | 0 | 0 | 0 | 200 | 170800 | 200 | 338995.3404 | 510.81 | 105.233
3638 | 6 | 0 | 0.99386 | 0.32169 | 300.1841 | 0 | 0 | 0 | 0 | 0 | 200 | 170800 | 200 | 339195.3404 | 510.81 | 100.1841
3639 | 6 | 0 | 0.88752 | 0.49687 | 276.6373 | 0 | 0 | 0 | 0 | 0 | 200 | 170800 | 200 | 339395.3404 | 510.81 | 76.6373
3640 | 6 | 0 | 0.72338 | 0.90097 | 245.7609 | 0 | 0 | 0 | 0 | 0 | 200 | 170800 | 200 | 339595.3404 | 510.81 | 45.7609
3641 | 6 | 0 | 0.52021 | 0.74119 | 180.5525 | 0 | 0 | 0 | 0 | 0 | 180.5525 | 170800 | 180.5525 | 339775.8929 | 510.81 | 0
3642 | 6 | 0 | 0.30312 | 0.90897 | 124.7168 | 0 | 0 | 0 | 0 | 0 | 124.7168 | 170800 | 124.7168 | 339900.6097 | 510.81 | 0
3643 | 6 | 0 | 0.10467 | 0.54222 | 52.4049 | 0 | 0 | 0 | 0 | 0 | 52.4049 | 170800 | 52.4049 | 339953.0147 | 510.81 | 0
3644 | 6 | 1 | 0 | 0.91323 | 37.351 | 200 | 37.351 | 162.649 | 200 | 0 | 0 | 170600 | 200 | 340153.0147 | 348.161 | 0
3645 | 6 | 1 | 0 | 0.84203 | 34.4391 | 200 | 34.4391 | 165.5609 | 200 | 0 | 0 | 170400 | 200 | 340353.0147 | 182.6001 | 0
3646 | 6 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 170400 | 0 | 340353.0147 | 218.0523 | 0
3647 | 6 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 170400 | 0 | 340353.0147 | 253.5044 | 0
3648 | 6 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 170400 | 0 | 340353.0147 | 288.9565 | 0
3649 | 6 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 170400 | 0 | 340353.0147 | 324.4086 | 0
3650 | 6 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 170400 | 0 | 340353.0147 | 359.8607 | 0
3651 | 6 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 170400 | 0 | 340353.0147 | 395.3129 | 0
3652 | 6 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 170400 | 0 | 340353.0147 | 430.765 | 0
3653 | 6 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 170400 | 0 | 340353.0147 | 466.2171 | 0
3654 | 6 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 170400 | 0 | 340353.0147 | 501.6692 | 0
3655 | 6 | 0 | 0.11292 | 1 | 73.511 | 0 | 0 | 0 | 0 | 10.5454 | 62.9656 | 170400 | 62.9656 | 340415.9802 | 510.81 | 0
3656 | 6 | 1 | 0.32701 | 1 | 135.3405 | 200 | 135.3405 | 64.6595 | 200 | 0 | 0 | 170200 | 200 | 340615.9802 | 446.1505 | 0
3657 | 6 | 1 | 0.56122 | 1 | 202.9806 | 200 | 200 | 0 | 200 | 2.9806 | 0 | 170000 | 200 | 340815.9802 | 448.7341 | 0
3658 | 6 | 0 | 0.7804 | 1 | 266.2787 | 0 | 0 | 0 | 0 | 71.615 | 194.6636 | 170000 | 194.6636 | 341010.6438 | 510.81 | 0
3659 | 6 | 0 | 0.95748 | 1 | 317.4196 | 0 | 0 | 0 | 0 | 0 | 200 | 170000 | 200 | 341210.6438 | 510.81 | 117.4196
3660 | 6 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 0 | 200 | 170000 | 200 | 341410.6438 | 510.81 | 129.7
3661 | 6 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 0 | 200 | 170000 | 200 | 341610.6438 | 510.81 | 129.7
3662 | 6 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 0 | 200 | 170000 | 200 | 341810.6438 | 510.81 | 129.7
3663 | 6 | 0 | 0.95748 | 1 | 317.4196 | 0 | 0 | 0 | 0 | 0 | 200 | 170000 | 200 | 342010.6438 | 510.81 | 117.4196
3664 | 6 | 0 | 0.7804 | 1 | 266.2787 | 0 | 0 | 0 | 0 | 0 | 200 | 170000 | 200 | 342210.6438 | 510.81 | 66.2787
3665 | 6 | 0 | 0.56122 | 1 | 202.9806 | 0 | 0 | 0 | 0 | 0 | 200 | 170000 | 200 | 342410.6438 | 510.81 | 2.9806
3666 | 6 | 0 | 0.32701 | 1 | 135.3405 | 0 | 0 | 0 | 0 | 0 | 135.3405 | 170000 | 135.3405 | 342545.9843 | 510.81 | 0
3667 | 6 | 0 | 0.11292 | 0.73119 | 62.5166 | 0 | 0 | 0 | 0 | 0 | 62.5166 | 170000 | 62.5166 | 342608.5009 | 510.81 | 0
3668 | 6 | 1 | 0 | 0.80737 | 33.0216 | 200 | 33.0216 | 166.9784 | 200 | 0 | 0 | 169800 | 200 | 342808.5009 | 343.8316 | 0
3669 | 6 | 1 | 0 | 0.90384 | 36.9672 | 200 | 36.9672 | 163.0328 | 200 | 0 | 0 | 169600 | 200 | 343008.5009 | 180.7988 | 0
3670 | 6 | 0 | 0 | 0.73015 | 29.863 | 0 | 0 | 0 | 0 | 29.863 | 0 | 169600 | 0 | 343008.5009 | 206.684 | 0
3671 | 6 | 0 | 0 | 0.56902 | 23.273 | 0 | 0 | 0 | 0 | 23.273 | 0 | 169600 | 0 | 343008.5009 | 226.857 | 0
3672 | 6 | 0 | 0 | 0.41581 | 17.0068 | 0 | 0 | 0 | 0 | 17.0068 | 0 | 169600 | 0 | 343008.5009 | 241.5985 | 0
3673 | 6 | 0 | 0 | 0.27289 | 11.1612 | 0 | 0 | 0 | 0 | 11.1612 | 0 | 169600 | 0 | 343008.5009 | 251.273 | 0
3674 | 6 | 0 | 0 | 0.24319 | 9.9465 | 0 | 0 | 0 | 0 | 9.9465 | 0 | 169600 | 0 | 343008.5009 | 259.8946 | 0
3675 | 6 | 0 | 0 | 0.3258 | 13.3251 | 0 | 0 | 0 | 0 | 13.3251 | 0 | 169600 | 0 | 343008.5009 | 271.4448 | 0
3676 | 6 | 0 | 0 | 0.40886 | 16.7224 | 0 | 0 | 0 | 0 | 16.7224 | 0 | 169600 | 0 | 343008.5009 | 285.9397 | 0
3677 | 6 | 0 | 0 | 0.48372 | 19.7843 | 0 | 0 | 0 | 0 | 19.7843 | 0 | 169600 | 0 | 343008.5009 | 303.0888 | 0
3678 | 6 | 0 | 0 | 0.61996 | 25.3564 | 0 | 0 | 0 | 0 | 25.3564 | 0 | 169600 | 0 | 343008.5009 | 325.0677 | 0
3679 | 6 | 0 | 0.11227 | 0.47615 | 51.8979 | 0 | 0 | 0 | 0 | 51.8979 | 0 | 169600 | 0 | 343008.5009 | 370.0528 | 0
3680 | 6 | 1 | 0.32513 | 0.44859 | 112.2444 | 200 | 112.2444 | 87.7556 | 200 | 0 | 0 | 169400 | 200 | 343208.5009 | 282.2973 | 0
3681 | 6 | 1 | 0.55799 | 0.47598 | 180.6159 | 200 | 180.6159 | 19.3841 | 200 | 0 | 0 | 169200 | 200 | 343408.5009 | 262.9131 | 0
3682 | 6 | 0 | 0.77591 | 0.3822 | 239.7139 | 0 | 0 | 0 | 0 | 180 | 59.7139 | 169200 | 59.7139 | 343468.2149 | 418.9371 | 0
3683 | 6 | 0 | 0.95197 | 0.52292 | 296.3162 | 0 | 0 | 0 | 0 | 105.9908 | 190.3254 | 169200 | 190.3254 | 343658.5402 | 510.81 | 0
3684 | 6 | 0 | 1 | 0.57449 | 312.2968 | 0 | 0 | 0 | 0 | 0 | 200 | 169200 | 200 | 343858.5402 | 510.81 | 112.2968
3685 | 6 | 0 | 1 | 0.42675 | 306.2542 | 0 | 0 | 0 | 0 | 0 | 200 | 169200 | 200 | 344058.5402 | 510.81 | 106.2542
3686 | 6 | 0 | 1 | 0.37948 | 304.3207 | 0 | 0 | 0 | 0 | 0 | 200 | 169200 | 200 | 344258.5402 | 510.81 | 104.3207
3687 | 6 | 0 | 0.95197 | 0.28277 | 286.4939 | 0 | 0 | 0 | 0 | 0 | 200 | 169200 | 200 | 344458.5402 | 510.81 | 86.4939
3688 | 6 | 0 | 0.77591 | 0.29831 | 236.2827 | 0 | 0 | 0 | 0 | 0 | 200 | 169200 | 200 | 344658.5402 | 510.81 | 36.2827
3689 | 6 | 0 | 0.55799 | 0.20968 | 169.7242 | 0 | 0 | 0 | 0 | 0 | 169.7242 | 169200 | 169.7242 | 344828.2644 | 510.81 | 0
3690 | 6 | 0 | 0.32513 | 0.19817 | 102.0021 | 0 | 0 | 0 | 0 | 0 | 102.0021 | 169200 | 102.0021 | 344930.2665 | 510.81 | 0
3691 | 6 | 0 | 0.11227 | 0.28247 | 43.9761 | 0 | 0 | 0 | 0 | 0 | 43.9761 | 169200 | 43.9761 | 344974.2426 | 510.81 | 0
3692 | 6 | 1 | 0 | 0.24451 | 10.0005 | 200 | 10.0005 | 180 | 190.0005 | 0 | 0 | 169000 | 190.0005 | 345164.2431 | 330.81 | 0
3693 | 6 | 1 | 0 | 0.18393 | 7.5227 | 200 | 7.5227 | 180 | 187.5227 | 0 | 0 | 168800 | 187.5227 | 345351.7659 | 150.81 | 0
3694 | 6 | 0 | 0 | 0.24047 | 9.8353 | 0 | 0 | 0 | 0 | 9.8353 | 0 | 168800 | 0 | 345351.7659 | 159.3353 | 0
3695 | 6 | 0 | 0 | 0.2255 | 9.2231 | 0 | 0 | 0 | 0 | 9.2231 | 0 | 168800 | 0 | 345351.7659 | 167.3298 | 0
3696 | 6 | 0 | 0 | 0.18508 | 7.5699 | 0 | 0 | 0 | 0 | 7.5699 | 0 | 168800 | 0 | 345351.7659 | 173.8915 | 0
3697 | 6 | 0 | 0 | 0.2782 | 11.3784 | 0 | 0 | 0 | 0 | 11.3784 | 0 | 168800 | 0 | 345351.7659 | 183.7543 | 0
3698 | 6 | 0 | 0 | 0.30117 | 12.3179 | 0 | 0 | 0 | 0 | 12.3179 | 0 | 168800 | 0 | 345351.7659 | 194.4314 | 0
3699 | 6 | 0 | 0 | 0.40134 | 16.4146 | 0 | 0 | 0 | 0 | 16.4146 | 0 | 168800 | 0 | 345351.7659 | 208.6596 | 0
3700 | 6 | 0 | 0 | 0.61226 | 25.0415 | 0 | 0 | 0 | 0 | 25.0415 | 0 | 168800 | 0 | 345351.7659 | 230.3656 | 0
3701 | 6 | 0 | 0 | 0.51895 | 21.225 | 0 | 0 | 0 | 0 | 21.225 | 0 | 168800 | 0 | 345351.7659 | 248.7634 | 0
3702 | 6 | 0 | 0 | 0.5709 | 23.3497 | 0 | 0 | 0 | 0 | 23.3497 | 0 | 168800 | 0 | 345351.7659 | 269.003 | 0
3703 | 6 | 0 | 0.10608 | 0.74072 | 60.9311 | 0 | 0 | 0 | 0 | 60.9311 | 0 | 168800 | 0 | 345351.7659 | 321.8181 | 0
3704 | 6 | 1 | 0.3072 | 0.5498 | 111.2075 | 200 | 111.2075 | 88.7925 | 200 | 0 | 0 | 168600 | 200 | 345551.7659 | 233.0256 | 0
3705 | 6 | 1 | 0.52723 | 0.6876 | 180.3868 | 200 | 180.3868 | 19.6132 | 200 | 0 | 0 | 168400 | 200 | 345751.7659 | 213.4125 | 0
3706 | 6 | 0 | 0.73313 | 0.86389 | 247.0616 | 0 | 0 | 0 | 0 | 180 | 67.0616 | 168400 | 67.0616 | 345818.8275 | 369.4365 | 0
3707 | 6 | 0 | 0.89949 | 0.7006 | 288.4266 | 0 | 0 | 0 | 0 | 163.0982 | 125.3284 | 168400 | 125.3284 | 345944.1559 | 510.81 | 0
3708 | 6 | 0 | 1 | 0.72592 | 318.49 | 0 | 0 | 0 | 0 | 0 | 200 | 168400 | 200 | 346144.1559 | 510.81 | 118.49
3709 | 6 | 0 | 1 | 0.55584 | 311.5337 | 0 | 0 | 0 | 0 | 0 | 200 | 168400 | 200 | 346344.1559 | 510.81 | 111.5337
3710 | 6 | 0 | 1 | 0.43613 | 306.6378 | 0 | 0 | 0 | 0 | 0 | 200 | 168400 | 200 | 346544.1559 | 510.81 | 106.6378
3711 | 6 | 0 | 0.89949 | 0.48339 | 279.5427 | 0 | 0 | 0 | 0 | 0 | 200 | 168400 | 200 | 346744.1559 | 510.81 | 79.5427
3712 | 6 | 0 | 0.73313 | 0.36521 | 226.6654 | 0 | 0 | 0 | 0 | 0 | 200 | 168400 | 200 | 346944.1559 | 510.81 | 26.6654
3713 | 6 | 0 | 0.52723 | 0.70462 | 181.083 | 0 | 0 | 0 | 0 | 0 | 181.083 | 168400 | 181.083 | 347125.2388 | 510.81 | 0
3714 | 6 | 0 | 0.3072 | 0.39659 | 104.941 | 0 | 0 | 0 | 0 | 0 | 104.941 | 168400 | 104.941 | 347230.1798 | 510.81 | 0
3715 | 6 | 0 | 0.10608 | 0.50216 | 51.1744 | 0 | 0 | 0 | 0 | 0 | 51.1744 | 168400 | 51.1744 | 347281.3542 | 510.81 | 0
3716 | 6 | 1 | 0 | 0.57378 | 23.4674 | 200 | 23.4674 | 176.5326 | 200 | 0 | 0 | 168200 | 200 | 347481.3542 | 334.2774 | 0
3717 | 6 | 1 | 0 | 0.67675 | 27.6792 | 200 | 27.6792 | 172.3208 | 200 | 0 | 0 | 168000 | 200 | 347681.3542 | 161.9566 | 0
3718 | 6 | 0 | 0 | 0.63845 | 26.1127 | 0 | 0 | 0 | 0 | 26.1127 | 0 | 168000 | 0 | 347681.3542 | 184.5911 | 0
3719 | 6 | 0 | 0 | 0.65589 | 26.8259 | 0 | 0 | 0 | 0 | 26.8259 | 0 | 168000 | 0 | 347681.3542 | 207.8439 | 0
3720 | 6 | 0 | 0 | 0.62007 | 25.3608 | 0 | 0 | 0 | 0 | 25.3608 | 0 | 168000 | 0 | 347681.3542 | 229.8266 | 0
3721 | 6 | 0 | 0 | 0.44628 | 18.253 | 0 | 0 | 0 | 0 | 18.253 | 0 | 168000 | 0 | 347681.3542 | 245.6483 | 0
3722 | 6 | 0 | 0 | 0.20314 | 8.3085 | 0 | 0 | 0 | 0 | 8.3085 | 0 | 168000 | 0 | 347681.3542 | 252.8502 | 0
3723 | 6 | 0 | 0 | 0.14234 | 5.8218 | 0 | 0 | 0 | 0 | 5.8218 | 0 | 168000 | 0 | 347681.3542 | 257.8965 | 0
3724 | 6 | 0 | 0 | 0.18627 | 7.6184 | 0 | 0 | 0 | 0 | 7.6184 | 0 | 168000 | 0 | 347681.3542 | 264.5002 | 0
3725 | 6 | 0 | 0 | 0.16993 | 6.95 | 0 | 0 | 0 | 0 | 6.95 | 0 | 168000 | 0 | 347681.3542 | 270.5244 | 0
3726 | 6 | 0 | 0 | 0.17977 | 7.3526 | 0 | 0 | 0 | 0 | 7.3526 | 0 | 168000 | 0 | 347681.3542 | 276.8976 | 0
3727 | 6 | 0 | 0.10377 | 0.19143 | 37.7979 | 0 | 0 | 0 | 0 | 37.7979 | 0 | 168000 | 0 | 347681.3542 | 309.6609 | 0
3728 | 6 | 1 | 0.30051 | 0.21769 | 95.6916 | 200 | 95.6916 | 104.3084 | 200 | 0 | 0 | 167800 | 200 | 347881.3542 | 205.3524 | 0
3729 | 6 | 1 | 0.51575 | 0.2491 | 159.1354 | 200 | 159.1354 | 40.8646 | 200 | 0 | 0 | 167600 | 200 | 348081.3542 | 164.4878 | 0
3730 | 6 | 0 | 0.71716 | 0.24002 | 216.9331 | 0 | 0 | 0 | 0 | 180 | 36.9331 | 167600 | 36.9331 | 348118.2873 | 320.5118 | 0
3731 | 6 | 0 | 0.87989 | 0.26517 | 264.9586 | 0 | 0 | 0 | 0 | 180 | 84.9586 | 167600 | 84.9586 | 348203.2459 | 476.5358 | 0
3732 | 6 | 0 | 0.98532 | 0.29443 | 296.6031 | 0 | 0 | 0 | 0 | 39.541 | 200 | 167600 | 200 | 348403.2459 | 510.81 | 57.0621
3733 | 6 | 0 | 1 | 0.35929 | 303.4952 | 0 | 0 | 0 | 0 | 0 | 200 | 167600 | 200 | 348603.2459 | 510.81 | 103.4952
3734 | 6 | 0 | 0.98532 | 0.51612 | 305.6702 | 0 | 0 | 0 | 0 | 0 | 200 | 167600 | 200 | 348803.2459 | 510.81 | 105.6702
3735 | 6 | 0 | 0.87989 | 0.51568 | 275.2045 | 0 | 0 | 0 | 0 | 0 | 200 | 167600 | 200 | 349003.2459 | 510.81 | 75.2045
3736 | 6 | 0 | 0.71716 | 0.54706 | 229.4912 | 0 | 0 | 0 | 0 | 0 | 200 | 167600 | 200 | 349203.2459 | 510.81 | 29.4912
3737 | 6 | 0 | 0.51575 | 0.99989 | 189.8425 | 0 | 0 | 0 | 0 | 0 | 189.8425 | 167600 | 189.8425 | 349393.0883 | 510.81 | 0
3738 | 6 | 0 | 0.30051 | 1 | 127.6879 | 0 | 0 | 0 | 0 | 0 | 127.6879 | 167600 | 127.6879 | 349520.7762 | 510.81 | 0
3739 | 6 | 0 | 0.10377 | 0.83211 | 64.0018 | 0 | 0 | 0 | 0 | 0 | 64.0018 | 167600 | 64.0018 | 349584.778 | 510.81 | 0
3740 | 6 | 1 | 0 | 0.89042 | 36.4182 | 200 | 36.4182 | 163.5818 | 200 | 0 | 0 | 167400 | 200 | 349784.778 | 347.2282 | 0
3741 | 6 | 1 | 0 | 0.90009 | 36.8136 | 200 | 36.8136 | 163.1864 | 200 | 0 | 0 | 167200 | 200 | 349984.778 | 184.0419 | 0
3742 | 6 | 0 | 0 | 0.73408 | 30.0239 | 0 | 0 | 0 | 0 | 30.0239 | 0 | 167200 | 0 | 349984.778 | 210.0666 | 0
3743 | 6 | 0 | 0 | 0.65551 | 26.8104 | 0 | 0 | 0 | 0 | 26.8104 | 0 | 167200 | 0 | 349984.778 | 233.3058 | 0
3744 | 6 | 0 | 0 | 0.55324 | 22.6274 | 0 | 0 | 0 | 0 | 22.6274 | 0 | 167200 | 0 | 349984.778 | 252.9192 | 0
3745 | 6 | 0 | 0 | 0.52963 | 21.6618 | 0 | 0 | 0 | 0 | 21.6618 | 0 | 167200 | 0 | 349984.778 | 271.6957 | 0
3746 | 6 | 0 | 0 | 0.61836 | 25.2908 | 0 | 0 | 0 | 0 | 25.2908 | 0 | 167200 | 0 | 349984.778 | 293.6177 | 0
3747 | 6 | 0 | 0 | 0.33191 | 13.5752 | 0 | 0 | 0 | 0 | 13.5752 | 0 | 167200 | 0 | 349984.778 | 305.3847 | 0
3748 | 6 | 0 | 0 | 0.33498 | 13.7006 | 0 | 0 | 0 | 0 | 13.7006 | 0 | 167200 | 0 | 349984.778 | 317.2604 | 0
3749 | 6 | 0 | 0 | 0.33253 | 13.6006 | 0 | 0 | 0 | 0 | 13.6006 | 0 | 167200 | 0 | 349984.778 | 329.0494 | 0
3750 | 6 | 0 | 0 | 0.36652 | 14.9908 | 0 | 0 | 0 | 0 | 14.9908 | 0 | 167200 | 0 | 349984.778 | 342.0434 | 0
3751 | 6 | 0 | 0.099674 | 0.37205 | 44.0026 | 0 | 0 | 0 | 0 | 44.0026 | 0 | 167200 | 0 | 349984.778 | 380.1849 | 0
3752 | 6 | 1 | 0.28865 | 0.4568 | 102.0467 | 200 | 102.0467 | 97.9533 | 200 | 0 | 0 | 167000 | 200 | 350184.778 | 282.2316 | 0
3753 | 6 | 1 | 0.49539 | 0.35606 | 157.6331 | 200 | 157.6331 | 42.3669 | 200 | 0 | 0 | 166800 | 200 | 350384.778 | 239.8647 | 0
3754 | 6 | 0 | 0.68886 | 0.42715 | 216.4144 | 0 | 0 | 0 | 0 | 180 | 36.4144 | 166800 | 36.4144 | 350421.1925 | 395.8887 | 0
3755 | 6 | 0 | 0.84518 | 0.31423 | 256.9384 | 0 | 0 | 0 | 0 | 132.5812 | 124.3572 | 166800 | 124.3572 | 350545.5497 | 510.81 | 0
3756 | 6 | 0 | 0.94644 | 0.38906 | 289.2453 | 0 | 0 | 0 | 0 | 0 | 200 | 166800 | 200 | 350745.5497 | 510.81 | 89.2453
3757 | 6 | 0 | 0.98147 | 0.44627 | 301.7018 | 0 | 0 | 0 | 0 | 0 | 200 | 166800 | 200 | 350945.5497 | 510.81 | 101.7018
3758 | 6 | 0 | 0.94644 | 0.67883 | 301.097 | 0 | 0 | 0 | 0 | 0 | 200 | 166800 | 200 | 351145.5497 | 510.81 | 101.097
3759 | 6 | 0 | 0.84518 | 1 | 284.9865 | 0 | 0 | 0 | 0 | 0 | 200 | 166800 | 200 | 351345.5497 | 510.81 | 84.9865
3760 | 6 | 0 | 0.68886 | 1 | 239.8439 | 0 | 0 | 0 | 0 | 0 | 200 | 166800 | 200 | 351545.5497 | 510.81 | 39.8439
3761 | 6 | 0 | 0.49539 | 1 | 183.9701 | 0 | 0 | 0 | 0 | 0 | 183.9701 | 166800 | 183.9701 | 351729.5198 | 510.81 | 0
3762 | 6 | 0 | 0.28865 | 1 | 124.2636 | 0 | 0 | 0 | 0 | 0 | 124.2636 | 166800 | 124.2636 | 351853.7834 | 510.81 | 0
3763 | 6 | 0 | 0.099674 | 1 | 69.6859 | 0 | 0 | 0 | 0 | 0 | 69.6859 | 166800 | 69.6859 | 351923.4692 | 510.81 | 0
3764 | 6 | 1 | 0 | 1 | 40.9 | 200 | 40.9 | 159.1 | 200 | 0 | 0 | 166600 | 200 | 352123.4692 | 351.71 | 0
3765 | 6 | 1 | 0 | 0.9763 | 39.9307 | 200 | 39.9307 | 160.0693 | 200 | 0 | 0 | 166400 | 200 | 352323.4692 | 191.6407 | 0
3766 | 6 | 0 | 0 | 0.90339 | 36.9485 | 0 | 0 | 0 | 0 | 36.9485 | 0 | 166400 | 0 | 352323.4692 | 223.6677 | 0
3767 | 6 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 166400 | 0 | 352323.4692 | 259.1198 | 0
3768 | 6 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 166400 | 0 | 352323.4692 | 294.5719 | 0
3769 | 6 | 0 | 0 | 0.79853 | 32.6599 | 0 | 0 | 0 | 0 | 32.6599 | 0 | 166400 | 0 | 352323.4692 | 322.8815 | 0
3770 | 6 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 166400 | 0 | 352323.4692 | 358.3336 | 0
3771 | 6 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 166400 | 0 | 352323.4692 | 393.7857 | 0
3772 | 6 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 166400 | 0 | 352323.4692 | 429.2378 | 0
3773 | 6 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 166400 | 0 | 352323.4692 | 464.69 | 0
3774 | 6 | 0 | 0 | 0.71157 | 29.1032 | 0 | 0 | 0 | 0 | 29.1032 | 0 | 166400 | 0 | 352323.4692 | 489.9166 | 0
3775 | 6 | 0 | 0.12012 | 1 | 75.5904 | 0 | 0 | 0 | 0 | 24.104 | 51.4863 | 166400 | 51.4863 | 352374.9555 | 510.81 | 0
3776 | 6 | 1 | 0.34786 | 1 | 141.3623 | 200 | 141.3623 | 58.6377 | 200 | 0 | 0 | 166200 | 200 | 352574.9555 | 452.1723 | 0
3777 | 6 | 1 | 0.59701 | 1 | 213.315 | 200 | 200 | 0 | 200 | 13.315 | 0 | 166000 | 200 | 352774.9555 | 463.7137 | 0
3778 | 6 | 0 | 0.83016 | 1 | 280.6493 | 0 | 0 | 0 | 0 | 54.3335 | 200 | 166000 | 200 | 352974.9555 | 510.81 | 26.3159
3779 | 6 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 0 | 200 | 166000 | 200 | 353174.9555 | 510.81 | 129.7
3780 | 6 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 0 | 200 | 166000 | 200 | 353374.9555 | 510.81 | 129.7
3781 | 6 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 0 | 200 | 166000 | 200 | 353574.9555 | 510.81 | 129.7
3782 | 6 | 0 | 1 | 0.60494 | 313.5418 | 0 | 0 | 0 | 0 | 0 | 200 | 166000 | 200 | 353774.9555 | 510.81 | 113.5418
3783 | 6 | 0 | 1 | 0.68234 | 316.7077 | 0 | 0 | 0 | 0 | 0 | 200 | 166000 | 200 | 353974.9555 | 510.81 | 116.7077
3784 | 6 | 0 | 0.83016 | 0.58834 | 263.8126 | 0 | 0 | 0 | 0 | 0 | 200 | 166000 | 200 | 354174.9555 | 510.81 | 63.8126
3785 | 6 | 0 | 0.59701 | 0.42687 | 189.8739 | 0 | 0 | 0 | 0 | 0 | 189.8739 | 166000 | 189.8739 | 354364.8295 | 510.81 | 0
3786 | 6 | 0 | 0.34786 | 0.45607 | 119.1156 | 0 | 0 | 0 | 0 | 0 | 119.1156 | 166000 | 119.1156 | 354483.9451 | 510.81 | 0
3787 | 6 | 0 | 0.12012 | 0.46058 | 53.5279 | 0 | 0 | 0 | 0 | 0 | 53.5279 | 166000 | 53.5279 | 354537.473 | 510.81 | 0
3788 | 6 | 1 | 0 | 0.42267 | 17.2871 | 200 | 17.2871 | 180 | 197.2871 | 0 | 0 | 165800 | 197.2871 | 354734.7602 | 330.81 | 0
3789 | 6 | 1 | 0 | 0.30769 | 12.5847 | 200 | 12.5847 | 180 | 192.5847 | 0 | 0 | 165600 | 192.5847 | 354927.3449 | 150.81 | 0
3790 | 6 | 0 | 0 | 0.25094 | 10.2635 | 0 | 0 | 0 | 0 | 10.2635 | 0 | 165600 | 0 | 354927.3449 | 159.7064 | 0
3791 | 6 | 0 | 0 | 0.37596 | 15.3767 | 0 | 0 | 0 | 0 | 15.3767 | 0 | 165600 | 0 | 354927.3449 | 173.0349 | 0
3792 | 6 | 0 | 0 | 0.38817 | 15.8762 | 0 | 0 | 0 | 0 | 15.8762 | 0 | 165600 | 0 | 354927.3449 | 186.7964 | 0
3793 | 6 | 0 | 0 | 0.36461 | 14.9127 | 0 | 0 | 0 | 0 | 14.9127 | 0 | 165600 | 0 | 354927.3449 | 199.7228 | 0
3794 | 6 | 0 | 0 | 0.25811 | 10.5567 | 0 | 0 | 0 | 0 | 10.5567 | 0 | 165600 | 0 | 354927.3449 | 208.8733 | 0
3795 | 6 | 0 | 0 | 0.3446 | 14.0943 | 0 | 0 | 0 | 0 | 14.0943 | 0 | 165600 | 0 | 354927.3449 | 221.0902 | 0
3796 | 6 | 0 | 0 | 0.38275 | 15.6545 | 0 | 0 | 0 | 0 | 15.6545 | 0 | 165600 | 0 | 354927.3449 | 234.6595 | 0
3797 | 6 | 0 | 0 | 0.44349 | 18.1387 | 0 | 0 | 0 | 0 | 18.1387 | 0 | 165600 | 0 | 354927.3449 | 250.3822 | 0
3798 | 6 | 0 | 0 | 0.64915 | 26.5504 | 0 | 0 | 0 | 0 | 26.5504 | 0 | 165600 | 0 | 354927.3449 | 273.396 | 0
3799 | 6 | 0 | 0.10946 | 0.47835 | 51.1756 | 0 | 0 | 0 | 0 | 51.1756 | 0 | 165600 | 0 | 354927.3449 | 317.755 | 0
3800 | 6 | 1 | 0.31699 | 0.53211 | 113.3085 | 200 | 113.3085 | 86.6915 | 200 | 0 | 0 | 165400 | 200 | 355127.3449 | 231.0635 | 0
3801 | 6 | 1 | 0.54402 | 0.4771 | 176.6252 | 200 | 176.6252 | 23.3748 | 200 | 0 | 0 | 165200 | 200 | 355327.3449 | 207.6887 | 0
3802 | 6 | 0 | 0.75647 | 0.48108 | 238.1457 | 0 | 0 | 0 | 0 | 180 | 58.1457 | 165200 | 58.1457 | 355385.4906 | 363.7127 | 0
3803 | 6 | 0 | 0.92813 | 0.71532 | 297.2992 | 0 | 0 | 0 | 0 | 169.7015 | 127.5977 | 165200 | 127.5977 | 355513.0883 | 510.81 | 0
3804 | 6 | 0 | 1 | 0.63545 | 314.7898 | 0 | 0 | 0 | 0 | 0 | 200 | 165200 | 200 | 355713.0883 | 510.81 | 114.7898
3805 | 6 | 0 | 1 | 0.64672 | 315.2508 | 0 | 0 | 0 | 0 | 0 | 200 | 165200 | 200 | 355913.0883 | 510.81 | 115.2508
3806 | 6 | 0 | 1 | 0.82719 | 322.6321 | 0 | 0 | 0 | 0 | 0 | 200 | 165200 | 200 | 356113.0883 | 510.81 | 122.6321
3807 | 6 | 0 | 0.92813 | 0.7873 | 300.2432 | 0 | 0 | 0 | 0 | 0 | 200 | 165200 | 200 | 356313.0883 | 510.81 | 100.2432
3808 | 6 | 0 | 0.75647 | 0.56504 | 241.5798 | 0 | 0 | 0 | 0 | 0 | 200 | 165200 | 200 | 356513.0883 | 510.81 | 41.5798
3809 | 6 | 0 | 0.54402 | 0.53903 | 179.1582 | 0 | 0 | 0 | 0 | 0 | 179.1582 | 165200 | 179.1582 | 356692.2465 | 510.81 | 0
3810 | 6 | 0 | 0.31699 | 0.43177 | 109.2045 | 0 | 0 | 0 | 0 | 0 | 109.2045 | 165200 | 109.2045 | 356801.451 | 510.81 | 0
3811 | 6 | 0 | 0.10946 | 0.35483 | 46.1236 | 0 | 0 | 0 | 0 | 0 | 46.1236 | 165200 | 46.1236 | 356847.5746 | 510.81 | 0
3812 | 6 | 1 | 0 | 0.42356 | 17.3236 | 200 | 17.3236 | 180 | 197.3236 | 0 | 0 | 165000 | 197.3236 | 357044.8982 | 330.81 | 0
3813 | 6 | 1 | 0 | 0.5356 | 21.9061 | 200 | 21.9061 | 178.0939 | 200 | 0 | 0 | 164800 | 200 | 357244.8982 | 152.7161 | 0
3814 | 6 | 0 | 0 | 0.45829 | 18.7441 | 0 | 0 | 0 | 0 | 18.7441 | 0 | 164800 | 0 | 357244.8982 | 168.9635 | 0
3815 | 6 | 0 | 0 | 0.3103 | 12.6914 | 0 | 0 | 0 | 0 | 12.6914 | 0 | 164800 | 0 | 357244.8982 | 179.9644 | 0
3816 | 6 | 0 | 0 | 0.19664 | 8.0428 | 0 | 0 | 0 | 0 | 8.0428 | 0 | 164800 | 0 | 357244.8982 | 186.9359 | 0
3817 | 6 | 0 | 0 | 0.3459 | 14.1474 | 0 | 0 | 0 | 0 | 14.1474 | 0 | 164800 | 0 | 357244.8982 | 199.1989 | 0
3818 | 6 | 0 | 0 | 0.37984 | 15.5356 | 0 | 0 | 0 | 0 | 15.5356 | 0 | 164800 | 0 | 357244.8982 | 212.6651 | 0
3819 | 6 | 0 | 0 | 0.40174 | 16.4311 | 0 | 0 | 0 | 0 | 16.4311 | 0 | 164800 | 0 | 357244.8982 | 226.9076 | 0
3820 | 6 | 0 | 0 | 0.32843 | 13.4329 | 0 | 0 | 0 | 0 | 13.4329 | 0 | 164800 | 0 | 357244.8982 | 238.5512 | 0
3821 | 6 | 0 | 0 | 0.39536 | 16.1701 | 0 | 0 | 0 | 0 | 16.1701 | 0 | 164800 | 0 | 357244.8982 | 252.5675 | 0
3822 | 6 | 0 | 0 | 0.46037 | 18.8292 | 0 | 0 | 0 | 0 | 18.8292 | 0 | 164800 | 0 | 357244.8982 | 268.8886 | 0
3823 | 6 | 0 | 0.13184 | 0.30374 | 50.4995 | 0 | 0 | 0 | 0 | 50.4995 | 0 | 164800 | 0 | 357244.8982 | 312.6615 | 0
3824 | 6 | 1 | 0.38182 | 0.29916 | 122.5041 | 200 | 122.5041 | 77.4959 | 200 | 0 | 0 | 164600 | 200 | 357444.8982 | 235.1656 | 0
3825 | 6 | 1 | 0.65528 | 0.35642 | 203.8225 | 200 | 200 | 0 | 200 | 3.8225 | 0 | 164400 | 200 | 357644.8982 | 238.479 | 0
3826 | 6 | 0 | 0.91119 | 0.47371 | 282.5266 | 0 | 0 | 0 | 0 | 180 | 102.5266 | 164400 | 102.5266 | 357747.4247 | 394.503 | 0
3827 | 6 | 0 | 1 | 0.43701 | 306.6739 | 0 | 0 | 0 | 0 | 134.1798 | 172.4941 | 164400 | 172.4941 | 357919.9189 | 510.81 | 0
3828 | 6 | 0 | 1 | 0.43619 | 306.6404 | 0 | 0 | 0 | 0 | 0 | 200 | 164400 | 200 | 358119.9189 | 510.81 | 106.6404
3829 | 6 | 0 | 1 | 0.45091 | 307.2423 | 0 | 0 | 0 | 0 | 0 | 200 | 164400 | 200 | 358319.9189 | 510.81 | 107.2423
3830 | 6 | 0 | 1 | 0.45785 | 307.5261 | 0 | 0 | 0 | 0 | 0 | 200 | 164400 | 200 | 358519.9189 | 510.81 | 107.5261
3831 | 6 | 0 | 1 | 0.45674 | 307.4807 | 0 | 0 | 0 | 0 | 0 | 200 | 164400 | 200 | 358719.9189 | 510.81 | 107.4807
3832 | 6 | 0 | 0.91119 | 0.33757 | 276.9584 | 0 | 0 | 0 | 0 | 0 | 200 | 164400 | 200 | 358919.9189 | 510.81 | 76.9584
3833 | 6 | 0 | 0.65528 | 0.22095 | 198.2816 | 0 | 0 | 0 | 0 | 0 | 198.2816 | 164400 | 198.2816 | 359118.2005 | 510.81 | 0
3834 | 6 | 0 | 0.38182 | 0.40617 | 126.8809 | 0 | 0 | 0 | 0 | 0 | 126.8809 | 164400 | 126.8809 | 359245.0814 | 510.81 | 0
3835 | 6 | 0 | 0.13184 | 0.30158 | 50.411 | 0 | 0 | 0 | 0 | 0 | 50.411 | 164400 | 50.411 | 359295.4924 | 510.81 | 0
3836 | 6 | 1 | 0 | 0.29443 | 12.0423 | 200 | 12.0423 | 180 | 192.0423 | 0 | 0 | 164200 | 192.0423 | 359487.5347 | 330.81 | 0
3837 | 6 | 1 | 0 | 0.20859 | 8.5312 | 200 | 8.5312 | 180 | 188.5312 | 0 | 0 | 164000 | 188.5312 | 359676.0659 | 150.81 | 0
3838 | 6 | 0 | 0 | 0.28707 | 11.7411 | 0 | 0 | 0 | 0 | 11.7411 | 0 | 164000 | 0 | 359676.0659 | 160.9872 | 0
3839 | 6 | 0 | 0 | 0.25604 | 10.472 | 0 | 0 | 0 | 0 | 10.472 | 0 | 164000 | 0 | 359676.0659 | 170.0643 | 0
3840 | 6 | 0 | 0 | 0.28009 | 11.4555 | 0 | 0 | 0 | 0 | 11.4555 | 0 | 164000 | 0 | 359676.0659 | 179.9939 | 0
3841 | 6 | 0 | 0 | 0.36848 | 15.0708 | 0 | 0 | 0 | 0 | 15.0708 | 0 | 164000 | 0 | 359676.0659 | 193.0573 | 0
3842 | 6 | 0 | 0 | 0.3696 | 15.1165 | 0 | 0 | 0 | 0 | 15.1165 | 0 | 164000 | 0 | 359676.0659 | 206.1603 | 0
3843 | 6 | 0 | 0 | 0.29973 | 12.2588 | 0 | 0 | 0 | 0 | 12.2588 | 0 | 164000 | 0 | 359676.0659 | 216.7862 | 0
3844 | 6 | 0 | 0 | 0.32432 | 13.2647 | 0 | 0 | 0 | 0 | 13.2647 | 0 | 164000 | 0 | 359676.0659 | 228.284 | 0
3845 | 6 | 0 | 0 | 0.36333 | 14.8603 | 0 | 0 | 0 | 0 | 14.8603 | 0 | 164000 | 0 | 359676.0659 | 241.165 | 0
3846 | 6 | 0 | 0 | 0.35675 | 14.5912 | 0 | 0 | 0 | 0 | 14.5912 | 0 | 164000 | 0 | 359676.0659 | 253.8126 | 0
3847 | 6 | 0 | 0.12671 | 0.39166 | 52.6122 | 0 | 0 | 0 | 0 | 52.6122 | 0 | 164000 | 0 | 359676.0659 | 299.4168 | 0
3848 | 6 | 1 | 0.36694 | 0.52779 | 127.56 | 200 | 127.56 | 72.44 | 200 | 0 | 0 | 163800 | 200 | 359876.0659 | 226.9768 | 0
3849 | 6 | 1 | 0.62976 | 0.74524 | 212.3541 | 200 | 200 | 0 | 200 | 12.3541 | 0 | 163600 | 200 | 360076.0659 | 237.6854 | 0
3850 | 6 | 0 | 0.8757 | 0.88638 | 289.1549 | 0 | 0 | 0 | 0 | 180 | 109.1549 | 163600 | 109.1549 | 360185.2208 | 393.7094 | 0
3851 | 6 | 0 | 1 | 0.88546 | 325.0155 | 0 | 0 | 0 | 0 | 135.0953 | 189.9202 | 163600 | 189.9202 | 360375.141 | 510.81 | 0
3852 | 6 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 0 | 200 | 163600 | 200 | 360575.141 | 510.81 | 129.7
3853 | 6 | 0 | 1 | 0.84366 | 323.3056 | 0 | 0 | 0 | 0 | 0 | 200 | 163600 | 200 | 360775.141 | 510.81 | 123.3056
3854 | 6 | 0 | 1 | 0.60847 | 313.6863 | 0 | 0 | 0 | 0 | 0 | 200 | 163600 | 200 | 360975.141 | 510.81 | 113.6863
3855 | 6 | 0 | 1 | 0.81803 | 322.2575 | 0 | 0 | 0 | 0 | 0 | 200 | 163600 | 200 | 361175.141 | 510.81 | 122.2575
3856 | 6 | 0 | 0.8757 | 0.79261 | 285.3195 | 0 | 0 | 0 | 0 | 0 | 200 | 163600 | 200 | 361375.141 | 510.81 | 85.3195
3857 | 6 | 0 | 0.62976 | 0.87087 | 217.4923 | 0 | 0 | 0 | 0 | 0 | 200 | 163600 | 200 | 361575.141 | 510.81 | 17.4923
3858 | 6 | 0 | 0.36694 | 1 | 146.8734 | 0 | 0 | 0 | 0 | 0 | 146.8734 | 163600 | 146.8734 | 361722.0144 | 510.81 | 0
3859 | 6 | 0 | 0.12671 | 1 | 77.4933 | 0 | 0 | 0 | 0 | 0 | 77.4933 | 163600 | 77.4933 | 361799.5077 | 510.81 | 0
3860 | 6 | 1 | 0 | 1 | 40.9 | 200 | 40.9 | 159.1 | 200 | 0 | 0 | 163400 | 200 | 361999.5077 | 351.71 | 0
3861 | 6 | 1 | 0 | 1 | 40.9 | 200 | 40.9 | 159.1 | 200 | 0 | 0 | 163200 | 200 | 362199.5077 | 192.61 | 0
3862 | 6 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 163200 | 0 | 362199.5077 | 228.0621 | 0
3863 | 6 | 0 | 0 | 0.73648 | 30.1222 | 0 | 0 | 0 | 0 | 30.1222 | 0 | 163200 | 0 | 362199.5077 | 254.1721 | 0
3864 | 6 | 0 | 0 | 0.77907 | 31.8641 | 0 | 0 | 0 | 0 | 31.8641 | 0 | 163200 | 0 | 362199.5077 | 281.7919 | 0
3865 | 6 | 0 | 0 | 0.65565 | 26.816 | 0 | 0 | 0 | 0 | 26.816 | 0 | 163200 | 0 | 362199.5077 | 305.036 | 0
3866 | 6 | 0 | 0 | 0.52267 | 21.3772 | 0 | 0 | 0 | 0 | 21.3772 | 0 | 163200 | 0 | 362199.5077 | 323.5658 | 0
3867 | 6 | 0 | 0 | 0.41282 | 16.8842 | 0 | 0 | 0 | 0 | 16.8842 | 0 | 163200 | 0 | 362199.5077 | 338.201 | 0
3868 | 6 | 0 | 0 | 0.541 | 22.1268 | 0 | 0 | 0 | 0 | 22.1268 | 0 | 163200 | 0 | 362199.5077 | 357.3805 | 0
3869 | 6 | 0 | 0 | 0.641 | 26.2169 | 0 | 0 | 0 | 0 | 26.2169 | 0 | 163200 | 0 | 362199.5077 | 380.1053 | 0
3870 | 6 | 0 | 0 | 0.55524 | 22.7093 | 0 | 0 | 0 | 0 | 22.7093 | 0 | 163200 | 0 | 362199.5077 | 399.7897 | 0
3871 | 6 | 0 | 0.11554 | 0.49761 | 53.7204 | 0 | 0 | 0 | 0 | 53.7204 | 0 | 163200 | 0 | 362199.5077 | 446.3546 | 0
3872 | 6 | 1 | 0.3346 | 0.38585 | 112.4136 | 200 | 112.4136 | 87.5864 | 200 | 0 | 0 | 163000 | 200 | 362399.5077 | 358.7682 | 0
3873 | 6 | 1 | 0.57425 | 0.41253 | 182.7148 | 200 | 182.7148 | 17.2852 | 200 | 0 | 0 | 162800 | 200 | 362599.5077 | 341.483 | 0
3874 | 6 | 0 | 0.79851 | 0.50827 | 251.3978 | 0 | 0 | 0 | 0 | 180 | 71.3978 | 162800 | 71.3978 | 362670.9055 | 497.507 | 0
3875 | 6 | 0 | 0.9797 | 0.38577 | 298.7156 | 0 | 0 | 0 | 0 | 15.3473 | 200 | 162800 | 200 | 362870.9055 | 510.81 | 83.3684
3876 | 6 | 0 | 1 | 0.33698 | 302.5824 | 0 | 0 | 0 | 0 | 0 | 200 | 162800 | 200 | 363070.9055 | 510.81 | 102.5824
3877 | 6 | 0 | 1 | 0.33102 | 302.3387 | 0 | 0 | 0 | 0 | 0 | 200 | 162800 | 200 | 363270.9055 | 510.81 | 102.3387
3878 | 6 | 0 | 1 | 0.44762 | 307.1076 | 0 | 0 | 0 | 0 | 0 | 200 | 162800 | 200 | 363470.9055 | 510.81 | 107.1076
3879 | 6 | 0 | 0.9797 | 0.47999 | 302.5692 | 0 | 0 | 0 | 0 | 0 | 200 | 162800 | 200 | 363670.9055 | 510.81 | 102.5692
3880 | 6 | 0 | 0.79851 | 0.49288 | 250.7686 | 0 | 0 | 0 | 0 | 0 | 200 | 162800 | 200 | 363870.9055 | 510.81 | 50.7686
3881 | 6 | 0 | 0.57425 | 0.34728 | 180.0461 | 0 | 0 | 0 | 0 | 0 | 180.0461 | 162800 | 180.0461 | 364050.9515 | 510.81 | 0
3882 | 6 | 0 | 0.3346 | 0.22318 | 105.7605 | 0 | 0 | 0 | 0 | 0 | 105.7605 | 162800 | 105.7605 | 364156.712 | 510.81 | 0
3883 | 6 | 0 | 0.11554 | 0.22955 | 42.7566 | 0 | 0 | 0 | 0 | 0 | 42.7566 | 162800 | 42.7566 | 364199.4686 | 510.81 | 0
3884 | 6 | 1 | 0 | 0.30553 | 12.4961 | 200 | 12.4961 | 180 | 192.4961 | 0 | 0 | 162600 | 192.4961 | 364391.9647 | 330.81 | 0
3885 | 6 | 1 | 0 | 0.35575 | 14.55 | 200 | 14.55 | 180 | 194.55 | 0 | 0 | 162400 | 194.55 | 364586.5147 | 150.81 | 0
3886 | 6 | 0 | 0 | 0.51167 | 20.9272 | 0 | 0 | 0 | 0 | 20.9272 | 0 | 162400 | 0 | 364586.5147 | 168.9497 | 0
3887 | 6 | 0 | 0 | 0.50594 | 20.6928 | 0 | 0 | 0 | 0 | 20.6928 | 0 | 162400 | 0 | 364586.5147 | 186.8863 | 0
3888 | 6 | 0 | 0 | 0.46888 | 19.1772 | 0 | 0 | 0 | 0 | 19.1772 | 0 | 162400 | 0 | 364586.5147 | 203.509 | 0
3889 | 6 | 0 | 0 | 0.30628 | 12.5271 | 0 | 0 | 0 | 0 | 12.5271 | 0 | 162400 | 0 | 364586.5147 | 214.3675 | 0
3890 | 6 | 0 | 0 | 0.3499 | 14.311 | 0 | 0 | 0 | 0 | 14.311 | 0 | 162400 | 0 | 364586.5147 | 226.7722 | 0
3891 | 6 | 0 | 0 | 0.42128 | 17.2305 | 0 | 0 | 0 | 0 | 17.2305 | 0 | 162400 | 0 | 364586.5147 | 241.7076 | 0
3892 | 6 | 0 | 0 | 0.37801 | 15.4607 | 0 | 0 | 0 | 0 | 15.4607 | 0 | 162400 | 0 | 364586.5147 | 255.1089 | 0
3893 | 6 | 0 | 0 | 0.33626 | 13.7532 | 0 | 0 | 0 | 0 | 13.7532 | 0 | 162400 | 0 | 364586.5147 | 267.0302 | 0
3894 | 6 | 0 | 0 | 0.23846 | 9.7531 | 0 | 0 | 0 | 0 | 9.7531 | 0 | 162400 | 0 | 364586.5147 | 275.4842 | 0
3895 | 6 | 0 | 0.10077 | 0.15777 | 35.5554 | 0 | 0 | 0 | 0 | 35.5554 | 0 | 162400 | 0 | 364586.5147 | 306.3036 | 0
3896 | 6 | 1 | 0.29183 | 0.15514 | 90.6249 | 200 | 90.6249 | 109.3751 | 200 | 0 | 0 | 162200 | 200 | 364786.5147 | 196.9285 | 0
3897 | 6 | 1 | 0.50084 | 0.21572 | 153.4654 | 200 | 153.4654 | 46.5346 | 200 | 0 | 0 | 162000 | 200 | 364986.5147 | 150.3939 | 0
3898 | 6 | 0 | 0.69644 | 0.35776 | 215.7626 | 0 | 0 | 0 | 0 | 180 | 35.7626 | 162000 | 35.7626 | 365022.2774 | 306.4179 | 0
3899 | 6 | 0 | 0.85446 | 0.52933 | 268.4186 | 0 | 0 | 0 | 0 | 180 | 88.4186 | 162000 | 88.4186 | 365110.696 | 462.4419 | 0
3900 | 6 | 0 | 0.95684 | 0.52846 | 297.9509 | 0 | 0 | 0 | 0 | 55.8008 | 200 | 162000 | 200 | 365310.696 | 510.81 | 42.1501
3901 | 6 | 0 | 0.99226 | 0.55192 | 309.1382 | 0 | 0 | 0 | 0 | 0 | 200 | 162000 | 200 | 365510.696 | 510.81 | 109.1382
3902 | 6 | 0 | 0.95684 | 0.6194 | 301.6703 | 0 | 0 | 0 | 0 | 0 | 200 | 162000 | 200 | 365710.696 | 510.81 | 101.6703
3903 | 6 | 0 | 0.85446 | 0.70471 | 275.5919 | 0 | 0 | 0 | 0 | 0 | 200 | 162000 | 200 | 365910.696 | 510.81 | 75.5919
3904 | 6 | 0 | 0.69644 | 0.53782 | 223.1272 | 0 | 0 | 0 | 0 | 0 | 200 | 162000 | 200 | 366110.696 | 510.81 | 23.1272
3905 | 6 | 0 | 0.50084 | 0.5901 | 168.7772 | 0 | 0 | 0 | 0 | 0 | 168.7772 | 162000 | 168.7772 | 366279.4732 | 510.81 | 0
3906 | 6 | 0 | 0.29183 | 0.50656 | 104.9978 | 0 | 0 | 0 | 0 | 0 | 104.9978 | 162000 | 104.9978 | 366384.471 | 510.81 | 0
3907 | 6 | 0 | 0.10077 | 0.332 | 42.6813 | 0 | 0 | 0 | 0 | 0 | 42.6813 | 162000 | 42.6813 | 366427.1523 | 510.81 | 0
3908 | 6 | 1 | 0 | 0.31427 | 12.8536 | 200 | 12.8536 | 180 | 192.8536 | 0 | 0 | 161800 | 192.8536 | 366620.0058 | 330.81 | 0
3909 | 6 | 1 | 0 | 0.30904 | 12.6395 | 200 | 12.6395 | 180 | 192.6395 | 0 | 0 | 161600 | 192.6395 | 366812.6454 | 150.81 | 0
3910 | 6 | 0 | 0 | 0.21357 | 8.735 | 0 | 0 | 0 | 0 | 8.735 | 0 | 161600 | 0 | 366812.6454 | 158.3815 | 0
3911 | 6 | 0 | 0 | 0.19113 | 7.8173 | 0 | 0 | 0 | 0 | 7.8173 | 0 | 161600 | 0 | 366812.6454 | 165.1575 | 0
3912 | 6 | 0 | 0 | 0.21772 | 8.9048 | 0 | 0 | 0 | 0 | 8.9048 | 0 | 161600 | 0 | 366812.6454 | 172.8762 | 0
3913 | 6 | 0 | 0 | 0.34347 | 14.0481 | 0 | 0 | 0 | 0 | 14.0481 | 0 | 161600 | 0 | 366812.6454 | 185.0531 | 0
3914 | 6 | 0 | 0 | 0.29229 | 11.9546 | 0 | 0 | 0 | 0 | 11.9546 | 0 | 161600 | 0 | 366812.6454 | 195.4153 | 0
3915 | 6 | 0 | 0 | 0.26891 | 10.9985 | 0 | 0 | 0 | 0 | 10.9985 | 0 | 161600 | 0 | 366812.6454 | 204.9488 | 0
3916 | 6 | 0 | 0 | 0.39991 | 16.3565 | 0 | 0 | 0 | 0 | 16.3565 | 0 | 161600 | 0 | 366812.6454 | 219.1266 | 0
3917 | 6 | 0 | 0 | 0.38006 | 15.5446 | 0 | 0 | 0 | 0 | 15.5446 | 0 | 161600 | 0 | 366812.6454 | 232.6007 | 0
3918 | 6 | 0 | 0 | 0.34535 | 14.1246 | 0 | 0 | 0 | 0 | 14.1246 | 0 | 161600 | 0 | 366812.6454 | 244.8439 | 0
3919 | 6 | 0 | 0.11959 | 0.37243 | 49.7696 | 0 | 0 | 0 | 0 | 49.7696 | 0 | 161600 | 0 | 366812.6454 | 287.9841 | 0
3920 | 6 | 1 | 0.34632 | 0.37725 | 115.4481 | 200 | 115.4481 | 84.5519 | 200 | 0 | 0 | 161400 | 200 | 367012.6454 | 203.4322 | 0
3921 | 6 | 1 | 0.59437 | 0.4922 | 191.785 | 200 | 191.785 | 8.215 | 200 | 0 | 0 | 161200 | 200 | 367212.6454 | 195.2173 | 0
3922 | 6 | 0 | 0.82649 | 0.44414 | 256.8564 | 0 | 0 | 0 | 0 | 180 | 76.8564 | 161200 | 76.8564 | 367289.5018 | 351.2413 | 0
3923 | 6 | 0 | 1 | 0.40894 | 305.5257 | 0 | 0 | 0 | 0 | 180 | 125.5257 | 161200 | 125.5257 | 367415.0275 | 507.2653 | 0
3924 | 6 | 0 | 1 | 0.51951 | 310.0479 | 0 | 0 | 0 | 0 | 4.0894 | 200 | 161200 | 200 | 367615.0275 | 510.81 | 105.9585
3925 | 6 | 0 | 1 | 0.71067 | 317.8666 | 0 | 0 | 0 | 0 | 0 | 200 | 161200 | 200 | 367815.0275 | 510.81 | 117.8666
3926 | 6 | 0 | 1 | 0.72088 | 318.2842 | 0 | 0 | 0 | 0 | 0 | 200 | 161200 | 200 | 368015.0275 | 510.81 | 118.2842
3927 | 6 | 0 | 1 | 0.93592 | 327.0793 | 0 | 0 | 0 | 0 | 0 | 200 | 161200 | 200 | 368215.0275 | 510.81 | 127.0793
3928 | 6 | 0 | 0.82649 | 0.75358 | 269.5125 | 0 | 0 | 0 | 0 | 0 | 200 | 161200 | 200 | 368415.0275 | 510.81 | 69.5125
3929 | 6 | 0 | 0.59437 | 0.63859 | 197.7726 | 0 | 0 | 0 | 0 | 0 | 197.7726 | 161200 | 197.7726 | 368612.8 | 510.81 | 0
3930 | 6 | 0 | 0.34632 | 0.78107 | 131.9645 | 0 | 0 | 0 | 0 | 0 | 131.9645 | 161200 | 131.9645 | 368744.7646 | 510.81 | 0
3931 | 6 | 0 | 0.11959 | 0.54875 | 56.9813 | 0 | 0 | 0 | 0 | 0 | 56.9813 | 161200 | 56.9813 | 368801.7459 | 510.81 | 0
3932 | 6 | 1 | 0 | 0.59028 | 24.1426 | 200 | 24.1426 | 175.8574 | 200 | 0 | 0 | 161000 | 200 | 369001.7459 | 334.9526 | 0
3933 | 6 | 1 | 0 | 0.40593 | 16.6024 | 200 | 16.6024 | 180 | 196.6024 | 0 | 0 | 160800 | 196.6024 | 369198.3483 | 154.9526 | 0
3934 | 6 | 0 | 0 | 0.40042 | 16.3771 | 0 | 0 | 0 | 0 | 16.3771 | 0 | 160800 | 0 | 369198.3483 | 169.1482 | 0
3935 | 6 | 0 | 0 | 0.34105 | 13.949 | 0 | 0 | 0 | 0 | 13.949 | 0 | 160800 | 0 | 369198.3483 | 181.2393 | 0
3936 | 6 | 0 | 0 | 0.27027 | 11.0542 | 0 | 0 | 0 | 0 | 11.0542 | 0 | 160800 | 0 | 369198.3483 | 190.8211 | 0
3937 | 6 | 0 | 0 | 0.20812 | 8.5123 | 0 | 0 | 0 | 0 | 8.5123 | 0 | 160800 | 0 | 369198.3483 | 198.1995 | 0
3938 | 6 | 0 | 0 | 0.17331 | 7.0885 | 0 | 0 | 0 | 0 | 7.0885 | 0 | 160800 | 0 | 369198.3483 | 204.3438 | 0
3939 | 6 | 0 | 0 | 0.21113 | 8.6353 | 0 | 0 | 0 | 0 | 8.6353 | 0 | 160800 | 0 | 369198.3483 | 211.8289 | 0
3940 | 6 | 0 | 0 | 0.19914 | 8.1447 | 0 | 0 | 0 | 0 | 8.1447 | 0 | 160800 | 0 | 369198.3483 | 218.8887 | 0
3941 | 6 | 0 | 0 | 0.22909 | 9.3699 | 0 | 0 | 0 | 0 | 9.3699 | 0 | 160800 | 0 | 369198.3483 | 227.0106 | 0
3942 | 6 | 0 | 0 | 0.20821 | 8.5159 | 0 | 0 | 0 | 0 | 8.5159 | 0 | 160800 | 0 | 369198.3483 | 234.3922 | 0
3943 | 6 | 0 | 0.10659 | 0.2086 | 39.3145 | 0 | 0 | 0 | 0 | 39.3145 | 0 | 160800 | 0 | 369198.3483 | 268.47 | 0
3944 | 6 | 1 | 0.30868 | 0.19872 | 97.2733 | 200 | 97.2733 | 102.7267 | 200 | 0 | 0 | 160600 | 200 | 369398.3483 | 165.7433 | 0
3945 | 6 | 1 | 0.52975 | 0.30198 | 165.3441 | 200 | 165.3441 | 34.6559 | 200 | 0 | 0 | 160400 | 200 | 369598.3483 | 131.0874 | 0
3946 | 6 | 0 | 0.73664 | 0.43398 | 230.4926 | 0 | 0 | 0 | 0 | 180 | 50.4926 | 160400 | 50.4926 | 369648.8409 | 287.1114 | 0
3947 | 6 | 0 | 0.9038 | 0.45676 | 279.698 | 0 | 0 | 0 | 0 | 180 | 99.698 | 160400 | 99.698 | 369748.5388 | 443.1354 | 0
3948 | 6 | 0 | 1 | 0.76962 | 320.2773 | 0 | 0 | 0 | 0 | 78.0741 | 200 | 160400 | 200 | 369948.5388 | 510.81 | 42.2032
3949 | 6 | 0 | 1 | 0.84427 | 323.3305 | 0 | 0 | 0 | 0 | 0 | 200 | 160400 | 200 | 370148.5388 | 510.81 | 123.3305
3950 | 6 | 0 | 1 | 0.69223 | 317.1122 | 0 | 0 | 0 | 0 | 0 | 200 | 160400 | 200 | 370348.5388 | 510.81 | 117.1122
3951 | 6 | 0 | 0.9038 | 0.60324 | 285.6889 | 0 | 0 | 0 | 0 | 0 | 200 | 160400 | 200 | 370548.5388 | 510.81 | 85.6889
3952 | 6 | 0 | 0.73664 | 0.51952 | 233.9913 | 0 | 0 | 0 | 0 | 0 | 200 | 160400 | 200 | 370748.5388 | 510.81 | 33.9913
3953 | 6 | 0 | 0.52975 | 0.58029 | 176.7271 | 0 | 0 | 0 | 0 | 0 | 176.7271 | 160400 | 176.7271 | 370925.266 | 510.81 | 0
3954 | 6 | 0 | 0.30868 | 0.66362 | 116.2876 | 0 | 0 | 0 | 0 | 0 | 116.2876 | 160400 | 116.2876 | 371041.5536 | 510.81 | 0
3955 | 6 | 0 | 0.10659 | 0.57351 | 54.2393 | 0 | 0 | 0 | 0 | 0 | 54.2393 | 160400 | 54.2393 | 371095.7929 | 510.81 | 0
3956 | 6 | 1 | 0 | 0.65906 | 26.9555 | 200 | 26.9555 | 173.0445 | 200 | 0 | 0 | 160200 | 200 | 371295.7929 | 337.7655 | 0
3957 | 6 | 1 | 0 | 0.77534 | 31.7114 | 200 | 31.7114 | 168.2886 | 200 | 0 | 0 | 160000 | 200 | 371495.7929 | 169.477 | 0
3958 | 6 | 0 | 0 | 0.74981 | 30.6671 | 0 | 0 | 0 | 0 | 30.6671 | 0 | 160000 | 0 | 371495.7929 | 196.0592 | 0
3959 | 6 | 0 | 0 | 0.72093 | 29.4859 | 0 | 0 | 0 | 0 | 29.4859 | 0 | 160000 | 0 | 371495.7929 | 221.6176 | 0
3960 | 6 | 0 | 0 | 0.69118 | 28.2692 | 0 | 0 | 0 | 0 | 28.2692 | 0 | 160000 | 0 | 371495.7929 | 246.1213 | 0
3961 | 6 | 0 | 0 | 0.54225 | 22.178 | 0 | 0 | 0 | 0 | 22.178 | 0 | 160000 | 0 | 371495.7929 | 265.3452 | 0
3962 | 6 | 0 | 0 | 0.48337 | 19.7699 | 0 | 0 | 0 | 0 | 19.7699 | 0 | 160000 | 0 | 371495.7929 | 282.4817 | 0
3963 | 6 | 0 | 0 | 0.53727 | 21.9744 | 0 | 0 | 0 | 0 | 21.9744 | 0 | 160000 | 0 | 371495.7929 | 301.5291 | 0
3964 | 6 | 0 | 0 | 0.72584 | 29.6867 | 0 | 0 | 0 | 0 | 29.6867 | 0 | 160000 | 0 | 371495.7929 | 327.2615 | 0
3965 | 6 | 0 | 0 | 0.40266 | 16.4688 | 0 | 0 | 0 | 0 | 16.4688 | 0 | 160000 | 0 | 371495.7929 | 341.5367 | 0
3966 | 6 | 0 | 0 | 0.43093 | 17.6249 | 0 | 0 | 0 | 0 | 17.6249 | 0 | 160000 | 0 | 371495.7929 | 356.8139 | 0
3967 | 6 | 0 | 0.10415 | 0.43964 | 48.0583 | 0 | 0 | 0 | 0 | 48.0583 | 0 | 160000 | 0 | 371495.7929 | 398.4709 | 0
3968 | 6 | 1 | 0.3016 | 0.45644 | 105.7715 | 200 | 105.7715 | 94.2285 | 200 | 0 | 0 | 159800 | 200 | 371695.7929 | 304.2424 | 0
3969 | 6 | 1 | 0.51762 | 0.42894 | 167.0312 | 200 | 167.0312 | 32.9688 | 200 | 0 | 0 | 159600 | 200 | 371895.7929 | 271.2736 | 0
3970 | 6 | 0 | 0.71976 | 0.28309 | 219.4462 | 0 | 0 | 0 | 0 | 180 | 39.4462 | 159600 | 39.4462 | 371935.2391 | 427.2976 | 0
3971 | 6 | 0 | 0.88309 | 0.38155 | 270.6405 | 0 | 0 | 0 | 0 | 96.3456 | 174.2948 | 159600 | 174.2948 | 372109.534 | 510.81 | 0
3972 | 6 | 0 | 0.9889 | 0.39006 | 301.5468 | 0 | 0 | 0 | 0 | 0 | 200 | 159600 | 200 | 372309.534 | 510.81 | 101.5468
3973 | 6 | 0 | 1 | 0.4208 | 306.0107 | 0 | 0 | 0 | 0 | 0 | 200 | 159600 | 200 | 372509.534 | 510.81 | 106.0107
3974 | 6 | 0 | 0.9889 | 0.51241 | 306.5511 | 0 | 0 | 0 | 0 | 0 | 200 | 159600 | 200 | 372709.534 | 510.81 | 106.5511
3975 | 6 | 0 | 0.88309 | 0.72342 | 284.6232 | 0 | 0 | 0 | 0 | 0 | 200 | 159600 | 200 | 372909.534 | 510.81 | 84.6232
3976 | 6 | 0 | 0.71976 | 0.67462 | 235.4599 | 0 | 0 | 0 | 0 | 0 | 200 | 159600 | 200 | 373109.534 | 510.81 | 35.4599
3977 | 6 | 0 | 0.51762 | 0.6957 | 177.9417 | 0 | 0 | 0 | 0 | 0 | 177.9417 | 159600 | 177.9417 | 373287.4757 | 510.81 | 0
3978 | 6 | 0 | 0.3016 | 0.40004 | 103.4646 | 0 | 0 | 0 | 0 | 0 | 103.4646 | 159600 | 103.4646 | 373390.9403 | 510.81 | 0
3979 | 6 | 0 | 0.10415 | 0.25918 | 40.6776 | 0 | 0 | 0 | 0 | 0 | 40.6776 | 159600 | 40.6776 | 373431.6179 | 510.81 | 0
3980 | 6 | 1 | 0 | 0.31418 | 12.8501 | 200 | 12.8501 | 180 | 192.8501 | 0 | 0 | 159400 | 192.8501 | 373624.468 | 330.81 | 0
3981 | 6 | 1 | 0 | 0.21807 | 8.9191 | 200 | 8.9191 | 180 | 188.9191 | 0 | 0 | 159200 | 188.9191 | 373813.3871 | 150.81 | 0
3982 | 6 | 0 | 0 | 0.19686 | 8.0517 | 0 | 0 | 0 | 0 | 8.0517 | 0 | 159200 | 0 | 373813.3871 | 157.7892 | 0
3983 | 6 | 0 | 0 | 0.11682 | 4.7779 | 0 | 0 | 0 | 0 | 4.7779 | 0 | 159200 | 0 | 373813.3871 | 161.9307 | 0
3984 | 6 | 0 | 0 | 0.13492 | 5.5182 | 0 | 0 | 0 | 0 | 5.5182 | 0 | 159200 | 0 | 373813.3871 | 166.7139 | 0
3985 | 6 | 0 | 0 | 0.13181 | 5.3909 | 0 | 0 | 0 | 0 | 5.3909 | 0 | 159200 | 0 | 373813.3871 | 171.3868 | 0
3986 | 6 | 0 | 0 | 0.15824 | 6.4721 | 0 | 0 | 0 | 0 | 6.4721 | 0 | 159200 | 0 | 373813.3871 | 176.9967 | 0
3987 | 6 | 0 | 0 | 0.14159 | 5.7912 | 0 | 0 | 0 | 0 | 5.7912 | 0 | 159200 | 0 | 373813.3871 | 182.0166 | 0
3988 | 6 | 0 | 0 | 0.0881 | 3.6033 | 0 | 0 | 0 | 0 | 3.6033 | 0 | 159200 | 0 | 373813.3871 | 185.1399 | 0
3989 | 6 | 0 | 0 | 0.1283 | 5.2476 | 0 | 0 | 0 | 0 | 5.2476 | 0 | 159200 | 0 | 373813.3871 | 189.6885 | 0
3990 | 6 | 0 | 0 | 0.12878 | 5.267 | 0 | 0 | 0 | 0 | 5.267 | 0 | 159200 | 0 | 373813.3871 | 194.254 | 0
3991 | 6 | 0 | 0.10962 | 0.092496 | 35.4425 | 0 | 0 | 0 | 0 | 35.4425 | 0 | 159200 | 0 | 373813.3871 | 224.9755 | 0
3992 | 6 | 1 | 0.31747 | 0.15462 | 98.0088 | 200 | 98.0088 | 101.9912 | 200 | 0 | 0 | 159000 | 200 | 374013.3871 | 122.9843 | 0
3993 | 6 | 1 | 0.54485 | 0.10171 | 161.5113 | 200 | 161.5113 | 38.4887 | 200 | 0 | 0 | 158800 | 200 | 374213.3871 | 84.4956 | 0
3994 | 6 | 0 | 0.75763 | 0.095016 | 222.6885 | 0 | 0 | 0 | 0 | 180 | 42.6885 | 158800 | 42.6885 | 374256.0757 | 240.5196 | 0
3995 | 6 | 0 | 0.92954 | 0.14549 | 274.4016 | 0 | 0 | 0 | 0 | 180 | 94.4016 | 158800 | 94.4016 | 374350.4773 | 396.5436 | 0
3996 | 6 | 0 | 1 | 0.24911 | 298.9888 | 0 | 0 | 0 | 0 | 131.8256 | 167.1632 | 158800 | 167.1632 | 374517.6404 | 510.81 | 0
3997 | 6 | 0 | 1 | 0.20953 | 297.3697 | 0 | 0 | 0 | 0 | 0 | 200 | 158800 | 200 | 374717.6404 | 510.81 | 97.3697
3998 | 6 | 0 | 1 | 0.20135 | 297.0353 | 0 | 0 | 0 | 0 | 0 | 200 | 158800 | 200 | 374917.6404 | 510.81 | 97.0353
3999 | 6 | 0 | 0.92954 | 0.22608 | 277.6974 | 0 | 0 | 0 | 0 | 0 | 200 | 158800 | 200 | 375117.6404 | 510.81 | 77.6974
4000 | 6 | 0 | 0.75763 | 0.25289 | 229.1454 | 0 | 0 | 0 | 0 | 0 | 200 | 158800 | 200 | 375317.6404 | 510.81 | 29.1454
4001 | 6 | 0 | 0.54485 | 0.29313 | 169.3404 | 0 | 0 | 0 | 0 | 0 | 169.3404 | 158800 | 169.3404 | 375486.9809 | 510.81 | 0
4002 | 6 | 0 | 0.31747 | 0.2132 | 100.4047 | 0 | 0 | 0 | 0 | 0 | 100.4047 | 158800 | 100.4047 | 375587.3856 | 510.81 | 0
4003 | 6 | 0 | 0.10962 | 0.1505 | 37.8147 | 0 | 0 | 0 | 0 | 0 | 37.8147 | 158800 | 37.8147 | 375625.2003 | 510.81 | 0
4004 | 6 | 1 | 0 | 0.17516 | 7.1641 | 200 | 7.1641 | 180 | 187.1641 | 0 | 0 | 158600 | 187.1641 | 375812.3644 | 330.81 | 0
4005 | 6 | 1 | 0 | 0.15791 | 6.4584 | 200 | 6.4584 | 180 | 186.4584 | 0 | 0 | 158400 | 186.4584 | 375998.8227 | 150.81 | 0
4006 | 6 | 0 | 0 | 0.14467 | 5.9169 | 0 | 0 | 0 | 0 | 5.9169 | 0 | 158400 | 0 | 375998.8227 | 155.9388 | 0
4007 | 6 | 0 | 0 | 0.14085 | 5.7606 | 0 | 0 | 0 | 0 | 5.7606 | 0 | 158400 | 0 | 375998.8227 | 160.9321 | 0
4008 | 6 | 0 | 0 | 0.16378 | 6.6986 | 0 | 0 | 0 | 0 | 6.6986 | 0 | 158400 | 0 | 375998.8227 | 166.7384 | 0
4009 | 6 | 0 | 0 | 0.17579 | 7.19 | 0 | 0 | 0 | 0 | 7.19 | 0 | 158400 | 0 | 375998.8227 | 172.9707 | 0
4010 | 6 | 0 | 0 | 0.20211 | 8.2661 | 0 | 0 | 0 | 0 | 8.2661 | 0 | 158400 | 0 | 375998.8227 | 180.1357 | 0
4011 | 6 | 0 | 0 | 0.26244 | 10.7338 | 0 | 0 | 0 | 0 | 10.7338 | 0 | 158400 | 0 | 375998.8227 | 189.4398 | 0
4012 | 6 | 0 | 0 | 0.26732 | 10.9336 | 0 | 0 | 0 | 0 | 10.9336 | 0 | 158400 | 0 | 375998.8227 | 198.917 | 0
4013 | 6 | 0 | 0 | 0.33744 | 13.8012 | 0 | 0 | 0 | 0 | 13.8012 | 0 | 158400 | 0 | 375998.8227 | 210.8799 | 0
4014 | 6 | 0 | 0 | 0.39466 | 16.1415 | 0 | 0 | 0 | 0 | 16.1415 | 0 | 158400 | 0 | 375998.8227 | 224.8714 | 0
4015 | 6 | 0 | 0.11311 | 0.30475 | 45.1316 | 0 | 0 | 0 | 0 | 45.1316 | 0 | 158400 | 0 | 375998.8227 | 263.9914 | 0
4016 | 6 | 1 | 0.32758 | 0.26508 | 105.4454 | 200 | 105.4454 | 94.5546 | 200 | 0 | 0 | 158200 | 200 | 376198.8227 | 169.4367 | 0
4017 | 6 | 1 | 0.56219 | 0.39425 | 178.4856 | 200 | 178.4856 | 21.5144 | 200 | 0 | 0 | 158000 | 200 | 376398.8227 | 147.9224 | 0
4018 | 6 | 0 | 0.78175 | 0.33325 | 239.3984 | 0 | 0 | 0 | 0 | 180 | 59.3984 | 158000 | 59.3984 | 376458.2211 | 303.9464 | 0
4019 | 6 | 0 | 0.95913 | 0.268 | 287.959 | 0 | 0 | 0 | 0 | 180 | 107.959 | 158000 | 107.959 | 376566.1801 | 459.9704 | 0
4020 | 6 | 0 | 1 | 0.37191 | 304.0111 | 0 | 0 | 0 | 0 | 58.6521 | 200 | 158000 | 200 | 376766.1801 | 510.81 | 45.359
4021 | 6 | 0 | 1 | 0.48927 | 308.8112 | 0 | 0 | 0 | 0 | 0 | 200 | 158000 | 200 | 376966.1801 | 510.81 | 108.8112
4022 | 6 | 0 | 1 | 0.5347 | 310.669 | 0 | 0 | 0 | 0 | 0 | 200 | 158000 | 200 | 377166.1801 | 510.81 | 110.669
4023 | 6 | 0 | 0.95913 | 0.39325 | 293.0818 | 0 | 0 | 0 | 0 | 0 | 200 | 158000 | 200 | 377366.1801 | 510.81 | 93.0818
4024 | 6 | 0 | 0.78175 | 0.37218 | 240.9906 | 0 | 0 | 0 | 0 | 0 | 200 | 158000 | 200 | 377566.1801 | 510.81 | 40.9906
4025 | 6 | 0 | 0.56219 | 0.34459 | 176.4545 | 0 | 0 | 0 | 0 | 0 | 176.4545 | 158000 | 176.4545 | 377742.6346 | 510.81 | 0
4026 | 6 | 0 | 0.32758 | 0.25764 | 105.1411 | 0 | 0 | 0 | 0 | 0 | 105.1411 | 158000 | 105.1411 | 377847.7757 | 510.81 | 0
4027 | 6 | 0 | 0.11311 | 0.29862 | 44.881 | 0 | 0 | 0 | 0 | 0 | 44.881 | 158000 | 44.881 | 377892.6567 | 510.81 | 0
4028 | 6 | 1 | 0 | 0.33473 | 13.6903 | 200 | 13.6903 | 180 | 193.6903 | 0 | 0 | 157800 | 193.6903 | 378086.347 | 330.81 | 0
4029 | 6 | 1 | 0 | 0.25502 | 10.4305 | 200 | 10.4305 | 180 | 190.4305 | 0 | 0 | 157600 | 190.4305 | 378276.7775 | 150.81 | 0
4030 | 6 | 0 | 0 | 0.31093 | 12.7168 | 0 | 0 | 0 | 0 | 12.7168 | 0 | 157600 | 0 | 378276.7775 | 161.833 | 0
4031 | 6 | 0 | 0 | 0.31583 | 12.9172 | 0 | 0 | 0 | 0 | 12.9172 | 0 | 157600 | 0 | 378276.7775 | 173.0296 | 0
4032 | 6 | 0 | 0 | 0.3874 | 15.8445 | 0 | 0 | 0 | 0 | 15.8445 | 0 | 157600 | 0 | 378276.7775 | 186.7636 | 0
4033 | 6 | 0 | 0 | 0.33684 | 13.7769 | 0 | 0 | 0 | 0 | 13.7769 | 0 | 157600 | 0 | 378276.7775 | 198.7055 | 0
4034 | 6 | 0 | 0 | 0.3493 | 14.2866 | 0 | 0 | 0 | 0 | 14.2866 | 0 | 157600 | 0 | 378276.7775 | 211.0891 | 0
4035 | 6 | 0 | 0 | 0.25592 | 10.467 | 0 | 0 | 0 | 0 | 10.467 | 0 | 157600 | 0 | 378276.7775 | 220.1618 | 0
4036 | 6 | 0 | 0 | 0.32836 | 13.4301 | 0 | 0 | 0 | 0 | 13.4301 | 0 | 157600 | 0 | 378276.7775 | 231.803 | 0
4037 | 6 | 0 | 0 | 0.46595 | 19.0574 | 0 | 0 | 0 | 0 | 19.0574 | 0 | 157600 | 0 | 378276.7775 | 248.322 | 0
4038 | 6 | 0 | 0 | 0.54251 | 22.1888 | 0 | 0 | 0 | 0 | 22.1888 | 0 | 157600 | 0 | 378276.7775 | 267.5552 | 0
4039 | 6 | 0 | 0.11678 | 0.52734 | 55.2952 | 0 | 0 | 0 | 0 | 55.2952 | 0 | 157600 | 0 | 378276.7775 | 315.4851 | 0
4040 | 6 | 1 | 0.3382 | 0.6233 | 123.1654 | 200 | 123.1654 | 76.8346 | 200 | 0 | 0 | 157400 | 200 | 378476.7775 | 238.6505 | 0
4041 | 6 | 1 | 0.58043 | 0.61065 | 192.6026 | 200 | 192.6026 | 7.3974 | 200 | 0 | 0 | 157200 | 200 | 378676.7775 | 231.2531 | 0
4042 | 6 | 0 | 0.8071 | 0.58219 | 256.9033 | 0 | 0 | 0 | 0 | 180 | 76.9033 | 157200 | 76.9033 | 378753.6809 | 387.2771 | 0
4043 | 6 | 0 | 0.99024 | 0.92744 | 323.9147 | 0 | 0 | 0 | 0 | 142.516 | 181.3987 | 157200 | 181.3987 | 378935.0795 | 510.81 | 0
4044 | 6 | 0 | 1 | 0.92966 | 326.8233 | 0 | 0 | 0 | 0 | 0 | 200 | 157200 | 200 | 379135.0795 | 510.81 | 126.8233
4045 | 6 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 0 | 200 | 157200 | 200 | 379335.0795 | 510.81 | 129.7
4046 | 6 | 0 | 1 | 0.99039 | 329.3071 | 0 | 0 | 0 | 0 | 0 | 200 | 157200 | 200 | 379535.0795 | 510.81 | 129.3071
4047 | 6 | 0 | 0.99024 | 0.70692 | 314.8953 | 0 | 0 | 0 | 0 | 0 | 200 | 157200 | 200 | 379735.0795 | 510.81 | 114.8953
4048 | 6 | 0 | 0.8071 | 0.76304 | 264.2998 | 0 | 0 | 0 | 0 | 0 | 200 | 157200 | 200 | 379935.0795 | 510.81 | 64.2998
4049 | 6 | 0 | 0.58043 | 0.60555 | 192.3941 | 0 | 0 | 0 | 0 | 0 | 192.3941 | 157200 | 192.3941 | 380127.4737 | 510.81 | 0
4050 | 6 | 0 | 0.3382 | 0.65777 | 124.5752 | 0 | 0 | 0 | 0 | 0 | 124.5752 | 157200 | 124.5752 | 380252.0488 | 510.81 | 0
4051 | 6 | 0 | 0.11678 | 0.39105 | 49.7207 | 0 | 0 | 0 | 0 | 0 | 49.7207 | 157200 | 49.7207 | 380301.7695 | 510.81 | 0
4052 | 6 | 1 | 0 | 0.55666 | 22.7674 | 200 | 22.7674 | 177.2326 | 200 | 0 | 0 | 157000 | 200 | 380501.7695 | 333.5774 | 0
4053 | 6 | 1 | 0 | 0.26411 | 10.8019 | 200 | 10.8019 | 180 | 190.8019 | 0 | 0 | 156800 | 190.8019 | 380692.5715 | 153.5774 | 0
4054 | 6 | 0 | 0 | 0.31347 | 12.821 | 0 | 0 | 0 | 0 | 12.821 | 0 | 156800 | 0 | 380692.5715 | 164.6906 | 0
4055 | 6 | 0 | 0 | 0.37657 | 15.4019 | 0 | 0 | 0 | 0 | 15.4019 | 0 | 156800 | 0 | 380692.5715 | 178.041 | 0
4056 | 6 | 0 | 0 | 0.35602 | 14.5613 | 0 | 0 | 0 | 0 | 14.5613 | 0 | 156800 | 0 | 380692.5715 | 190.6628 | 0
4057 | 6 | 0 | 0 | 0.21917 | 8.9642 | 0 | 0 | 0 | 0 | 8.9642 | 0 | 156800 | 0 | 380692.5715 | 198.433 | 0
4058 | 6 | 0 | 0 | 0.23497 | 9.6104 | 0 | 0 | 0 | 0 | 9.6104 | 0 | 156800 | 0 | 380692.5715 | 206.7633 | 0
4059 | 6 | 0 | 0 | 0.28752 | 11.7595 | 0 | 0 | 0 | 0 | 11.7595 | 0 | 156800 | 0 | 380692.5715 | 216.9564 | 0
4060 | 6 | 0 | 0 | 0.36522 | 14.9377 | 0 | 0 | 0 | 0 | 14.9377 | 0 | 156800 | 0 | 380692.5715 | 229.9043 | 0
4061 | 6 | 0 | 0 | 0.32366 | 13.2375 | 0 | 0 | 0 | 0 | 13.2375 | 0 | 156800 | 0 | 380692.5715 | 241.3786 | 0
4062 | 6 | 0 | 0 | 0.41017 | 16.7761 | 0 | 0 | 0 | 0 | 16.7761 | 0 | 156800 | 0 | 380692.5715 | 255.9201 | 0
4063 | 6 | 0 | 0.12326 | 0.28299 | 47.1722 | 0 | 0 | 0 | 0 | 47.1722 | 0 | 156800 | 0 | 380692.5715 | 296.809 | 0
4064 | 6 | 1 | 0.35696 | 0.29221 | 115.0424 | 200 | 115.0424 | 84.9576 | 200 | 0 | 0 | 156600 | 200 | 380892.5715 | 211.8514 | 0
4065 | 6 | 1 | 0.61263 | 0.38428 | 192.6441 | 200 | 192.6441 | 7.3559 | 200 | 0 | 0 | 156400 | 200 | 381092.5715 | 204.4955 | 0
4066 | 6 | 0 | 0.85188 | 0.4972 | 266.3584 | 0 | 0 | 0 | 0 | 180 | 86.3584 | 156400 | 86.3584 | 381178.9299 | 360.5195 | 0
4067 | 6 | 0 | 1 | 0.60258 | 313.4455 | 0 | 0 | 0 | 0 | 173.3854 | 140.0601 | 156400 | 140.0601 | 381318.99 | 510.81 | 0
4068 | 6 | 0 | 1 | 0.40808 | 305.4907 | 0 | 0 | 0 | 0 | 0 | 200 | 156400 | 200 | 381518.99 | 510.81 | 105.4907
4069 | 6 | 0 | 1 | 0.49722 | 309.1362 | 0 | 0 | 0 | 0 | 0 | 200 | 156400 | 200 | 381718.99 | 510.81 | 109.1362
4070 | 6 | 0 | 1 | 0.39834 | 305.092 | 0 | 0 | 0 | 0 | 0 | 200 | 156400 | 200 | 381918.99 | 510.81 | 105.092
4071 | 6 | 0 | 1 | 0.44783 | 307.1161 | 0 | 0 | 0 | 0 | 0 | 200 | 156400 | 200 | 382118.99 | 510.81 | 107.1161
4072 | 6 | 0 | 0.85188 | 0.45996 | 264.8355 | 0 | 0 | 0 | 0 | 0 | 200 | 156400 | 200 | 382318.99 | 510.81 | 64.8355
4073 | 6 | 0 | 0.61263 | 0.43757 | 194.8235 | 0 | 0 | 0 | 0 | 0 | 194.8235 | 156400 | 194.8235 | 382513.8135 | 510.81 | 0
4074 | 6 | 0 | 0.35696 | 0.42784 | 120.5896 | 0 | 0 | 0 | 0 | 0 | 120.5896 | 156400 | 120.5896 | 382634.4031 | 510.81 | 0
4075 | 6 | 0 | 0.12326 | 0.43704 | 53.4729 | 0 | 0 | 0 | 0 | 0 | 53.4729 | 156400 | 53.4729 | 382687.876 | 510.81 | 0
4076 | 6 | 1 | 0 | 0.34441 | 14.0865 | 200 | 14.0865 | 180 | 194.0865 | 0 | 0 | 156200 | 194.0865 | 382881.9625 | 330.81 | 0
4077 | 6 | 1 | 0 | 0.28687 | 11.7331 | 200 | 11.7331 | 180 | 191.7331 | 0 | 0 | 156000 | 191.7331 | 383073.6956 | 150.81 | 0
4078 | 6 | 0 | 0 | 0.23352 | 9.5509 | 0 | 0 | 0 | 0 | 9.5509 | 0 | 156000 | 0 | 383073.6956 | 159.0887 | 0
4079 | 6 | 0 | 0 | 0.30035 | 12.2842 | 0 | 0 | 0 | 0 | 12.2842 | 0 | 156000 | 0 | 383073.6956 | 169.7366 | 0
4080 | 6 | 0 | 0 | 0.25291 | 10.3439 | 0 | 0 | 0 | 0 | 10.3439 | 0 | 156000 | 0 | 383073.6956 | 178.7027 | 0
4081 | 6 | 0 | 0 | 0.21733 | 8.889 | 0 | 0 | 0 | 0 | 8.889 | 0 | 156000 | 0 | 383073.6956 | 186.4077 | 0
4082 | 6 | 0 | 0 | 0.21616 | 8.8407 | 0 | 0 | 0 | 0 | 8.8407 | 0 | 156000 | 0 | 383073.6956 | 194.0708 | 0
4083 | 6 | 0 | 0 | 0.23775 | 9.7238 | 0 | 0 | 0 | 0 | 9.7238 | 0 | 156000 | 0 | 383073.6956 | 202.4994 | 0
4084 | 6 | 0 | 0 | 0.3346 | 13.6852 | 0 | 0 | 0 | 0 | 13.6852 | 0 | 156000 | 0 | 383073.6956 | 214.3617 | 0
4085 | 6 | 0 | 0 | 0.36934 | 15.1058 | 0 | 0 | 0 | 0 | 15.1058 | 0 | 156000 | 0 | 383073.6956 | 227.4554 | 0
4086 | 6 | 0 | 0 | 0.45306 | 18.5303 | 0 | 0 | 0 | 0 | 18.5303 | 0 | 156000 | 0 | 383073.6956 | 243.5175 | 0
4087 | 6 | 0 | 0.094821 | 0.44827 | 45.7184 | 0 | 0 | 0 | 0 | 45.7184 | 0 | 156000 | 0 | 383073.6956 | 283.1462 | 0
4088 | 6 | 1 | 0.2746 | 0.42989 | 96.8871 | 200 | 96.8871 | 103.1129 | 200 | 0 | 0 | 155800 | 200 | 383273.6956 | 180.0333 | 0
4089 | 6 | 1 | 0.47127 | 0.49413 | 156.3134 | 200 | 156.3134 | 43.6866 | 200 | 0 | 0 | 155600 | 200 | 383473.6956 | 136.3467 | 0
4090 | 6 | 0 | 0.65532 | 0.49914 | 209.6719 | 0 | 0 | 0 | 0 | 180 | 29.6719 | 155600 | 29.6719 | 383503.3675 | 292.3707 | 0
4091 | 6 | 0 | 0.80402 | 0.51518 | 253.2723 | 0 | 0 | 0 | 0 | 180 | 73.2723 | 155600 | 73.2723 | 383576.6398 | 448.3947 | 0
4092 | 6 | 0 | 0.90036 | 0.59361 | 284.3026 | 0 | 0 | 0 | 0 | 72.0066 | 200 | 155600 | 200 | 383776.6398 | 510.81 | 12.296
4093 | 6 | 0 | 0.93368 | 0.58071 | 293.3991 | 0 | 0 | 0 | 0 | 0 | 200 | 155600 | 200 | 383976.6398 | 510.81 | 93.3991
4094 | 6 | 0 | 0.90036 | 0.78473 | 292.1194 | 0 | 0 | 0 | 0 | 0 | 200 | 155600 | 200 | 384176.6398 | 510.81 | 92.1194
4095 | 6 | 0 | 0.80402 | 0.69133 | 260.4768 | 0 | 0 | 0 | 0 | 0 | 200 | 155600 | 200 | 384376.6398 | 510.81 | 60.4768
4096 | 6 | 0 | 0.65532 | 0.78548 | 221.3832 | 0 | 0 | 0 | 0 | 0 | 200 | 155600 | 200 | 384576.6398 | 510.81 | 21.3832
4097 | 6 | 0 | 0.47127 | 0.64488 | 162.4792 | 0 | 0 | 0 | 0 | 0 | 162.4792 | 155600 | 162.4792 | 384739.119 | 510.81 | 0
4098 | 6 | 0 | 0.2746 | 0.51302 | 100.2871 | 0 | 0 | 0 | 0 | 0 | 100.2871 | 155600 | 100.2871 | 384839.4061 | 510.81 | 0
4099 | 6 | 0 | 0.094821 | 0.46311 | 46.3255 | 0 | 0 | 0 | 0 | 0 | 46.3255 | 155600 | 46.3255 | 384885.7316 | 510.81 | 0
4100 | 6 | 1 | 0 | 0.48572 | 19.8659 | 200 | 19.8659 | 180 | 199.8659 | 0 | 0 | 155400 | 199.8659 | 385085.5975 | 330.81 | 0
4101 | 6 | 1 | 0 | 0.78264 | 32.0101 | 200 | 32.0101 | 167.9899 | 200 | 0 | 0 | 155200 | 200 | 385285.5975 | 162.8201 | 0
4102 | 6 | 0 | 0 | 0.75935 | 31.0573 | 0 | 0 | 0 | 0 | 31.0573 | 0 | 155200 | 0 | 385285.5975 | 189.7405 | 0
4103 | 6 | 0 | 0 | 0.76367 | 31.2342 | 0 | 0 | 0 | 0 | 31.2342 | 0 | 155200 | 0 | 385285.5975 | 216.8143 | 0
4104 | 6 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 155200 | 0 | 385285.5975 | 252.2665 | 0
4105 | 6 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 155200 | 0 | 385285.5975 | 287.7186 | 0
4106 | 6 | 0 | 0 | 0.91829 | 37.558 | 0 | 0 | 0 | 0 | 37.558 | 0 | 155200 | 0 | 385285.5975 | 320.2739 | 0
4107 | 6 | 0 | 0 | 0.86375 | 35.3274 | 0 | 0 | 0 | 0 | 35.3274 | 0 | 155200 | 0 | 385285.5975 | 350.8956 | 0
4108 | 6 | 0 | 0 | 0.96759 | 39.5744 | 0 | 0 | 0 | 0 | 39.5744 | 0 | 155200 | 0 | 385285.5975 | 385.1988 | 0
4109 | 6 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 155200 | 0 | 385285.5975 | 420.6509 | 0
4110 | 6 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 155200 | 0 | 385285.5975 | 456.103 | 0
4111 | 6 | 0 | 0.12064 | 0.99403 | 75.4959 | 0 | 0 | 0 | 0 | 63.1137 | 12.3821 | 155200 | 12.3821 | 385297.9797 | 510.81 | 0
4112 | 6 | 1 | 0.34937 | 1 | 141.7969 | 200 | 141.7969 | 58.2031 | 200 | 0 | 0 | 155000 | 200 | 385497.9797 | 452.6069 | 0
4113 | 6 | 1 | 0.59959 | 1 | 214.061 | 200 | 200 | 0 | 200 | 14.061 | 0 | 154800 | 200 | 385697.9797 | 464.795 | 0
4114 | 6 | 0 | 0.83375 | 1 | 281.6864 | 0 | 0 | 0 | 0 | 53.0861 | 200 | 154800 | 200 | 385897.9797 | 510.81 | 28.6003
4115 | 6 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 0 | 200 | 154800 | 200 | 386097.9797 | 510.81 | 129.7
4116 | 6 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 0 | 200 | 154800 | 200 | 386297.9797 | 510.81 | 129.7
4117 | 6 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 0 | 200 | 154800 | 200 | 386497.9797 | 510.81 | 129.7
4118 | 6 | 0 | 1 | 0.9803 | 328.8941 | 0 | 0 | 0 | 0 | 0 | 200 | 154800 | 200 | 386697.9797 | 510.81 | 128.8941
4119 | 6 | 0 | 1 | 0.58913 | 312.8953 | 0 | 0 | 0 | 0 | 0 | 200 | 154800 | 200 | 386897.9797 | 510.81 | 112.8953
4120 | 6 | 0 | 0.83375 | 0.52901 | 262.4228 | 0 | 0 | 0 | 0 | 0 | 200 | 154800 | 200 | 387097.9797 | 510.81 | 62.4228
4121 | 6 | 0 | 0.59959 | 0.43388 | 190.9066 | 0 | 0 | 0 | 0 | 0 | 190.9066 | 154800 | 190.9066 | 387288.8863 | 510.81 | 0
4122 | 6 | 0 | 0.34937 | 0.41309 | 117.7921 | 0 | 0 | 0 | 0 | 0 | 117.7921 | 154800 | 117.7921 | 387406.6784 | 510.81 | 0
4123 | 6 | 0 | 0.12064 | 0.51193 | 55.7781 | 0 | 0 | 0 | 0 | 0 | 55.7781 | 154800 | 55.7781 | 387462.4565 | 510.81 | 0
4124 | 6 | 1 | 0 | 0.44105 | 18.0387 | 200 | 18.0387 | 180 | 198.0387 | 0 | 0 | 154600 | 198.0387 | 387660.4952 | 330.81 | 0
4125 | 6 | 1 | 0 | 0.54387 | 22.2445 | 200 | 22.2445 | 177.7555 | 200 | 0 | 0 | 154400 | 200 | 387860.4952 | 153.0545 | 0
4126 | 6 | 0 | 0 | 0.77234 | 31.5886 | 0 | 0 | 0 | 0 | 31.5886 | 0 | 154400 | 0 | 387860.4952 | 180.4355 | 0
4127 | 6 | 0 | 0 | 0.74353 | 30.4105 | 0 | 0 | 0 | 0 | 30.4105 | 0 | 154400 | 0 | 387860.4952 | 206.7954 | 0
4128 | 6 | 0 | 0 | 0.62728 | 25.6558 | 0 | 0 | 0 | 0 | 25.6558 | 0 | 154400 | 0 | 387860.4952 | 229.0338 | 0
4129 | 6 | 0 | 0 | 0.42852 | 17.5266 | 0 | 0 | 0 | 0 | 17.5266 | 0 | 154400 | 0 | 387860.4952 | 244.2259 | 0
4130 | 6 | 0 | 0 | 0.32437 | 13.2667 | 0 | 0 | 0 | 0 | 13.2667 | 0 | 154400 | 0 | 387860.4952 | 255.7254 | 0
4131 | 6 | 0 | 0 | 0.3033 | 12.4051 | 0 | 0 | 0 | 0 | 12.4051 | 0 | 154400 | 0 | 387860.4952 | 266.4782 | 0
4132 | 6 | 0 | 0 | 0.31893 | 13.0441 | 0 | 0 | 0 | 0 | 13.0441 | 0 | 154400 | 0 | 387860.4952 | 277.7848 | 0
4133 | 6 | 0 | 0 | 0.34755 | 14.215 | 0 | 0 | 0 | 0 | 14.215 | 0 | 154400 | 0 | 387860.4952 | 290.1063 | 0
4134 | 6 | 0 | 0 | 0.24611 | 10.0658 | 0 | 0 | 0 | 0 | 10.0658 | 0 | 154400 | 0 | 387860.4952 | 298.8313 | 0
4135 | 6 | 0 | 0.11375 | 0.17485 | 40.0031 | 0 | 0 | 0 | 0 | 40.0031 | 0 | 154400 | 0 | 387860.4952 | 333.506 | 0
4136 | 6 | 1 | 0.32942 | 0.26912 | 106.1442 | 200 | 106.1442 | 93.8558 | 200 | 0 | 0 | 154200 | 200 | 388060.4952 | 239.6502 | 0
4137 | 6 | 1 | 0.56536 | 0.22941 | 172.659 | 200 | 172.659 | 27.341 | 200 | 0 | 0 | 154000 | 200 | 388260.4952 | 212.3092 | 0
4138 | 6 | 0 | 0.78615 | 0.27337 | 238.2217 | 0 | 0 | 0 | 0 | 180 | 58.2217 | 154000 | 58.2217 | 388318.7169 | 368.3332 | 0
4139 | 6 | 0 | 0.96454 | 0.42043 | 295.7546 | 0 | 0 | 0 | 0 | 164.371 | 131.3836 | 154000 | 131.3836 | 388450.1005 | 510.81 | 0
4140 | 6 | 0 | 1 | 0.5061 | 309.4995 | 0 | 0 | 0 | 0 | 0 | 200 | 154000 | 200 | 388650.1005 | 510.81 | 109.4995
4141 | 6 | 0 | 1 | 0.5239 | 310.2277 | 0 | 0 | 0 | 0 | 0 | 200 | 154000 | 200 | 388850.1005 | 510.81 | 110.2277
4142 | 6 | 0 | 1 | 0.39829 | 305.0901 | 0 | 0 | 0 | 0 | 0 | 200 | 154000 | 200 | 389050.1005 | 510.81 | 105.0901
4143 | 6 | 0 | 0.96454 | 0.39443 | 294.6912 | 0 | 0 | 0 | 0 | 0 | 200 | 154000 | 200 | 389250.1005 | 510.81 | 94.6912
4144 | 6 | 0 | 0.78615 | 0.31945 | 240.1064 | 0 | 0 | 0 | 0 | 0 | 200 | 154000 | 200 | 389450.1005 | 510.81 | 40.1064
4145 | 6 | 0 | 0.56536 | 0.39848 | 179.5737 | 0 | 0 | 0 | 0 | 0 | 179.5737 | 154000 | 179.5737 | 389629.6742 | 510.81 | 0
4146 | 6 | 0 | 0.32942 | 0.3669 | 110.1434 | 0 | 0 | 0 | 0 | 0 | 110.1434 | 154000 | 110.1434 | 389739.8177 | 510.81 | 0
4147 | 6 | 0 | 0.11375 | 0.27447 | 44.0774 | 0 | 0 | 0 | 0 | 0 | 44.0774 | 154000 | 44.0774 | 389783.895 | 510.81 | 0
4148 | 6 | 1 | 0 | 0.42587 | 17.4179 | 200 | 17.4179 | 180 | 197.4179 | 0 | 0 | 153800 | 197.4179 | 389981.3129 | 330.81 | 0
4149 | 6 | 1 | 0 | 0.43495 | 17.7896 | 200 | 17.7896 | 180 | 197.7896 | 0 | 0 | 153600 | 197.7896 | 390179.1026 | 150.81 | 0
4150 | 6 | 0 | 0 | 0.45953 | 18.7947 | 0 | 0 | 0 | 0 | 18.7947 | 0 | 153600 | 0 | 390179.1026 | 167.1013 | 0
4151 | 6 | 0 | 0 | 0.47366 | 19.3726 | 0 | 0 | 0 | 0 | 19.3726 | 0 | 153600 | 0 | 390179.1026 | 183.8934 | 0
4152 | 6 | 0 | 0 | 0.49925 | 20.4192 | 0 | 0 | 0 | 0 | 20.4192 | 0 | 153600 | 0 | 390179.1026 | 201.5928 | 0
4153 | 6 | 0 | 0 | 0.61979 | 25.3492 | 0 | 0 | 0 | 0 | 25.3492 | 0 | 153600 | 0 | 390179.1026 | 223.5655 | 0
4154 | 6 | 0 | 0 | 0.69251 | 28.3238 | 0 | 0 | 0 | 0 | 28.3238 | 0 | 153600 | 0 | 390179.1026 | 248.1166 | 0
4155 | 6 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 153600 | 0 | 390179.1026 | 283.5687 | 0
4156 | 6 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 153600 | 0 | 390179.1026 | 319.0208 | 0
4157 | 6 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 153600 | 0 | 390179.1026 | 354.473 | 0
4158 | 6 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 153600 | 0 | 390179.1026 | 389.9251 | 0
4159 | 6 | 0 | 0.13055 | 1 | 78.6017 | 0 | 0 | 0 | 0 | 78.6017 | 0 | 153600 | 0 | 390179.1026 | 458.057 | 0
4160 | 6 | 1 | 0.37806 | 1 | 150.0829 | 200 | 150.0829 | 49.9171 | 200 | 0 | 0 | 153400 | 200 | 390379.1026 | 408.1399 | 0
4161 | 6 | 1 | 0.64883 | 0.70078 | 216.0435 | 200 | 200 | 0 | 200 | 16.0435 | 0 | 153200 | 200 | 390579.1026 | 422.0464 | 0
4162 | 6 | 0 | 0.90222 | 0.57437 | 284.0525 | 0 | 0 | 0 | 0 | 102.4038 | 181.6487 | 153200 | 181.6487 | 390760.7512 | 510.81 | 0
4163 | 6 | 0 | 1 | 0.53861 | 310.8289 | 0 | 0 | 0 | 0 | 0 | 200 | 153200 | 200 | 390960.7512 | 510.81 | 110.8289
4164 | 6 | 0 | 1 | 0.32594 | 302.1312 | 0 | 0 | 0 | 0 | 0 | 200 | 153200 | 200 | 391160.7512 | 510.81 | 102.1312
4165 | 6 | 0 | 1 | 0.63142 | 314.6251 | 0 | 0 | 0 | 0 | 0 | 200 | 153200 | 200 | 391360.7512 | 510.81 | 114.6251
4166 | 6 | 0 | 1 | 0.69905 | 317.391 | 0 | 0 | 0 | 0 | 0 | 200 | 153200 | 200 | 391560.7512 | 510.81 | 117.391
4167 | 6 | 0 | 1 | 0.71866 | 318.1934 | 0 | 0 | 0 | 0 | 0 | 200 | 153200 | 200 | 391760.7512 | 510.81 | 118.1934
4168 | 6 | 0 | 0.90222 | 1 | 301.4608 | 0 | 0 | 0 | 0 | 0 | 200 | 153200 | 200 | 391960.7512 | 510.81 | 101.4608
4169 | 6 | 0 | 0.64883 | 1 | 228.2815 | 0 | 0 | 0 | 0 | 0 | 200 | 153200 | 200 | 392160.7512 | 510.81 | 28.2815
4170 | 6 | 0 | 0.37806 | 0.97971 | 149.2529 | 0 | 0 | 0 | 0 | 0 | 149.2529 | 153200 | 149.2529 | 392310.0041 | 510.81 | 0
4171 | 6 | 0 | 0.13055 | 0.66576 | 64.9311 | 0 | 0 | 0 | 0 | 0 | 64.9311 | 153200 | 64.9311 | 392374.9352 | 510.81 | 0
4172 | 6 | 1 | 0 | 0.88404 | 36.1571 | 200 | 36.1571 | 163.8429 | 200 | 0 | 0 | 153000 | 200 | 392574.9352 | 346.9671 | 0
4173 | 6 | 1 | 0 | 0.61564 | 25.1797 | 200 | 25.1797 | 174.8203 | 200 | 0 | 0 | 152800 | 200 | 392774.9352 | 172.1468 | 0
4174 | 6 | 0 | 0 | 0.52805 | 21.5972 | 0 | 0 | 0 | 0 | 21.5972 | 0 | 152800 | 0 | 392774.9352 | 190.8672 | 0
4175 | 6 | 0 | 0 | 0.48069 | 19.6601 | 0 | 0 | 0 | 0 | 19.6601 | 0 | 152800 | 0 | 392774.9352 | 207.9085 | 0
4176 | 6 | 0 | 0 | 0.67215 | 27.491 | 0 | 0 | 0 | 0 | 27.491 | 0 | 152800 | 0 | 392774.9352 | 231.7378 | 0
4177 | 6 | 0 | 0 | 0.61375 | 25.1025 | 0 | 0 | 0 | 0 | 25.1025 | 0 | 152800 | 0 | 392774.9352 | 253.4966 | 0
4178 | 6 | 0 | 0 | 0.54542 | 22.3078 | 0 | 0 | 0 | 0 | 22.3078 | 0 | 152800 | 0 | 392774.9352 | 272.833 | 0
4179 | 6 | 0 | 0 | 0.50129 | 20.5028 | 0 | 0 | 0 | 0 | 20.5028 | 0 | 152800 | 0 | 392774.9352 | 290.6048 | 0
4180 | 6 | 0 | 0 | 0.45063 | 18.4309 | 0 | 0 | 0 | 0 | 18.4309 | 0 | 152800 | 0 | 392774.9352 | 306.5807 | 0
4181 | 6 | 0 | 0 | 0.67525 | 27.6179 | 0 | 0 | 0 | 0 | 27.6179 | 0 | 152800 | 0 | 392774.9352 | 330.5199 | 0
4182 | 6 | 0 | 0 | 0.56105 | 22.9468 | 0 | 0 | 0 | 0 | 22.9468 | 0 | 152800 | 0 | 392774.9352 | 350.4102 | 0
4183 | 6 | 0 | 0.1363 | 0.66531 | 66.5741 | 0 | 0 | 0 | 0 | 66.5741 | 0 | 152800 | 0 | 392774.9352 | 408.1166 | 0
4184 | 6 | 1 | 0.39471 | 0.4807 | 133.6545 | 200 | 133.6545 | 66.3455 | 200 | 0 | 0 | 152600 | 200 | 392974.9352 | 341.7711 | 0
4185 | 6 | 1 | 0.67742 | 0.52001 | 216.9068 | 200 | 200 | 0 | 200 | 16.9068 | 0 | 152400 | 200 | 393174.9352 | 356.4259 | 0
4186 | 6 | 0 | 0.94197 | 0.55788 | 294.8593 | 0 | 0 | 0 | 0 | 178.1081 | 116.7512 | 152400 | 116.7512 | 393291.6864 | 510.81 | 0
4187 | 6 | 0 | 1 | 0.5856 | 312.7509 | 0 | 0 | 0 | 0 | 0 | 200 | 152400 | 200 | 393491.6864 | 510.81 | 112.7509
4188 | 6 | 0 | 1 | 0.39776 | 305.0682 | 0 | 0 | 0 | 0 | 0 | 200 | 152400 | 200 | 393691.6864 | 510.81 | 105.0682
4189 | 6 | 0 | 1 | 0.38209 | 304.4273 | 0 | 0 | 0 | 0 | 0 | 200 | 152400 | 200 | 393891.6864 | 510.81 | 104.4273
4190 | 6 | 0 | 1 | 0.24733 | 298.916 | 0 | 0 | 0 | 0 | 0 | 200 | 152400 | 200 | 394091.6864 | 510.81 | 98.916
4191 | 6 | 0 | 1 | 0.22795 | 298.1234 | 0 | 0 | 0 | 0 | 0 | 200 | 152400 | 200 | 394291.6864 | 510.81 | 98.1234
4192 | 6 | 0 | 0.94197 | 0.24312 | 281.9853 | 0 | 0 | 0 | 0 | 0 | 200 | 152400 | 200 | 394491.6864 | 510.81 | 81.9853
4193 | 6 | 0 | 0.67742 | 0.28995 | 207.4972 | 0 | 0 | 0 | 0 | 0 | 200 | 152400 | 200 | 394691.6864 | 510.81 | 7.4972
4194 | 6 | 0 | 0.39471 | 0.15057 | 120.1519 | 0 | 0 | 0 | 0 | 0 | 120.1519 | 152400 | 120.1519 | 394811.8383 | 510.81 | 0
4195 | 6 | 0 | 0.1363 | 0.10117 | 43.5007 | 0 | 0 | 0 | 0 | 0 | 43.5007 | 152400 | 43.5007 | 394855.339 | 510.81 | 0
4196 | 6 | 1 | 0 | 0.17835 | 7.2946 | 200 | 7.2946 | 180 | 187.2946 | 0 | 0 | 152200 | 187.2946 | 395042.6335 | 330.81 | 0
4197 | 6 | 1 | 0 | 0.20552 | 8.4056 | 200 | 8.4056 | 180 | 188.4056 | 0 | 0 | 152000 | 188.4056 | 395231.0392 | 150.81 | 0
4198 | 6 | 0 | 0 | 0.1791 | 7.3251 | 0 | 0 | 0 | 0 | 7.3251 | 0 | 152000 | 0 | 395231.0392 | 157.1594 | 0
4199 | 6 | 0 | 0 | 0.14235 | 5.822 | 0 | 0 | 0 | 0 | 5.822 | 0 | 152000 | 0 | 395231.0392 | 162.2059 | 0
4200 | 6 | 0 | 0 | 0.12759 | 5.2186 | 0 | 0 | 0 | 0 | 5.2186 | 0 | 152000 | 0 | 395231.0392 | 166.7294 | 0
4201 | 6 | 0 | 0 | 0.12788 | 5.2303 | 0 | 0 | 0 | 0 | 5.2303 | 0 | 152000 | 0 | 395231.0392 | 171.263 | 0
4202 | 6 | 0 | 0 | 0.18702 | 7.6493 | 0 | 0 | 0 | 0 | 7.6493 | 0 | 152000 | 0 | 395231.0392 | 177.8935 | 0
4203 | 6 | 0 | 0 | 0.24001 | 9.8163 | 0 | 0 | 0 | 0 | 9.8163 | 0 | 152000 | 0 | 395231.0392 | 186.4022 | 0
4204 | 6 | 0 | 0 | 0.1436 | 5.8732 | 0 | 0 | 0 | 0 | 5.8732 | 0 | 152000 | 0 | 395231.0392 | 191.4931 | 0
4205 | 6 | 0 | 0 | 0.14284 | 5.842 | 0 | 0 | 0 | 0 | 5.842 | 0 | 152000 | 0 | 395231.0392 | 196.557 | 0
4206 | 6 | 0 | 0 | 0.17121 | 7.0026 | 0 | 0 | 0 | 0 | 7.0026 | 0 | 152000 | 0 | 395231.0392 | 202.6268 | 0
4207 | 6 | 0 | 0.1385 | 0.1816 | 47.4262 | 0 | 0 | 0 | 0 | 47.4262 | 0 | 152000 | 0 | 395231.0392 | 243.7358 | 0
4208 | 6 | 1 | 0.40109 | 0.2352 | 125.455 | 200 | 125.455 | 74.545 | 200 | 0 | 0 | 151800 | 200 | 395431.0392 | 169.1909 | 0
4209 | 6 | 1 | 0.68836 | 0.29248 | 210.7616 | 200 | 200 | 0 | 200 | 10.7616 | 0 | 151600 | 200 | 395631.0392 | 178.519 | 0
4210 | 6 | 0 | 0.95719 | 0.29108 | 288.3422 | 0 | 0 | 0 | 0 | 180 | 108.3422 | 151600 | 108.3422 | 395739.3814 | 334.543 | 0
4211 | 6 | 0 | 1 | 0.28635 | 300.5116 | 0 | 0 | 0 | 0 | 180 | 120.5116 | 151600 | 120.5116 | 395859.893 | 490.567 | 0
4212 | 6 | 0 | 1 | 0.28565 | 300.483 | 0 | 0 | 0 | 0 | 23.3537 | 200 | 151600 | 200 | 396059.893 | 510.81 | 77.1294
4213 | 6 | 0 | 1 | 0.27042 | 299.8603 | 0 | 0 | 0 | 0 | 0 | 200 | 151600 | 200 | 396259.893 | 510.81 | 99.8603
4214 | 6 | 0 | 1 | 0.36997 | 303.9319 | 0 | 0 | 0 | 0 | 0 | 200 | 151600 | 200 | 396459.893 | 510.81 | 103.9319
4215 | 6 | 0 | 1 | 0.45613 | 307.4557 | 0 | 0 | 0 | 0 | 0 | 200 | 151600 | 200 | 396659.893 | 510.81 | 107.4557
4216 | 6 | 0 | 0.95719 | 0.41027 | 293.2171 | 0 | 0 | 0 | 0 | 0 | 200 | 151600 | 200 | 396859.893 | 510.81 | 93.2171
4217 | 6 | 0 | 0.68836 | 0.45317 | 217.3338 | 0 | 0 | 0 | 0 | 0 | 200 | 151600 | 200 | 397059.893 | 510.81 | 17.3338
4218 | 6 | 0 | 0.40109 | 0.56431 | 138.9155 | 0 | 0 | 0 | 0 | 0 | 138.9155 | 151600 | 138.9155 | 397198.8085 | 510.81 | 0
4219 | 6 | 0 | 0.1385 | 0.58931 | 64.1016 | 0 | 0 | 0 | 0 | 0 | 64.1016 | 151600 | 64.1016 | 397262.9101 | 510.81 | 0
4220 | 6 | 1 | 0 | 0.48851 | 19.9803 | 200 | 19.9803 | 180 | 199.9803 | 0 | 0 | 151400 | 199.9803 | 397462.8903 | 330.81 | 0
4221 | 6 | 1 | 0 | 0.65504 | 26.7912 | 200 | 26.7912 | 173.2088 | 200 | 0 | 0 | 151200 | 200 | 397662.8903 | 157.6012 | 0
4222 | 6 | 0 | 0 | 0.65729 | 26.883 | 0 | 0 | 0 | 0 | 26.883 | 0 | 151200 | 0 | 397662.8903 | 180.9034 | 0
4223 | 6 | 0 | 0 | 0.84009 | 34.3596 | 0 | 0 | 0 | 0 | 34.3596 | 0 | 151200 | 0 | 397662.8903 | 210.6862 | 0
4224 | 6 | 0 | 0 | 0.98616 | 40.3339 | 0 | 0 | 0 | 0 | 40.3339 | 0 | 151200 | 0 | 397662.8903 | 245.6477 | 0
4225 | 6 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 151200 | 0 | 397662.8903 | 281.0998 | 0
4226 | 6 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 151200 | 0 | 397662.8903 | 316.5519 | 0
4227 | 6 | 0 | 0 | 0.97306 | 39.7983 | 0 | 0 | 0 | 0 | 39.7983 | 0 | 151200 | 0 | 397662.8903 | 351.049 | 0
4228 | 6 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 151200 | 0 | 397662.8903 | 386.5012 | 0
4229 | 6 | 0 | 0 | 0.89096 | 36.4403 | 0 | 0 | 0 | 0 | 36.4403 | 0 | 151200 | 0 | 397662.8903 | 418.0876 | 0
4230 | 6 | 0 | 0 | 0.61906 | 25.3196 | 0 | 0 | 0 | 0 | 25.3196 | 0 | 151200 | 0 | 397662.8903 | 440.0347 | 0
4231 | 6 | 0 | 0.10612 | 0.39517 | 46.8083 | 0 | 0 | 0 | 0 | 46.8083 | 0 | 151200 | 0 | 397662.8903 | 480.6082 | 0
4232 | 6 | 1 | 0.30731 | 0.38991 | 104.6977 | 200 | 104.6977 | 95.3023 | 200 | 0 | 0 | 151000 | 200 | 397862.8903 | 385.3059 | 0
4233 | 6 | 1 | 0.52741 | 0.3762 | 167.7014 | 200 | 167.7014 | 32.2986 | 200 | 0 | 0 | 150800 | 200 | 398062.8903 | 353.0072 | 0
4234 | 6 | 0 | 0.73338 | 0.23619 | 221.4596 | 0 | 0 | 0 | 0 | 180 | 41.4596 | 150800 | 41.4596 | 398104.3499 | 509.0312 | 0
4235 | 6 | 0 | 0.89979 | 0.14722 | 265.8801 | 0 | 0 | 0 | 0 | 2.0521 | 200 | 150800 | 200 | 398304.3499 | 510.81 | 63.828
4236 | 6 | 0 | 1 | 0.15354 | 295.0797 | 0 | 0 | 0 | 0 | 0 | 200 | 150800 | 200 | 398504.3499 | 510.81 | 95.0797
4237 | 6 | 0 | 1 | 0.21427 | 297.5638 | 0 | 0 | 0 | 0 | 0 | 200 | 150800 | 200 | 398704.3499 | 510.81 | 97.5638
4238 | 6 | 0 | 1 | 0.20748 | 297.2861 | 0 | 0 | 0 | 0 | 0 | 200 | 150800 | 200 | 398904.3499 | 510.81 | 97.2861
4239 | 6 | 0 | 0.89979 | 0.24092 | 269.7123 | 0 | 0 | 0 | 0 | 0 | 200 | 150800 | 200 | 399104.3499 | 510.81 | 69.7123
4240 | 6 | 0 | 0.73338 | 0.24615 | 221.8669 | 0 | 0 | 0 | 0 | 0 | 200 | 150800 | 200 | 399304.3499 | 510.81 | 21.8669
4241 | 6 | 0 | 0.52741 | 0.41317 | 169.2136 | 0 | 0 | 0 | 0 | 0 | 169.2136 | 150800 | 169.2136 | 399473.5635 | 510.81 | 0
4242 | 6 | 0 | 0.30731 | 0.29219 | 100.701 | 0 | 0 | 0 | 0 | 0 | 100.701 | 150800 | 100.701 | 399574.2645 | 510.81 | 0
4243 | 6 | 0 | 0.10612 | 0.20783 | 39.1462 | 0 | 0 | 0 | 0 | 0 | 39.1462 | 150800 | 39.1462 | 399613.4107 | 510.81 | 0
4244 | 6 | 1 | 0 | 0.29892 | 12.2258 | 200 | 12.2258 | 180 | 192.2258 | 0 | 0 | 150600 | 192.2258 | 399805.6365 | 330.81 | 0
4245 | 6 | 1 | 0 | 0.23932 | 9.7884 | 200 | 9.7884 | 180 | 189.7884 | 0 | 0 | 150400 | 189.7884 | 399995.4249 | 150.81 | 0
4246 | 6 | 0 | 0 | 0.17855 | 7.3027 | 0 | 0 | 0 | 0 | 7.3027 | 0 | 150400 | 0 | 399995.4249 | 157.1399 | 0
4247 | 6 | 0 | 0 | 0.2088 | 8.54 | 0 | 0 | 0 | 0 | 8.54 | 0 | 150400 | 0 | 399995.4249 | 164.5424 | 0
4248 | 6 | 0 | 0 | 0.23281 | 9.5218 | 0 | 0 | 0 | 0 | 9.5218 | 0 | 150400 | 0 | 399995.4249 | 172.7959 | 0
4249 | 6 | 0 | 0 | 0.28306 | 11.5772 | 0 | 0 | 0 | 0 | 11.5772 | 0 | 150400 | 0 | 399995.4249 | 182.831 | 0
4250 | 6 | 0 | 0 | 0.29903 | 12.2304 | 0 | 0 | 0 | 0 | 12.2304 | 0 | 150400 | 0 | 399995.4249 | 193.4323 | 0
4251 | 6 | 0 | 0 | 0.29679 | 12.1388 | 0 | 0 | 0 | 0 | 12.1388 | 0 | 150400 | 0 | 399995.4249 | 203.9542 | 0
4252 | 6 | 0 | 0 | 0.25492 | 10.4261 | 0 | 0 | 0 | 0 | 10.4261 | 0 | 150400 | 0 | 399995.4249 | 212.9916 | 0
4253 | 6 | 0 | 0 | 0.22951 | 9.3869 | 0 | 0 | 0 | 0 | 9.3869 | 0 | 150400 | 0 | 399995.4249 | 221.1281 | 0
4254 | 6 | 0 | 0 | 0.2283 | 9.3373 | 0 | 0 | 0 | 0 | 9.3373 | 0 | 150400 | 0 | 399995.4249 | 229.2217 | 0
4255 | 6 | 0 | 0.094749 | 0.26946 | 38.3843 | 0 | 0 | 0 | 0 | 38.3843 | 0 | 150400 | 0 | 399995.4249 | 262.4932 | 0
4256 | 6 | 1 | 0.27439 | 0.39995 | 95.6018 | 200 | 95.6018 | 104.3982 | 200 | 0 | 0 | 150200 | 200 | 400195.4249 | 158.095 | 0
4257 | 6 | 1 | 0.47091 | 0.5764 | 159.5748 | 200 | 159.5748 | 40.4252 | 200 | 0 | 0 | 150000 | 200 | 400395.4249 | 117.6698 | 0
4258 | 6 | 0 | 0.65482 | 0.48712 | 209.0362 | 0 | 0 | 0 | 0 | 180 | 29.0362 | 150000 | 29.0362 | 400424.4611 | 273.6938 | 0
4259 | 6 | 0 | 0.80341 | 0.49697 | 252.3506 | 0 | 0 | 0 | 0 | 180 | 72.3506 | 150000 | 72.3506 | 400496.8117 | 429.7178 | 0
4260 | 6 | 0 | 0.89967 | 0.45856 | 278.5808 | 0 | 0 | 0 | 0 | 93.5536 | 185.0272 | 150000 | 185.0272 | 400681.8389 | 510.81 | 0
4261 | 6 | 0 | 0.93297 | 0.31099 | 282.1619 | 0 | 0 | 0 | 0 | 0 | 200 | 150000 | 200 | 400881.8389 | 510.81 | 82.1619
4262 | 6 | 0 | 0.89967 | 0.45959 | 278.623 | 0 | 0 | 0 | 0 | 0 | 200 | 150000 | 200 | 401081.8389 | 510.81 | 78.623
4263 | 6 | 0 | 0.80341 | 0.60061 | 256.5895 | 0 | 0 | 0 | 0 | 0 | 200 | 150000 | 200 | 401281.8389 | 510.81 | 56.5895
4264 | 6 | 0 | 0.65482 | 0.6121 | 214.1479 | 0 | 0 | 0 | 0 | 0 | 200 | 150000 | 200 | 401481.8389 | 510.81 | 14.1479
4265 | 6 | 0 | 0.47091 | 0.45012 | 154.4101 | 0 | 0 | 0 | 0 | 0 | 154.4101 | 150000 | 154.4101 | 401636.249 | 510.81 | 0
4266 | 6 | 0 | 0.27439 | 0.30333 | 91.6499 | 0 | 0 | 0 | 0 | 0 | 91.6499 | 150000 | 91.6499 | 401727.8989 | 510.81 | 0
4267 | 6 | 0 | 0.094749 | 0.28346 | 38.957 | 0 | 0 | 0 | 0 | 0 | 38.957 | 150000 | 38.957 | 401766.8559 | 510.81 | 0
4268 | 6 | 1 | 0 | 0.57763 | 23.625 | 200 | 23.625 | 176.375 | 200 | 0 | 0 | 149800 | 200 | 401966.8559 | 334.435 | 0
4269 | 6 | 1 | 0 | 0.74543 | 30.488 | 200 | 30.488 | 169.512 | 200 | 0 | 0 | 149600 | 200 | 402166.8559 | 164.923 | 0
4270 | 6 | 0 | 0 | 0.50249 | 20.5519 | 0 | 0 | 0 | 0 | 20.5519 | 0 | 149600 | 0 | 402166.8559 | 182.7374 | 0
4271 | 6 | 0 | 0 | 0.40157 | 16.4243 | 0 | 0 | 0 | 0 | 16.4243 | 0 | 149600 | 0 | 402166.8559 | 196.974 | 0
4272 | 6 | 0 | 0 | 0.27059 | 11.0673 | 0 | 0 | 0 | 0 | 11.0673 | 0 | 149600 | 0 | 402166.8559 | 206.5671 | 0
4273 | 6 | 0 | 0 | 0.23927 | 9.786 | 0 | 0 | 0 | 0 | 9.786 | 0 | 149600 | 0 | 402166.8559 | 215.0496 | 0
4274 | 6 | 0 | 0 | 0.21739 | 8.8914 | 0 | 0 | 0 | 0 | 8.8914 | 0 | 149600 | 0 | 402166.8559 | 222.7567 | 0
4275 | 6 | 0 | 0 | 0.16534 | 6.7626 | 0 | 0 | 0 | 0 | 6.7626 | 0 | 149600 | 0 | 402166.8559 | 228.6185 | 0
4276 | 6 | 0 | 0 | 0.20532 | 8.3976 | 0 | 0 | 0 | 0 | 8.3976 | 0 | 149600 | 0 | 402166.8559 | 235.8976 | 0
4277 | 6 | 0 | 0 | 0.31193 | 12.7579 | 0 | 0 | 0 | 0 | 12.7579 | 0 | 149600 | 0 | 402166.8559 | 246.9562 | 0
4278 | 6 | 0 | 0 | 0.34221 | 13.9964 | 0 | 0 | 0 | 0 | 13.9964 | 0 | 149600 | 0 | 402166.8559 | 259.0882 | 0
4279 | 6 | 0 | 0.12961 | 0.37365 | 52.7149 | 0 | 0 | 0 | 0 | 52.7149 | 0 | 149600 | 0 | 402166.8559 | 304.7815 | 0
4280 | 6 | 1 | 0.37536 | 0.48788 | 128.3584 | 200 | 128.3584 | 71.6416 | 200 | 0 | 0 | 149400 | 200 | 402366.8559 | 233.1399 | 0
4281 | 6 | 1 | 0.6442 | 0.49887 | 206.4489 | 200 | 200 | 0 | 200 | 6.4489 | 0 | 149200 | 200 | 402566.8559 | 238.7298 | 0
4282 | 6 | 0 | 0.89578 | 0.55843 | 281.542 | 0 | 0 | 0 | 0 | 180 | 101.542 | 149200 | 101.542 | 402668.3979 | 394.7538 | 0
4283 | 6 | 0 | 1 | 0.74232 | 319.161 | 0 | 0 | 0 | 0 | 133.8904 | 185.2706 | 149200 | 185.2706 | 402853.6685 | 510.81 | 0
4284 | 6 | 0 | 1 | 0.65225 | 315.4771 | 0 | 0 | 0 | 0 | 0 | 200 | 149200 | 200 | 403053.6685 | 510.81 | 115.4771
4285 | 6 | 0 | 1 | 0.61573 | 313.9834 | 0 | 0 | 0 | 0 | 0 | 200 | 149200 | 200 | 403253.6685 | 510.81 | 113.9834
4286 | 6 | 0 | 1 | 0.76126 | 319.9354 | 0 | 0 | 0 | 0 | 0 | 200 | 149200 | 200 | 403453.6685 | 510.81 | 119.9354
4287 | 6 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 0 | 200 | 149200 | 200 | 403653.6685 | 510.81 | 129.7
4288 | 6 | 0 | 0.89578 | 0.95147 | 297.6174 | 0 | 0 | 0 | 0 | 0 | 200 | 149200 | 200 | 403853.6685 | 510.81 | 97.6174
4289 | 6 | 0 | 0.6442 | 0.65281 | 212.7448 | 0 | 0 | 0 | 0 | 0 | 200 | 149200 | 200 | 404053.6685 | 510.81 | 12.7448
4290 | 6 | 0 | 0.37536 | 0.43448 | 126.1743 | 0 | 0 | 0 | 0 | 0 | 126.1743 | 149200 | 126.1743 | 404179.8429 | 510.81 | 0
4291 | 6 | 0 | 0.12961 | 0.66606 | 64.6745 | 0 | 0 | 0 | 0 | 0 | 64.6745 | 149200 | 64.6745 | 404244.5173 | 510.81 | 0
4292 | 6 | 1 | 0 | 0.552 | 22.5768 | 200 | 22.5768 | 177.4232 | 200 | 0 | 0 | 149000 | 200 | 404444.5173 | 333.3868 | 0
4293 | 6 | 1 | 0 | 0.47815 | 19.5564 | 200 | 19.5564 | 180 | 199.5564 | 0 | 0 | 148800 | 199.5564 | 404644.0737 | 153.3868 | 0
4294 | 6 | 0 | 0 | 0.48144 | 19.6907 | 0 | 0 | 0 | 0 | 19.6907 | 0 | 148800 | 0 | 404644.0737 | 170.4548 | 0
4295 | 6 | 0 | 0 | 0.55963 | 22.8887 | 0 | 0 | 0 | 0 | 22.8887 | 0 | 148800 | 0 | 404644.0737 | 190.2947 | 0
4296 | 6 | 0 | 0 | 0.49023 | 20.0506 | 0 | 0 | 0 | 0 | 20.0506 | 0 | 148800 | 0 | 404644.0737 | 207.6746 | 0
4297 | 6 | 0 | 0 | 0.43684 | 17.8669 | 0 | 0 | 0 | 0 | 17.8669 | 0 | 148800 | 0 | 404644.0737 | 223.1616 | 0
4298 | 6 | 0 | 0 | 0.40351 | 16.5036 | 0 | 0 | 0 | 0 | 16.5036 | 0 | 148800 | 0 | 404644.0737 | 237.467 | 0
4299 | 6 | 0 | 0 | 0.41018 | 16.7763 | 0 | 0 | 0 | 0 | 16.7763 | 0 | 148800 | 0 | 404644.0737 | 252.0087 | 0
4300 | 6 | 0 | 0 | 0.53959 | 22.0692 | 0 | 0 | 0 | 0 | 22.0692 | 0 | 148800 | 0 | 404644.0737 | 271.1383 | 0
4301 | 6 | 0 | 0 | 0.49777 | 20.3586 | 0 | 0 | 0 | 0 | 20.3586 | 0 | 148800 | 0 | 404644.0737 | 288.7851 | 0
4302 | 6 | 0 | 0 | 0.4987 | 20.3967 | 0 | 0 | 0 | 0 | 20.3967 | 0 | 148800 | 0 | 404644.0737 | 306.465 | 0
4303 | 6 | 0 | 0.091621 | 0.58263 | 50.2897 | 0 | 0 | 0 | 0 | 50.2897 | 0 | 148800 | 0 | 404644.0737 | 350.0561 | 0
4304 | 6 | 1 | 0.26533 | 0.42702 | 94.0929 | 200 | 94.0929 | 105.9071 | 200 | 0 | 0 | 148600 | 200 | 404844.0737 | 244.149 | 0
4305 | 6 | 1 | 0.45537 | 0.53743 | 153.4906 | 200 | 153.4906 | 46.5094 | 200 | 0 | 0 | 148400 | 200 | 405044.0737 | 197.6396 | 0
4306 | 6 | 0 | 0.6332 | 0.53829 | 204.8851 | 0 | 0 | 0 | 0 | 180 | 24.8851 | 148400 | 24.8851 | 405068.9588 | 353.6636 | 0
4307 | 6 | 0 | 0.77688 | 0.43894 | 242.3165 | 0 | 0 | 0 | 0 | 180 | 62.3165 | 148400 | 62.3165 | 405131.2753 | 509.6876 | 0
4308 | 6 | 0 | 0.86997 | 0.23964 | 261.0482 | 0 | 0 | 0 | 0 | 1.2949 | 200 | 148400 | 200 | 405331.2753 | 510.81 | 59.7534
4309 | 6 | 0 | 0.90217 | 0.22853 | 269.8931 | 0 | 0 | 0 | 0 | 0 | 200 | 148400 | 200 | 405531.2753 | 510.81 | 69.8931
4310 | 6 | 0 | 0.86997 | 0.23 | 260.6541 | 0 | 0 | 0 | 0 | 0 | 200 | 148400 | 200 | 405731.2753 | 510.81 | 60.6541
4311 | 6 | 0 | 0.77688 | 0.23313 | 233.899 | 0 | 0 | 0 | 0 | 0 | 200 | 148400 | 200 | 405931.2753 | 510.81 | 33.899
4312 | 6 | 0 | 0.6332 | 0.24044 | 192.7029 | 0 | 0 | 0 | 0 | 0 | 192.7029 | 148400 | 192.7029 | 406123.9781 | 510.81 | 0
4313 | 6 | 0 | 0.45537 | 0.20272 | 139.8009 | 0 | 0 | 0 | 0 | 0 | 139.8009 | 148400 | 139.8009 | 406263.779 | 510.81 | 0
4314 | 6 | 0 | 0.26533 | 0.26079 | 87.294 | 0 | 0 | 0 | 0 | 0 | 87.294 | 148400 | 87.294 | 406351.073 | 510.81 | 0
4315 | 6 | 0 | 0.091621 | 0.31883 | 39.5005 | 0 | 0 | 0 | 0 | 0 | 39.5005 | 148400 | 39.5005 | 406390.5735 | 510.81 | 0
4316 | 6 | 1 | 0 | 0.36129 | 14.7766 | 200 | 14.7766 | 180 | 194.7766 | 0 | 0 | 148200 | 194.7766 | 406585.3501 | 330.81 | 0
4317 | 6 | 1 | 0 | 0.40046 | 16.3787 | 200 | 16.3787 | 180 | 196.3787 | 0 | 0 | 148000 | 196.3787 | 406781.7287 | 150.81 | 0
4318 | 6 | 0 | 0 | 0.38432 | 15.7186 | 0 | 0 | 0 | 0 | 15.7186 | 0 | 148000 | 0 | 406781.7287 | 164.4349 | 0
4319 | 6 | 0 | 0 | 0.37562 | 15.363 | 0 | 0 | 0 | 0 | 15.363 | 0 | 148000 | 0 | 406781.7287 | 177.7516 | 0
4320 | 6 | 0 | 0 | 0.50849 | 20.7974 | 0 | 0 | 0 | 0 | 20.7974 | 0 | 148000 | 0 | 406781.7287 | 195.7787 | 0
4321 | 6 | 0 | 0 | 0.46984 | 19.2164 | 0 | 0 | 0 | 0 | 19.2164 | 0 | 148000 | 0 | 406781.7287 | 212.4355 | 0
4322 | 6 | 0 | 0 | 0.41995 | 17.1759 | 0 | 0 | 0 | 0 | 17.1759 | 0 | 148000 | 0 | 406781.7287 | 227.3236 | 0
4323 | 6 | 0 | 0 | 0.43393 | 17.7477 | 0 | 0 | 0 | 0 | 17.7477 | 0 | 148000 | 0 | 406781.7287 | 242.7072 | 0
4324 | 6 | 0 | 0 | 0.29149 | 11.922 | 0 | 0 | 0 | 0 | 11.922 | 0 | 148000 | 0 | 406781.7287 | 253.0412 | 0
4325 | 6 | 0 | 0 | 0.22933 | 9.3797 | 0 | 0 | 0 | 0 | 9.3797 | 0 | 148000 | 0 | 406781.7287 | 261.1716 | 0
4326 | 6 | 0 | 0 | 0.23697 | 9.6921 | 0 | 0 | 0 | 0 | 9.6921 | 0 | 148000 | 0 | 406781.7287 | 269.5727 | 0
4327 | 6 | 0 | 0.10303 | 0.30496 | 42.2285 | 0 | 0 | 0 | 0 | 42.2285 | 0 | 148000 | 0 | 406781.7287 | 306.1763 | 0
4328 | 6 | 1 | 0.29838 | 0.3296 | 99.6523 | 200 | 99.6523 | 100.3477 | 200 | 0 | 0 | 147800 | 200 | 406981.7287 | 205.8286 | 0
4329 | 6 | 1 | 0.51208 | 0.41528 | 164.8746 | 200 | 164.8746 | 35.1254 | 200 | 0 | 0 | 147600 | 200 | 407181.7287 | 170.7032 | 0
4330 | 6 | 0 | 0.71207 | 0.41728 | 222.7124 | 0 | 0 | 0 | 0 | 180 | 42.7124 | 147600 | 42.7124 | 407224.4412 | 326.7272 | 0
4331 | 6 | 0 | 0.87365 | 0.42818 | 269.8217 | 0 | 0 | 0 | 0 | 180 | 89.8217 | 147600 | 89.8217 | 407314.2629 | 482.7512 | 0
4332 | 6 | 0 | 0.97833 | 0.375 | 297.8778 | 0 | 0 | 0 | 0 | 32.3705 | 200 | 147600 | 200 | 407514.2629 | 510.81 | 65.5073
4333 | 6 | 0 | 1 | 0.33691 | 302.5797 | 0 | 0 | 0 | 0 | 0 | 200 | 147600 | 200 | 407714.2629 | 510.81 | 102.5797
4334 | 6 | 0 | 0.97833 | 0.45327 | 301.0795 | 0 | 0 | 0 | 0 | 0 | 200 | 147600 | 200 | 407914.2629 | 510.81 | 101.0795
4335 | 6 | 0 | 0.87365 | 0.43727 | 270.1933 | 0 | 0 | 0 | 0 | 0 | 200 | 147600 | 200 | 408114.2629 | 510.81 | 70.1933
4336 | 6 | 0 | 0.71207 | 0.59195 | 229.8564 | 0 | 0 | 0 | 0 | 0 | 200 | 147600 | 200 | 408314.2629 | 510.81 | 29.8564
4337 | 6 | 0 | 0.51208 | 0.39083 | 163.8745 | 0 | 0 | 0 | 0 | 0 | 163.8745 | 147600 | 163.8745 | 408478.1374 | 510.81 | 0
4338 | 6 | 0 | 0.29838 | 0.50445 | 106.8034 | 0 | 0 | 0 | 0 | 0 | 106.8034 | 147600 | 106.8034 | 408584.9408 | 510.81 | 0
4339 | 6 | 0 | 0.10303 | 0.46299 | 48.6921 | 0 | 0 | 0 | 0 | 0 | 48.6921 | 147600 | 48.6921 | 408633.6329 | 510.81 | 0
4340 | 6 | 1 | 0 | 0.35472 | 14.508 | 200 | 14.508 | 180 | 194.508 | 0 | 0 | 147400 | 194.508 | 408828.1409 | 330.81 | 0
4341 | 6 | 1 | 0 | 0.34235 | 14.0019 | 200 | 14.0019 | 180 | 194.0019 | 0 | 0 | 147200 | 194.0019 | 409022.1428 | 150.81 | 0
4342 | 6 | 0 | 0 | 0.30698 | 12.5555 | 0 | 0 | 0 | 0 | 12.5555 | 0 | 147200 | 0 | 409022.1428 | 161.6931 | 0
4343 | 6 | 0 | 0 | 0.32777 | 13.406 | 0 | 0 | 0 | 0 | 13.406 | 0 | 147200 | 0 | 409022.1428 | 173.3134 | 0
4344 | 6 | 0 | 0 | 0.3034 | 12.4089 | 0 | 0 | 0 | 0 | 12.4089 | 0 | 147200 | 0 | 409022.1428 | 184.0694 | 0
4345 | 7 | 0 | 0 | 0.24816 | 10.1498 | 0 | 0 | 0 | 0 | 10.1498 | 0 | 147200 | 0 | 409022.1428 | 192.8673 | 0
4346 | 7 | 0 | 0 | 0.55954 | 22.8853 | 0 | 0 | 0 | 0 | 22.8853 | 0 | 147200 | 0 | 409022.1428 | 212.7043 | 0
4347 | 7 | 0 | 0 | 0.41303 | 16.8931 | 0 | 0 | 0 | 0 | 16.8931 | 0 | 147200 | 0 | 409022.1428 | 227.3472 | 0
4348 | 7 | 0 | 0 | 0.61837 | 25.2913 | 0 | 0 | 0 | 0 | 25.2913 | 0 | 147200 | 0 | 409022.1428 | 249.2697 | 0
4349 | 7 | 0 | 0 | 0.61809 | 25.2798 | 0 | 0 | 0 | 0 | 25.2798 | 0 | 147200 | 0 | 409022.1428 | 271.1822 | 0
4350 | 7 | 0 | 0 | 0.51921 | 21.2356 | 0 | 0 | 0 | 0 | 21.2356 | 0 | 147200 | 0 | 409022.1428 | 289.5892 | 0
4351 | 7 | 0 | 0.090864 | 0.5455 | 48.5525 | 0 | 0 | 0 | 0 | 48.5525 | 0 | 147200 | 0 | 409022.1428 | 331.6745 | 0
4352 | 7 | 1 | 0.29218 | 0.4271 | 101.8491 | 200 | 101.8491 | 98.1509 | 200 | 0 | 0 | 147000 | 200 | 409222.1428 | 233.5237 | 0
4353 | 7 | 1 | 0.51617 | 0.46224 | 167.9761 | 200 | 167.9761 | 32.0239 | 200 | 0 | 0 | 146800 | 200 | 409422.1428 | 201.4998 | 0
4354 | 7 | 0 | 0.72736 | 0.52166 | 231.3979 | 0 | 0 | 0 | 0 | 180 | 51.3979 | 146800 | 51.3979 | 409473.5406 | 357.5238 | 0
4355 | 7 | 0 | 0.89871 | 0.52235 | 280.9128 | 0 | 0 | 0 | 0 | 176.8415 | 104.0714 | 146800 | 104.0714 | 409577.612 | 510.81 | 0
4356 | 7 | 0 | 1 | 0.85925 | 323.9433 | 0 | 0 | 0 | 0 | 0 | 200 | 146800 | 200 | 409777.612 | 510.81 | 123.9433
4357 | 7 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 0 | 200 | 146800 | 200 | 409977.612 | 510.81 | 129.7
4358 | 7 | 0 | 1 | 0.86054 | 323.9962 | 0 | 0 | 0 | 0 | 0 | 200 | 146800 | 200 | 410177.612 | 510.81 | 123.9962
4359 | 7 | 0 | 0.89871 | 0.77294 | 291.162 | 0 | 0 | 0 | 0 | 0 | 200 | 146800 | 200 | 410377.612 | 510.81 | 91.162
4360 | 7 | 0 | 0.72736 | 1 | 250.9619 | 0 | 0 | 0 | 0 | 0 | 200 | 146800 | 200 | 410577.612 | 510.81 | 50.9619
4361 | 7 | 0 | 0.51617 | 1 | 189.9705 | 0 | 0 | 0 | 0 | 0 | 189.9705 | 146800 | 189.9705 | 410767.5825 | 510.81 | 0
4362 | 7 | 0 | 0.29218 | 0.72394 | 113.9897 | 0 | 0 | 0 | 0 | 0 | 113.9897 | 146800 | 113.9897 | 410881.5722 | 510.81 | 0
4363 | 7 | 0 | 0.090864 | 0.37476 | 41.5692 | 0 | 0 | 0 | 0 | 0 | 41.5692 | 146800 | 41.5692 | 410923.1414 | 510.81 | 0
4364 | 7 | 1 | 0 | 0.45118 | 18.4532 | 200 | 18.4532 | 180 | 198.4532 | 0 | 0 | 146600 | 198.4532 | 411121.5946 | 330.81 | 0
4365 | 7 | 1 | 0 | 0.39297 | 16.0726 | 200 | 16.0726 | 180 | 196.0726 | 0 | 0 | 146400 | 196.0726 | 411317.6672 | 150.81 | 0
4366 | 7 | 0 | 0 | 0.45848 | 18.7519 | 0 | 0 | 0 | 0 | 18.7519 | 0 | 146400 | 0 | 411317.6672 | 167.0642 | 0
4367 | 7 | 0 | 0 | 0.56626 | 23.16 | 0 | 0 | 0 | 0 | 23.16 | 0 | 146400 | 0 | 411317.6672 | 187.1393 | 0
4368 | 7 | 0 | 0 | 0.83055 | 33.9693 | 0 | 0 | 0 | 0 | 33.9693 | 0 | 146400 | 0 | 411317.6672 | 216.5839 | 0
4369 | 7 | 0 | 0 | 0.62925 | 25.7362 | 0 | 0 | 0 | 0 | 25.7362 | 0 | 146400 | 0 | 411317.6672 | 238.8921 | 0
4370 | 7 | 0 | 0 | 0.56772 | 23.2198 | 0 | 0 | 0 | 0 | 23.2198 | 0 | 146400 | 0 | 411317.6672 | 259.019 | 0
4371 | 7 | 0 | 0 | 0.61702 | 25.236 | 0 | 0 | 0 | 0 | 25.236 | 0 | 146400 | 0 | 411317.6672 | 280.8936 | 0
4372 | 7 | 0 | 0 | 0.60645 | 24.8037 | 0 | 0 | 0 | 0 | 24.8037 | 0 | 146400 | 0 | 411317.6672 | 302.3934 | 0
4373 | 7 | 0 | 0 | 0.68412 | 27.9806 | 0 | 0 | 0 | 0 | 27.9806 | 0 | 146400 | 0 | 411317.6672 | 326.647 | 0
4374 | 7 | 0 | 0 | 0.80032 | 32.7331 | 0 | 0 | 0 | 0 | 32.7331 | 0 | 146400 | 0 | 411317.6672 | 355.0201 | 0
4375 | 7 | 0 | 0.079412 | 0.60041 | 47.491 | 0 | 0 | 0 | 0 | 47.491 | 0 | 146400 | 0 | 411317.6672 | 396.1853 | 0
4376 | 7 | 1 | 0.25535 | 1 | 114.6457 | 200 | 114.6457 | 85.3543 | 200 | 0 | 0 | 146200 | 200 | 411517.6672 | 310.831 | 0
4377 | 7 | 1 | 0.45112 | 0.83111 | 164.2748 | 200 | 164.2748 | 35.7252 | 200 | 0 | 0 | 146000 | 200 | 411717.6672 | 275.1058 | 0
4378 | 7 | 0 | 0.63569 | 0.97109 | 223.3046 | 0 | 0 | 0 | 0 | 180 | 43.3046 | 146000 | 43.3046 | 411760.9718 | 431.1298 | 0
4379 | 7 | 0 | 0.78544 | 0.96207 | 266.1853 | 0 | 0 | 0 | 0 | 91.9245 | 174.2607 | 146000 | 174.2607 | 411935.2325 | 510.81 | 0
4380 | 7 | 0 | 0.8827 | 0.57918 | 278.6139 | 0 | 0 | 0 | 0 | 0 | 200 | 146000 | 200 | 412135.2325 | 510.81 | 78.6139
4381 | 7 | 0 | 0.91639 | 0.45855 | 283.4071 | 0 | 0 | 0 | 0 | 0 | 200 | 146000 | 200 | 412335.2325 | 510.81 | 83.4071
4382 | 7 | 0 | 0.8827 | 0.47506 | 274.3551 | 0 | 0 | 0 | 0 | 0 | 200 | 146000 | 200 | 412535.2325 | 510.81 | 74.3551
4383 | 7 | 0 | 0.78544 | 0.54357 | 249.0684 | 0 | 0 | 0 | 0 | 0 | 200 | 146000 | 200 | 412735.2325 | 510.81 | 49.0684
4384 | 7 | 0 | 0.63569 | 0.70028 | 212.2284 | 0 | 0 | 0 | 0 | 0 | 200 | 146000 | 200 | 412935.2325 | 510.81 | 12.2284
4385 | 7 | 0 | 0.45112 | 0.55027 | 152.7886 | 0 | 0 | 0 | 0 | 0 | 152.7886 | 146000 | 152.7886 | 413088.021 | 510.81 | 0
4386 | 7 | 0 | 0.25535 | 0.59805 | 98.2061 | 0 | 0 | 0 | 0 | 0 | 98.2061 | 146000 | 98.2061 | 413186.2271 | 510.81 | 0
4387 | 7 | 0 | 0.079412 | 0.51503 | 43.999 | 0 | 0 | 0 | 0 | 0 | 43.999 | 146000 | 43.999 | 413230.2261 | 510.81 | 0
4388 | 7 | 1 | 0 | 0.71488 | 29.2384 | 200 | 29.2384 | 170.7616 | 200 | 0 | 0 | 145800 | 200 | 413430.2261 | 340.0484 | 0
4389 | 7 | 1 | 0 | 1 | 40.9 | 200 | 40.9 | 159.1 | 200 | 0 | 0 | 145600 | 200 | 413630.2261 | 180.9484 | 0
4390 | 7 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 145600 | 0 | 413630.2261 | 216.4005 | 0
4391 | 7 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 145600 | 0 | 413630.2261 | 251.8527 | 0
4392 | 7 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 145600 | 0 | 413630.2261 | 287.3048 | 0
4393 | 7 | 0 | 0 | 0.71994 | 29.4457 | 0 | 0 | 0 | 0 | 29.4457 | 0 | 145600 | 0 | 413630.2261 | 312.8283 | 0
4394 | 7 | 0 | 0 | 0.8425 | 34.4585 | 0 | 0 | 0 | 0 | 34.4585 | 0 | 145600 | 0 | 413630.2261 | 342.6969 | 0
4395 | 7 | 0 | 0 | 0.58196 | 23.802 | 0 | 0 | 0 | 0 | 23.802 | 0 | 145600 | 0 | 413630.2261 | 363.3285 | 0
4396 | 7 | 0 | 0 | 0.49525 | 20.2556 | 0 | 0 | 0 | 0 | 20.2556 | 0 | 145600 | 0 | 413630.2261 | 380.886 | 0
4397 | 7 | 0 | 0 | 0.54873 | 22.443 | 0 | 0 | 0 | 0 | 22.443 | 0 | 145600 | 0 | 413630.2261 | 400.3396 | 0
4398 | 7 | 0 | 0 | 0.57516 | 23.5241 | 0 | 0 | 0 | 0 | 23.5241 | 0 | 145600 | 0 | 413630.2261 | 420.7303 | 0
4399 | 7 | 0 | 0.08655 | 0.62141 | 50.4115 | 0 | 0 | 0 | 0 | 50.4115 | 0 | 145600 | 0 | 413630.2261 | 464.427 | 0
4400 | 7 | 1 | 0.2783 | 0.72834 | 110.1631 | 200 | 110.1631 | 89.8369 | 200 | 0 | 0 | 145400 | 200 | 413830.2261 | 374.5901 | 0
4401 | 7 | 1 | 0.49166 | 0.71689 | 171.3125 | 200 | 171.3125 | 28.6875 | 200 | 0 | 0 | 145200 | 200 | 414030.2261 | 345.9026 | 0
4402 | 7 | 0 | 0.69282 | 0.81084 | 233.2503 | 0 | 0 | 0 | 0 | 180 | 53.2503 | 145200 | 53.2503 | 414083.4765 | 501.9266 | 0
4403 | 7 | 0 | 0.85604 | 0.99015 | 287.7207 | 0 | 0 | 0 | 0 | 10.2486 | 200 | 145200 | 200 | 414283.4765 | 510.81 | 77.4721
4404 | 7 | 0 | 0.96204 | 0.7981 | 310.4792 | 0 | 0 | 0 | 0 | 0 | 200 | 145200 | 200 | 414483.4765 | 510.81 | 110.4792
4405 | 7 | 0 | 0.99875 | 0.93528 | 326.6909 | 0 | 0 | 0 | 0 | 0 | 200 | 145200 | 200 | 414683.4765 | 510.81 | 126.6909
4406 | 7 | 0 | 0.96204 | 0.49658 | 298.1468 | 0 | 0 | 0 | 0 | 0 | 200 | 145200 | 200 | 414883.4765 | 510.81 | 98.1468
4407 | 7 | 0 | 0.85604 | 0.28293 | 258.7954 | 0 | 0 | 0 | 0 | 0 | 200 | 145200 | 200 | 415083.4765 | 510.81 | 58.7954
4408 | 7 | 0 | 0.69282 | 0.31154 | 212.8289 | 0 | 0 | 0 | 0 | 0 | 200 | 145200 | 200 | 415283.4765 | 510.81 | 12.8289
4409 | 7 | 0 | 0.49166 | 0.3165 | 154.9368 | 0 | 0 | 0 | 0 | 0 | 154.9368 | 145200 | 154.9368 | 415438.4132 | 510.81 | 0
4410 | 7 | 0 | 0.2783 | 0.33234 | 93.9665 | 0 | 0 | 0 | 0 | 0 | 93.9665 | 145200 | 93.9665 | 415532.3798 | 510.81 | 0
4411 | 7 | 0 | 0.08655 | 0.41789 | 42.0874 | 0 | 0 | 0 | 0 | 0 | 42.0874 | 145200 | 42.0874 | 415574.4672 | 510.81 | 0
4412 | 7 | 1 | 0 | 0.4766 | 19.4929 | 200 | 19.4929 | 180 | 199.4929 | 0 | 0 | 145000 | 199.4929 | 415773.9601 | 330.81 | 0
4413 | 7 | 1 | 0 | 0.30958 | 12.662 | 200 | 12.662 | 180 | 192.662 | 0 | 0 | 144800 | 192.662 | 415966.6221 | 150.81 | 0
4414 | 7 | 0 | 0 | 0.35362 | 14.463 | 0 | 0 | 0 | 0 | 14.463 | 0 | 144800 | 0 | 415966.6221 | 163.3465 | 0
4415 | 7 | 0 | 0 | 0.24843 | 10.1607 | 0 | 0 | 0 | 0 | 10.1607 | 0 | 144800 | 0 | 415966.6221 | 172.1538 | 0
4416 | 7 | 0 | 0 | 0.33856 | 13.847 | 0 | 0 | 0 | 0 | 13.847 | 0 | 144800 | 0 | 415966.6221 | 184.1564 | 0
4417 | 7 | 0 | 0 | 0.39281 | 16.0657 | 0 | 0 | 0 | 0 | 16.0657 | 0 | 144800 | 0 | 415966.6221 | 198.0822 | 0
4418 | 7 | 0 | 0 | 0.43326 | 17.7203 | 0 | 0 | 0 | 0 | 17.7203 | 0 | 144800 | 0 | 415966.6221 | 213.4421 | 0
4419 | 7 | 0 | 0 | 0.39738 | 16.2527 | 0 | 0 | 0 | 0 | 16.2527 | 0 | 144800 | 0 | 415966.6221 | 227.53 | 0
4420 | 7 | 0 | 0 | 0.36979 | 15.1246 | 0 | 0 | 0 | 0 | 15.1246 | 0 | 144800 | 0 | 415966.6221 | 240.64 | 0
4421 | 7 | 0 | 0 | 0.49584 | 20.28 | 0 | 0 | 0 | 0 | 20.28 | 0 | 144800 | 0 | 415966.6221 | 258.2187 | 0
4422 | 7 | 0 | 0 | 0.43194 | 17.6662 | 0 | 0 | 0 | 0 | 17.6662 | 0 | 144800 | 0 | 415966.6221 | 273.5318 | 0
4423 | 7 | 0 | 0.060595 | 0.44788 | 35.8179 | 0 | 0 | 0 | 0 | 35.8179 | 0 | 144800 | 0 | 415966.6221 | 304.5787 | 0
4424 | 7 | 1 | 0.19485 | 0.49348 | 76.4549 | 200 | 76.4549 | 123.5451 | 200 | 0 | 0 | 144600 | 200 | 416166.6221 | 181.0336 | 0
4425 | 7 | 1 | 0.34422 | 0.35844 | 114.0716 | 200 | 114.0716 | 85.9284 | 200 | 0 | 0 | 144400 | 200 | 416366.6221 | 95.1052 | 0
4426 | 7 | 0 | 0.48506 | 0.37473 | 155.4117 | 0 | 0 | 0 | 0 | 155.4117 | 0 | 144400 | 0 | 416366.6221 | 229.8161 | 0
4427 | 7 | 0 | 0.59933 | 0.27925 | 184.508 | 0 | 0 | 0 | 0 | 180 | 4.508 | 144400 | 4.508 | 416371.1301 | 385.8401 | 0
4428 | 7 | 0 | 0.67354 | 0.31265 | 207.3071 | 0 | 0 | 0 | 0 | 144.1739 | 63.1332 | 144400 | 63.1332 | 416434.2633 | 510.81 | 0
4429 | 7 | 0 | 0.69925 | 0.26358 | 212.7225 | 0 | 0 | 0 | 0 | 0 | 200 | 144400 | 200 | 416634.2633 | 510.81 | 12.7225
4430 | 7 | 0 | 0.67354 | 0.54511 | 216.8148 | 0 | 0 | 0 | 0 | 0 | 200 | 144400 | 200 | 416834.2633 | 510.81 | 16.8148
4431 | 7 | 0 | 0.59933 | 0.60191 | 197.705 | 0 | 0 | 0 | 0 | 0 | 197.705 | 144400 | 197.705 | 417031.9683 | 510.81 | 0
4432 | 7 | 0 | 0.48506 | 0.71165 | 169.1918 | 0 | 0 | 0 | 0 | 0 | 169.1918 | 144400 | 169.1918 | 417201.1601 | 510.81 | 0
4433 | 7 | 0 | 0.34422 | 0.50814 | 120.1947 | 0 | 0 | 0 | 0 | 0 | 120.1947 | 144400 | 120.1947 | 417321.3547 | 510.81 | 0
4434 | 7 | 0 | 0.19485 | 0.61029 | 81.2323 | 0 | 0 | 0 | 0 | 0 | 81.2323 | 144400 | 81.2323 | 417402.587 | 510.81 | 0
4435 | 7 | 0 | 0.060595 | 0.39267 | 33.5599 | 0 | 0 | 0 | 0 | 0 | 33.5599 | 144400 | 33.5599 | 417436.1469 | 510.81 | 0
4436 | 7 | 1 | 0 | 0.33483 | 13.6948 | 200 | 13.6948 | 180 | 193.6948 | 0 | 0 | 144200 | 193.6948 | 417629.8417 | 330.81 | 0
4437 | 7 | 1 | 0 | 0.43817 | 17.9209 | 200 | 17.9209 | 180 | 197.9209 | 0 | 0 | 144000 | 197.9209 | 417827.7626 | 150.81 | 0
4438 | 7 | 0 | 0 | 0.44176 | 18.0679 | 0 | 0 | 0 | 0 | 18.0679 | 0 | 144000 | 0 | 417827.7626 | 166.4712 | 0
4439 | 7 | 0 | 0 | 0.35358 | 14.4615 | 0 | 0 | 0 | 0 | 14.4615 | 0 | 144000 | 0 | 417827.7626 | 179.0065 | 0
4440 | 7 | 0 | 0 | 0.34072 | 13.9353 | 0 | 0 | 0 | 0 | 13.9353 | 0 | 144000 | 0 | 417827.7626 | 191.0856 | 0
4441 | 7 | 0 | 0 | 0.29507 | 12.0682 | 0 | 0 | 0 | 0 | 12.0682 | 0 | 144000 | 0 | 417827.7626 | 201.5463 | 0
4442 | 7 | 0 | 0 | 0.33325 | 13.6297 | 0 | 0 | 0 | 0 | 13.6297 | 0 | 144000 | 0 | 417827.7626 | 213.3606 | 0
4443 | 7 | 0 | 0 | 0.43434 | 17.7647 | 0 | 0 | 0 | 0 | 17.7647 | 0 | 144000 | 0 | 417827.7626 | 228.759 | 0
4444 | 7 | 0 | 0 | 0.25541 | 10.4462 | 0 | 0 | 0 | 0 | 10.4462 | 0 | 144000 | 0 | 417827.7626 | 237.8138 | 0
4445 | 7 | 0 | 0 | 0.28972 | 11.8495 | 0 | 0 | 0 | 0 | 11.8495 | 0 | 144000 | 0 | 417827.7626 | 248.0849 | 0
4446 | 7 | 0 | 0 | 0.14027 | 5.737 | 0 | 0 | 0 | 0 | 5.737 | 0 | 144000 | 0 | 417827.7626 | 253.0577 | 0
4447 | 7 | 0 | 0.084776 | 0.18141 | 31.9029 | 0 | 0 | 0 | 0 | 31.9029 | 0 | 144000 | 0 | 417827.7626 | 280.7111 | 0
4448 | 7 | 1 | 0.2726 | 0.3138 | 91.5608 | 200 | 91.5608 | 108.4392 | 200 | 0 | 0 | 143800 | 200 | 418027.7626 | 172.2719 | 0
4449 | 7 | 1 | 0.48158 | 0.2201 | 148.0838 | 200 | 148.0838 | 51.9162 | 200 | 0 | 0 | 143600 | 200 | 418227.7626 | 120.3557 | 0
4450 | 7 | 0 | 0.67862 | 0.30172 | 208.3262 | 0 | 0 | 0 | 0 | 180 | 28.3262 | 143600 | 28.3262 | 418256.0888 | 276.3797 | 0
4451 | 7 | 0 | 0.83849 | 0.24798 | 252.2991 | 0 | 0 | 0 | 0 | 180 | 72.2991 | 143600 | 72.2991 | 418328.3879 | 432.4037 | 0
4452 | 7 | 0 | 0.94232 | 0.28081 | 283.6274 | 0 | 0 | 0 | 0 | 90.4549 | 193.1725 | 143600 | 193.1725 | 418521.5604 | 510.81 | 0
4453 | 7 | 0 | 0.97828 | 0.27507 | 293.7766 | 0 | 0 | 0 | 0 | 0 | 200 | 143600 | 200 | 418721.5604 | 510.81 | 93.7766
4454 | 7 | 0 | 0.94232 | 0.29603 | 284.25 | 0 | 0 | 0 | 0 | 0 | 200 | 143600 | 200 | 418921.5604 | 510.81 | 84.25
4455 | 7 | 0 | 0.83849 | 0.29647 | 254.2824 | 0 | 0 | 0 | 0 | 0 | 200 | 143600 | 200 | 419121.5604 | 510.81 | 54.2824
4456 | 7 | 0 | 0.67862 | 0.31965 | 209.0599 | 0 | 0 | 0 | 0 | 0 | 200 | 143600 | 200 | 419321.5604 | 510.81 | 9.0599
4457 | 7 | 0 | 0.48158 | 0.33919 | 152.9542 | 0 | 0 | 0 | 0 | 0 | 152.9542 | 143600 | 152.9542 | 419474.5146 | 510.81 | 0
4458 | 7 | 0 | 0.2726 | 0.33469 | 92.4149 | 0 | 0 | 0 | 0 | 0 | 92.4149 | 143600 | 92.4149 | 419566.9295 | 510.81 | 0
4459 | 7 | 0 | 0.084776 | 0.44878 | 42.8382 | 0 | 0 | 0 | 0 | 0 | 42.8382 | 143600 | 42.8382 | 419609.7678 | 510.81 | 0
4460 | 7 | 1 | 0 | 0.33608 | 13.7456 | 200 | 13.7456 | 180 | 193.7456 | 0 | 0 | 143400 | 193.7456 | 419803.5134 | 330.81 | 0
4461 | 7 | 1 | 0 | 0.73574 | 30.0916 | 200 | 30.0916 | 169.9084 | 200 | 0 | 0 | 143200 | 200 | 420003.5134 | 160.9016 | 0
4462 | 7 | 0 | 0 | 0.5077 | 20.7648 | 0 | 0 | 0 | 0 | 20.7648 | 0 | 143200 | 0 | 420003.5134 | 178.9005 | 0
4463 | 7 | 0 | 0 | 0.38598 | 15.7866 | 0 | 0 | 0 | 0 | 15.7866 | 0 | 143200 | 0 | 420003.5134 | 192.5844 | 0
4464 | 7 | 0 | 0 | 0.39944 | 16.3372 | 0 | 0 | 0 | 0 | 16.3372 | 0 | 143200 | 0 | 420003.5134 | 206.7455 | 0
4465 | 7 | 0 | 0 | 0.43252 | 17.6903 | 0 | 0 | 0 | 0 | 17.6903 | 0 | 143200 | 0 | 420003.5134 | 222.0794 | 0
4466 | 7 | 0 | 0 | 0.59329 | 24.2655 | 0 | 0 | 0 | 0 | 24.2655 | 0 | 143200 | 0 | 420003.5134 | 243.1127 | 0
4467 | 7 | 0 | 0 | 0.61738 | 25.2508 | 0 | 0 | 0 | 0 | 25.2508 | 0 | 143200 | 0 | 420003.5134 | 265.0001 | 0
4468 | 7 | 0 | 0 | 0.55699 | 22.7809 | 0 | 0 | 0 | 0 | 22.7809 | 0 | 143200 | 0 | 420003.5134 | 284.7466 | 0
4469 | 7 | 0 | 0 | 0.47887 | 19.5857 | 0 | 0 | 0 | 0 | 19.5857 | 0 | 143200 | 0 | 420003.5134 | 301.7235 | 0
4470 | 7 | 0 | 0 | 0.32027 | 13.0991 | 0 | 0 | 0 | 0 | 13.0991 | 0 | 143200 | 0 | 420003.5134 | 313.0778 | 0
4471 | 7 | 0 | 0.09019 | 0.23177 | 35.5261 | 0 | 0 | 0 | 0 | 35.5261 | 0 | 143200 | 0 | 420003.5134 | 343.8718 | 0
4472 | 7 | 1 | 0.29001 | 0.34486 | 97.8589 | 200 | 97.8589 | 102.1411 | 200 | 0 | 0 | 143000 | 200 | 420203.5134 | 241.7307 | 0
4473 | 7 | 1 | 0.51234 | 0.30817 | 160.5678 | 200 | 160.5678 | 39.4322 | 200 | 0 | 0 | 142800 | 200 | 420403.5134 | 202.2986 | 0
4474 | 7 | 0 | 0.72196 | 0.46713 | 227.6077 | 0 | 0 | 0 | 0 | 180 | 47.6077 | 142800 | 47.6077 | 420451.1212 | 358.3226 | 0
4475 | 7 | 0 | 0.89204 | 0.42321 | 274.9308 | 0 | 0 | 0 | 0 | 175.92 | 99.0108 | 142800 | 99.0108 | 420550.132 | 510.81 | 0
4476 | 7 | 0 | 1 | 0.29477 | 300.8559 | 0 | 0 | 0 | 0 | 0 | 200 | 142800 | 200 | 420750.132 | 510.81 | 100.8559
4477 | 7 | 0 | 1 | 0.40906 | 305.5305 | 0 | 0 | 0 | 0 | 0 | 200 | 142800 | 200 | 420950.132 | 510.81 | 105.5305
4478 | 7 | 0 | 1 | 0.35033 | 303.1285 | 0 | 0 | 0 | 0 | 0 | 200 | 142800 | 200 | 421150.132 | 510.81 | 103.1285
4479 | 7 | 0 | 0.89204 | 0.39024 | 273.5824 | 0 | 0 | 0 | 0 | 0 | 200 | 142800 | 200 | 421350.132 | 510.81 | 73.5824
4480 | 7 | 0 | 0.72196 | 0.32548 | 221.8144 | 0 | 0 | 0 | 0 | 0 | 200 | 142800 | 200 | 421550.132 | 510.81 | 21.8144
4481 | 7 | 0 | 0.51234 | 0.27481 | 159.2032 | 0 | 0 | 0 | 0 | 0 | 159.2032 | 142800 | 159.2032 | 421709.3351 | 510.81 | 0
4482 | 7 | 0 | 0.29001 | 0.24051 | 93.5909 | 0 | 0 | 0 | 0 | 0 | 93.5909 | 142800 | 93.5909 | 421802.926 | 510.81 | 0
4483 | 7 | 0 | 0.09019 | 0.37877 | 41.5385 | 0 | 0 | 0 | 0 | 0 | 41.5385 | 142800 | 41.5385 | 421844.4645 | 510.81 | 0
4484 | 7 | 1 | 0 | 0.48841 | 19.9762 | 200 | 19.9762 | 180 | 199.9762 | 0 | 0 | 142600 | 199.9762 | 422044.4406 | 330.81 | 0
4485 | 7 | 1 | 0 | 0.31031 | 12.6918 | 200 | 12.6918 | 180 | 192.6918 | 0 | 0 | 142400 | 192.6918 | 422237.1324 | 150.81 | 0
4486 | 7 | 0 | 0 | 0.47096 | 19.2624 | 0 | 0 | 0 | 0 | 19.2624 | 0 | 142400 | 0 | 422237.1324 | 167.5066 | 0
4487 | 7 | 0 | 0 | 0.40126 | 16.4115 | 0 | 0 | 0 | 0 | 16.4115 | 0 | 142400 | 0 | 422237.1324 | 181.7322 | 0
4488 | 7 | 0 | 0 | 0.4054 | 16.5807 | 0 | 0 | 0 | 0 | 16.5807 | 0 | 142400 | 0 | 422237.1324 | 196.1043 | 0
4489 | 7 | 0 | 0 | 0.44366 | 18.1457 | 0 | 0 | 0 | 0 | 18.1457 | 0 | 142400 | 0 | 422237.1324 | 211.833 | 0
4490 | 7 | 0 | 0 | 0.46298 | 18.9357 | 0 | 0 | 0 | 0 | 18.9357 | 0 | 142400 | 0 | 422237.1324 | 228.2464 | 0
4491 | 7 | 0 | 0 | 0.59879 | 24.4903 | 0 | 0 | 0 | 0 | 24.4903 | 0 | 142400 | 0 | 422237.1324 | 249.4746 | 0
4492 | 7 | 0 | 0 | 0.45813 | 18.7375 | 0 | 0 | 0 | 0 | 18.7375 | 0 | 142400 | 0 | 422237.1324 | 265.7163 | 0
4493 | 7 | 0 | 0 | 0.34594 | 14.1489 | 0 | 0 | 0 | 0 | 14.1489 | 0 | 142400 | 0 | 422237.1324 | 277.9805 | 0
4494 | 7 | 0 | 0 | 0.3543 | 14.4909 | 0 | 0 | 0 | 0 | 14.4909 | 0 | 142400 | 0 | 422237.1324 | 290.5412 | 0
4495 | 7 | 0 | 0.078194 | 0.33252 | 36.1824 | 0 | 0 | 0 | 0 | 36.1824 | 0 | 142400 | 0 | 422237.1324 | 321.9041 | 0
4496 | 7 | 1 | 0.25143 | 0.34194 | 86.5994 | 200 | 86.5994 | 113.4006 | 200 | 0 | 0 | 142200 | 200 | 422437.1324 | 208.5036 | 0
4497 | 7 | 1 | 0.44419 | 0.45388 | 146.8469 | 200 | 146.8469 | 53.1531 | 200 | 0 | 0 | 142000 | 200 | 422637.1324 | 155.3504 | 0
4498 | 7 | 0 | 0.62593 | 0.42704 | 198.2358 | 0 | 0 | 0 | 0 | 180 | 18.2358 | 142000 | 18.2358 | 422655.3682 | 311.3744 | 0
4499 | 7 | 0 | 0.77339 | 0.36405 | 238.2451 | 0 | 0 | 0 | 0 | 180 | 58.2451 | 142000 | 58.2451 | 422713.6133 | 467.3984 | 0
4500 | 7 | 0 | 0.86916 | 0.5174 | 272.1751 | 0 | 0 | 0 | 0 | 50.0826 | 200 | 142000 | 200 | 422913.6133 | 510.81 | 22.0926
4501 | 7 | 0 | 0.90232 | 0.7794 | 292.4686 | 0 | 0 | 0 | 0 | 0 | 200 | 142000 | 200 | 423113.6133 | 510.81 | 92.4686
4502 | 7 | 0 | 0.86916 | 0.97236 | 290.7828 | 0 | 0 | 0 | 0 | 0 | 200 | 142000 | 200 | 423313.6133 | 510.81 | 90.7828
4503 | 7 | 0 | 0.77339 | 1 | 264.2556 | 0 | 0 | 0 | 0 | 0 | 200 | 142000 | 200 | 423513.6133 | 510.81 | 64.2556
4504 | 7 | 0 | 0.62593 | 0.98642 | 221.1142 | 0 | 0 | 0 | 0 | 0 | 200 | 142000 | 200 | 423713.6133 | 510.81 | 21.1142
4505 | 7 | 0 | 0.44419 | 0.74708 | 158.8388 | 0 | 0 | 0 | 0 | 0 | 158.8388 | 142000 | 158.8388 | 423872.4521 | 510.81 | 0
4506 | 7 | 0 | 0.25143 | 0.9215 | 110.3036 | 0 | 0 | 0 | 0 | 0 | 110.3036 | 142000 | 110.3036 | 423982.7557 | 510.81 | 0
4507 | 7 | 0 | 0.078194 | 1 | 63.4824 | 0 | 0 | 0 | 0 | 0 | 63.4824 | 142000 | 63.4824 | 424046.2381 | 510.81 | 0
4508 | 7 | 1 | 0 | 1 | 40.9 | 200 | 40.9 | 159.1 | 200 | 0 | 0 | 141800 | 200 | 424246.2381 | 351.71 | 0
4509 | 7 | 1 | 0 | 1 | 40.9 | 200 | 40.9 | 159.1 | 200 | 0 | 0 | 141600 | 200 | 424446.2381 | 192.61 | 0
4510 | 7 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 141600 | 0 | 424446.2381 | 228.0621 | 0
4511 | 7 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 141600 | 0 | 424446.2381 | 263.5142 | 0
4512 | 7 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 141600 | 0 | 424446.2381 | 298.9664 | 0
4513 | 7 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 141600 | 0 | 424446.2381 | 334.4185 | 0
4514 | 7 | 0 | 0 | 0.92504 | 37.834 | 0 | 0 | 0 | 0 | 37.834 | 0 | 141600 | 0 | 424446.2381 | 367.213 | 0
4515 | 7 | 0 | 0 | 0.69621 | 28.475 | 0 | 0 | 0 | 0 | 28.475 | 0 | 141600 | 0 | 424446.2381 | 391.8951 | 0
4516 | 7 | 0 | 0 | 0.70658 | 28.8993 | 0 | 0 | 0 | 0 | 28.8993 | 0 | 141600 | 0 | 424446.2381 | 416.945 | 0
4517 | 7 | 0 | 0 | 0.62501 | 25.5629 | 0 | 0 | 0 | 0 | 25.5629 | 0 | 141600 | 0 | 424446.2381 | 439.1029 | 0
4518 | 7 | 0 | 0 | 0.75204 | 30.7586 | 0 | 0 | 0 | 0 | 30.7586 | 0 | 141600 | 0 | 424446.2381 | 465.7645 | 0
4519 | 7 | 0 | 0.079391 | 0.85384 | 57.85 | 0 | 0 | 0 | 0 | 51.9676 | 5.8824 | 141600 | 5.8824 | 424452.1205 | 510.81 | 0
4520 | 7 | 1 | 0.25528 | 0.61244 | 98.7753 | 200 | 98.7753 | 101.2247 | 200 | 0 | 0 | 141400 | 200 | 424652.1205 | 409.5853 | 0
4521 | 7 | 1 | 0.451 | 0.68727 | 158.3575 | 200 | 158.3575 | 41.6425 | 200 | 0 | 0 | 141200 | 200 | 424852.1205 | 367.9428 | 0
4522 | 7 | 0 | 0.63552 | 0.63116 | 209.3532 | 0 | 0 | 0 | 0 | 164.8214 | 44.5318 | 141200 | 44.5318 | 424896.6523 | 510.81 | 0
4523 | 7 | 0 | 0.78524 | 0.70504 | 255.6132 | 0 | 0 | 0 | 0 | 0 | 200 | 141200 | 200 | 425096.6523 | 510.81 | 55.6132
4524 | 7 | 0 | 0.88247 | 0.50214 | 275.3957 | 0 | 0 | 0 | 0 | 0 | 200 | 141200 | 200 | 425296.6523 | 510.81 | 75.3957
4525 | 7 | 0 | 0.91614 | 0.5852 | 288.5175 | 0 | 0 | 0 | 0 | 0 | 200 | 141200 | 200 | 425496.6523 | 510.81 | 88.5175
4526 | 7 | 0 | 0.88247 | 0.71539 | 284.1176 | 0 | 0 | 0 | 0 | 0 | 200 | 141200 | 200 | 425696.6523 | 510.81 | 84.1176
4527 | 7 | 0 | 0.78524 | 0.61043 | 251.7435 | 0 | 0 | 0 | 0 | 0 | 200 | 141200 | 200 | 425896.6523 | 510.81 | 51.7435
4528 | 7 | 0 | 0.63552 | 0.92412 | 221.3353 | 0 | 0 | 0 | 0 | 0 | 200 | 141200 | 200 | 426096.6523 | 510.81 | 21.3353
4529 | 7 | 0 | 0.451 | 0.9978 | 171.0581 | 0 | 0 | 0 | 0 | 0 | 171.0581 | 141200 | 171.0581 | 426267.7103 | 510.81 | 0
4530 | 7 | 0 | 0.25528 | 0.55535 | 96.4402 | 0 | 0 | 0 | 0 | 0 | 96.4402 | 141200 | 96.4402 | 426364.1506 | 510.81 | 0
4531 | 7 | 0 | 0.079391 | 0.40542 | 39.5099 | 0 | 0 | 0 | 0 | 0 | 39.5099 | 141200 | 39.5099 | 426403.6605 | 510.81 | 0
4532 | 7 | 1 | 0 | 0.56037 | 22.9191 | 200 | 22.9191 | 177.0809 | 200 | 0 | 0 | 141000 | 200 | 426603.6605 | 333.7291 | 0
4533 | 7 | 1 | 0 | 0.48015 | 19.6382 | 200 | 19.6382 | 180 | 199.6382 | 0 | 0 | 140800 | 199.6382 | 426803.2986 | 153.7291 | 0
4534 | 7 | 0 | 0 | 0.49996 | 20.4482 | 0 | 0 | 0 | 0 | 20.4482 | 0 | 140800 | 0 | 426803.2986 | 171.4536 | 0
4535 | 7 | 0 | 0 | 0.45345 | 18.5463 | 0 | 0 | 0 | 0 | 18.5463 | 0 | 140800 | 0 | 426803.2986 | 187.5295 | 0
4536 | 7 | 0 | 0 | 0.36225 | 14.8159 | 0 | 0 | 0 | 0 | 14.8159 | 0 | 140800 | 0 | 426803.2986 | 200.372 | 0
4537 | 7 | 0 | 0 | 0.39829 | 16.2899 | 0 | 0 | 0 | 0 | 16.2899 | 0 | 140800 | 0 | 426803.2986 | 214.4921 | 0
4538 | 7 | 0 | 0 | 0.46987 | 19.2177 | 0 | 0 | 0 | 0 | 19.2177 | 0 | 140800 | 0 | 426803.2986 | 231.15 | 0
4539 | 7 | 0 | 0 | 0.60325 | 24.6728 | 0 | 0 | 0 | 0 | 24.6728 | 0 | 140800 | 0 | 426803.2986 | 252.5364 | 0
4540 | 7 | 0 | 0 | 0.54632 | 22.3443 | 0 | 0 | 0 | 0 | 22.3443 | 0 | 140800 | 0 | 426803.2986 | 271.9045 | 0
4541 | 7 | 0 | 0 | 0.70964 | 29.0242 | 0 | 0 | 0 | 0 | 29.0242 | 0 | 140800 | 0 | 426803.2986 | 297.0627 | 0
4542 | 7 | 0 | 0 | 0.5465 | 22.352 | 0 | 0 | 0 | 0 | 22.352 | 0 | 140800 | 0 | 426803.2986 | 316.4374 | 0
4543 | 7 | 0 | 0.069602 | 0.46716 | 39.2079 | 0 | 0 | 0 | 0 | 39.2079 | 0 | 140800 | 0 | 426803.2986 | 350.4228 | 0
4544 | 7 | 1 | 0.22381 | 0.57137 | 88.0046 | 200 | 88.0046 | 111.9954 | 200 | 0 | 0 | 140600 | 200 | 427003.2986 | 238.4274 | 0
4545 | 7 | 1 | 0.39539 | 0.43375 | 131.9287 | 200 | 131.9287 | 68.0713 | 200 | 0 | 0 | 140400 | 200 | 427203.2986 | 170.3562 | 0
4546 | 7 | 0 | 0.55716 | 0.48616 | 180.792 | 0 | 0 | 0 | 0 | 180 | 0.79196 | 140400 | 0.79196 | 427204.0906 | 326.3802 | 0
4547 | 7 | 0 | 0.68842 | 0.489 | 218.8148 | 0 | 0 | 0 | 0 | 180 | 38.8148 | 140400 | 38.8148 | 427242.9055 | 482.4042 | 0
4548 | 7 | 0 | 0.77366 | 0.52367 | 244.8517 | 0 | 0 | 0 | 0 | 32.7709 | 200 | 140400 | 200 | 427442.9055 | 510.81 | 12.0808
4549 | 7 | 0 | 0.80318 | 0.54663 | 254.3163 | 0 | 0 | 0 | 0 | 0 | 200 | 140400 | 200 | 427642.9055 | 510.81 | 54.3163
4550 | 7 | 0 | 0.77366 | 0.45579 | 242.0752 | 0 | 0 | 0 | 0 | 0 | 200 | 140400 | 200 | 427842.9055 | 510.81 | 42.0752
4551 | 7 | 0 | 0.68842 | 0.44221 | 216.9011 | 0 | 0 | 0 | 0 | 0 | 200 | 140400 | 200 | 428042.9055 | 510.81 | 16.9011
4552 | 7 | 0 | 0.55716 | 0.45699 | 179.5991 | 0 | 0 | 0 | 0 | 0 | 179.5991 | 140400 | 179.5991 | 428222.5046 | 510.81 | 0
4553 | 7 | 0 | 0.39539 | 0.39342 | 130.2791 | 0 | 0 | 0 | 0 | 0 | 130.2791 | 140400 | 130.2791 | 428352.7837 | 510.81 | 0
4554 | 7 | 0 | 0.22381 | 0.42212 | 81.9003 | 0 | 0 | 0 | 0 | 0 | 81.9003 | 140400 | 81.9003 | 428434.6839 | 510.81 | 0
4555 | 7 | 0 | 0.069602 | 0.32873 | 33.546 | 0 | 0 | 0 | 0 | 0 | 33.546 | 140400 | 33.546 | 428468.2299 | 510.81 | 0
4556 | 7 | 1 | 0 | 0.47028 | 19.2345 | 200 | 19.2345 | 180 | 199.2345 | 0 | 0 | 140200 | 199.2345 | 428667.4644 | 330.81 | 0
4557 | 7 | 1 | 0 | 0.35508 | 14.5229 | 200 | 14.5229 | 180 | 194.5229 | 0 | 0 | 140000 | 194.5229 | 428861.9873 | 150.81 | 0
4558 | 7 | 0 | 0 | 0.28501 | 11.6568 | 0 | 0 | 0 | 0 | 11.6568 | 0 | 140000 | 0 | 428861.9873 | 160.9141 | 0
4559 | 7 | 0 | 0 | 0.30255 | 12.3744 | 0 | 0 | 0 | 0 | 12.3744 | 0 | 140000 | 0 | 428861.9873 | 171.6402 | 0
4560 | 7 | 0 | 0 | 0.29181 | 11.9352 | 0 | 0 | 0 | 0 | 11.9352 | 0 | 140000 | 0 | 428861.9873 | 181.9857 | 0
4561 | 7 | 0 | 0 | 0.3224 | 13.1863 | 0 | 0 | 0 | 0 | 13.1863 | 0 | 140000 | 0 | 428861.9873 | 193.4156 | 0
4562 | 7 | 0 | 0 | 0.37493 | 15.3346 | 0 | 0 | 0 | 0 | 15.3346 | 0 | 140000 | 0 | 428861.9873 | 206.7076 | 0
4563 | 7 | 0 | 0 | 0.30758 | 12.5799 | 0 | 0 | 0 | 0 | 12.5799 | 0 | 140000 | 0 | 428861.9873 | 217.6119 | 0
4564 | 7 | 0 | 0 | 0.35054 | 14.3371 | 0 | 0 | 0 | 0 | 14.3371 | 0 | 140000 | 0 | 428861.9873 | 230.0393 | 0
4565 | 7 | 0 | 0 | 0.39815 | 16.2845 | 0 | 0 | 0 | 0 | 16.2845 | 0 | 140000 | 0 | 428861.9873 | 244.1547 | 0
4566 | 7 | 0 | 0 | 0.30741 | 12.5732 | 0 | 0 | 0 | 0 | 12.5732 | 0 | 140000 | 0 | 428861.9873 | 255.0531 | 0
4567 | 7 | 0 | 0.088652 | 0.30993 | 38.2788 | 0 | 0 | 0 | 0 | 38.2788 | 0 | 140000 | 0 | 428861.9873 | 288.2332 | 0
4568 | 7 | 1 | 0.28506 | 0.21426 | 91.0891 | 200 | 91.0891 | 108.9109 | 200 | 0 | 0 | 139800 | 200 | 429061.9873 | 179.3223 | 0
4569 | 7 | 1 | 0.5036 | 0.24346 | 155.3985 | 200 | 155.3985 | 44.6015 | 200 | 0 | 0 | 139600 | 200 | 429261.9873 | 134.7208 | 0
4570 | 7 | 0 | 0.70965 | 0.26867 | 215.9357 | 0 | 0 | 0 | 0 | 180 | 35.9357 | 139600 | 35.9357 | 429297.923 | 290.7448 | 0
4571 | 7 | 0 | 0.87683 | 0.21824 | 262.155 | 0 | 0 | 0 | 0 | 180 | 82.155 | 139600 | 82.155 | 429380.078 | 446.7688 | 0
4572 | 7 | 0 | 0.98541 | 0.4187 | 301.7105 | 0 | 0 | 0 | 0 | 73.8824 | 200 | 139600 | 200 | 429580.078 | 510.81 | 27.8282
4573 | 7 | 0 | 1 | 0.52046 | 310.0869 | 0 | 0 | 0 | 0 | 0 | 200 | 139600 | 200 | 429780.078 | 510.81 | 110.0869
4574 | 7 | 0 | 0.98541 | 0.40405 | 301.1113 | 0 | 0 | 0 | 0 | 0 | 200 | 139600 | 200 | 429980.078 | 510.81 | 101.1113
4575 | 7 | 0 | 0.87683 | 0.35777 | 267.8617 | 0 | 0 | 0 | 0 | 0 | 200 | 139600 | 200 | 430180.078 | 510.81 | 67.8617
4576 | 7 | 0 | 0.70965 | 0.27033 | 216.0035 | 0 | 0 | 0 | 0 | 0 | 200 | 139600 | 200 | 430380.078 | 510.81 | 16.0035
4577 | 7 | 0 | 0.5036 | 0.32146 | 158.5885 | 0 | 0 | 0 | 0 | 0 | 158.5885 | 139600 | 158.5885 | 430538.6665 | 510.81 | 0
4578 | 7 | 0 | 0.28506 | 0.22369 | 91.4749 | 0 | 0 | 0 | 0 | 0 | 91.4749 | 139600 | 91.4749 | 430630.1414 | 510.81 | 0
4579 | 7 | 0 | 0.088652 | 0.18743 | 33.2686 | 0 | 0 | 0 | 0 | 0 | 33.2686 | 139600 | 33.2686 | 430663.41 | 510.81 | 0
4580 | 7 | 1 | 0 | 0.11757 | 4.8087 | 200 | 4.8087 | 180 | 184.8087 | 0 | 0 | 139400 | 184.8087 | 430848.2187 | 330.81 | 0
4581 | 7 | 1 | 0 | 0.065437 | 2.6764 | 200 | 2.6764 | 180 | 182.6764 | 0 | 0 | 139200 | 182.6764 | 431030.8951 | 150.81 | 0
4582 | 7 | 0 | 0 | 0.060251 | 2.4643 | 0 | 0 | 0 | 0 | 2.4643 | 0 | 139200 | 0 | 431030.8951 | 152.946 | 0
4583 | 7 | 0 | 0 | 0.059213 | 2.4218 | 0 | 0 | 0 | 0 | 2.4218 | 0 | 139200 | 0 | 431030.8951 | 155.0453 | 0
4584 | 7 | 0 | 0 | 0.060676 | 2.4816 | 0 | 0 | 0 | 0 | 2.4816 | 0 | 139200 | 0 | 431030.8951 | 157.1963 | 0
4585 | 7 | 0 | 0 | 0.074749 | 3.0572 | 0 | 0 | 0 | 0 | 3.0572 | 0 | 139200 | 0 | 431030.8951 | 159.8464 | 0
4586 | 7 | 0 | 0 | 0.065094 | 2.6623 | 0 | 0 | 0 | 0 | 2.6623 | 0 | 139200 | 0 | 431030.8951 | 162.1541 | 0
4587 | 7 | 0 | 0 | 0.10242 | 4.189 | 0 | 0 | 0 | 0 | 4.189 | 0 | 139200 | 0 | 431030.8951 | 165.7851 | 0
4588 | 7 | 0 | 0 | 0.16822 | 6.88 | 0 | 0 | 0 | 0 | 6.88 | 0 | 139200 | 0 | 431030.8951 | 171.7487 | 0
4589 | 7 | 0 | 0 | 0.20011 | 8.1844 | 0 | 0 | 0 | 0 | 8.1844 | 0 | 139200 | 0 | 431030.8951 | 178.8429 | 0
4590 | 7 | 0 | 0 | 0.17777 | 7.2707 | 0 | 0 | 0 | 0 | 7.2707 | 0 | 139200 | 0 | 431030.8951 | 185.1452 | 0
4591 | 7 | 0 | 0.088116 | 0.36012 | 40.1766 | 0 | 0 | 0 | 0 | 40.1766 | 0 | 139200 | 0 | 431030.8951 | 219.9703 | 0
4592 | 7 | 1 | 0.28334 | 0.36459 | 96.7408 | 200 | 96.7408 | 103.2592 | 200 | 0 | 0 | 139000 | 200 | 431230.8951 | 116.7111 | 0
4593 | 7 | 1 | 0.50056 | 0.47825 | 164.1227 | 200 | 164.1227 | 35.8773 | 200 | 0 | 0 | 138800 | 200 | 431430.8951 | 80.8338 | 0
4594 | 7 | 0 | 0.70536 | 0.49049 | 223.7701 | 0 | 0 | 0 | 0 | 180 | 43.7701 | 138800 | 43.7701 | 431474.6652 | 236.8578 | 0
4595 | 7 | 0 | 0.87153 | 0.32009 | 264.7912 | 0 | 0 | 0 | 0 | 180 | 84.7912 | 138800 | 84.7912 | 431559.4563 | 392.8818 | 0
4596 | 7 | 0 | 0.97945 | 0.44192 | 300.941 | 0 | 0 | 0 | 0 | 136.0501 | 164.8909 | 138800 | 164.8909 | 431724.3473 | 510.81 | 0
4597 | 7 | 0 | 1 | 0.3134 | 301.618 | 0 | 0 | 0 | 0 | 0 | 200 | 138800 | 200 | 431924.3473 | 510.81 | 101.618
4598 | 7 | 0 | 0.97945 | 0.5677 | 306.0855 | 0 | 0 | 0 | 0 | 0 | 200 | 138800 | 200 | 432124.3473 | 510.81 | 106.0855
4599 | 7 | 0 | 0.87153 | 0.52697 | 273.2523 | 0 | 0 | 0 | 0 | 0 | 200 | 138800 | 200 | 432324.3473 | 510.81 | 73.2523
4600 | 7 | 0 | 0.70536 | 0.61215 | 228.7462 | 0 | 0 | 0 | 0 | 0 | 200 | 138800 | 200 | 432524.3473 | 510.81 | 28.7462
4601 | 7 | 0 | 0.50056 | 0.82096 | 178.1395 | 0 | 0 | 0 | 0 | 0 | 178.1395 | 138800 | 178.1395 | 432702.4868 | 510.81 | 0
4602 | 7 | 0 | 0.28334 | 0.86238 | 117.1 | 0 | 0 | 0 | 0 | 0 | 117.1 | 138800 | 117.1 | 432819.5868 | 510.81 | 0
4603 | 7 | 0 | 0.088116 | 0.71015 | 54.4932 | 0 | 0 | 0 | 0 | 0 | 54.4932 | 138800 | 54.4932 | 432874.08 | 510.81 | 0
4604 | 7 | 1 | 0 | 1 | 40.9 | 200 | 40.9 | 159.1 | 200 | 0 | 0 | 138600 | 200 | 433074.08 | 351.71 | 0
4605 | 7 | 1 | 0 | 0.87819 | 35.9182 | 200 | 35.9182 | 164.0818 | 200 | 0 | 0 | 138400 | 200 | 433274.08 | 187.6282 | 0
4606 | 7 | 0 | 0 | 0.51688 | 21.1405 | 0 | 0 | 0 | 0 | 21.1405 | 0 | 138400 | 0 | 433274.08 | 205.9527 | 0
4607 | 7 | 0 | 0 | 0.37075 | 15.1638 | 0 | 0 | 0 | 0 | 15.1638 | 0 | 138400 | 0 | 433274.08 | 219.0967 | 0
4608 | 7 | 0 | 0 | 0.22916 | 9.3726 | 0 | 0 | 0 | 0 | 9.3726 | 0 | 138400 | 0 | 433274.08 | 227.2208 | 0
4609 | 7 | 0 | 0 | 0.27743 | 11.3469 | 0 | 0 | 0 | 0 | 11.3469 | 0 | 138400 | 0 | 433274.08 | 237.0563 | 0
4610 | 7 | 0 | 0 | 0.28213 | 11.539 | 0 | 0 | 0 | 0 | 11.539 | 0 | 138400 | 0 | 433274.08 | 247.0583 | 0
4611 | 7 | 0 | 0 | 0.28232 | 11.5468 | 0 | 0 | 0 | 0 | 11.5468 | 0 | 138400 | 0 | 433274.08 | 257.0671 | 0
4612 | 7 | 0 | 0 | 0.26915 | 11.008 | 0 | 0 | 0 | 0 | 11.008 | 0 | 138400 | 0 | 433274.08 | 266.6089 | 0
4613 | 7 | 0 | 0 | 0.27098 | 11.0832 | 0 | 0 | 0 | 0 | 11.0832 | 0 | 138400 | 0 | 433274.08 | 276.2158 | 0
4614 | 7 | 0 | 0 | 0.48908 | 20.0033 | 0 | 0 | 0 | 0 | 20.0033 | 0 | 138400 | 0 | 433274.08 | 293.5546 | 0
4615 | 7 | 0 | 0.073823 | 0.51187 | 42.2557 | 0 | 0 | 0 | 0 | 42.2557 | 0 | 138400 | 0 | 433274.08 | 330.1819 | 0
4616 | 7 | 1 | 0.23738 | 0.59368 | 92.8365 | 200 | 92.8365 | 107.1635 | 200 | 0 | 0 | 138200 | 200 | 433474.08 | 223.0184 | 0
4617 | 7 | 1 | 0.41936 | 0.73406 | 151.1353 | 200 | 151.1353 | 48.8647 | 200 | 0 | 0 | 138000 | 200 | 433674.08 | 174.1537 | 0
4618 | 7 | 0 | 0.59095 | 1 | 211.5649 | 0 | 0 | 0 | 0 | 180 | 31.5649 | 138000 | 31.5649 | 433705.6449 | 330.1777 | 0
4619 | 7 | 0 | 0.73016 | 1 | 251.7702 | 0 | 0 | 0 | 0 | 180 | 71.7702 | 138000 | 71.7702 | 433777.4151 | 486.2017 | 0
4620 | 7 | 0 | 0.82057 | 1 | 277.8818 | 0 | 0 | 0 | 0 | 28.3899 | 200 | 138000 | 200 | 433977.4151 | 510.81 | 49.4919
4621 | 7 | 0 | 0.85189 | 1 | 286.9244 | 0 | 0 | 0 | 0 | 0 | 200 | 138000 | 200 | 434177.4151 | 510.81 | 86.9244
4622 | 7 | 0 | 0.82057 | 1 | 277.8818 | 0 | 0 | 0 | 0 | 0 | 200 | 138000 | 200 | 434377.4151 | 510.81 | 77.8818
4623 | 7 | 0 | 0.73016 | 1 | 251.7702 | 0 | 0 | 0 | 0 | 0 | 200 | 138000 | 200 | 434577.4151 | 510.81 | 51.7702
4624 | 7 | 0 | 0.59095 | 1 | 211.5649 | 0 | 0 | 0 | 0 | 0 | 200 | 138000 | 200 | 434777.4151 | 510.81 | 11.5649
4625 | 7 | 0 | 0.41936 | 1 | 162.0123 | 0 | 0 | 0 | 0 | 0 | 162.0123 | 138000 | 162.0123 | 434939.4275 | 510.81 | 0
4626 | 7 | 0 | 0.23738 | 1 | 109.4551 | 0 | 0 | 0 | 0 | 0 | 109.4551 | 138000 | 109.4551 | 435048.8825 | 510.81 | 0
4627 | 7 | 0 | 0.073823 | 1 | 62.2201 | 0 | 0 | 0 | 0 | 0 | 62.2201 | 138000 | 62.2201 | 435111.1026 | 510.81 | 0
4628 | 7 | 1 | 0 | 1 | 40.9 | 200 | 40.9 | 159.1 | 200 | 0 | 0 | 137800 | 200 | 435311.1026 | 351.71 | 0
4629 | 7 | 1 | 0 | 1 | 40.9 | 200 | 40.9 | 159.1 | 200 | 0 | 0 | 137600 | 200 | 435511.1026 | 192.61 | 0
4630 | 7 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 137600 | 0 | 435511.1026 | 228.0621 | 0
4631 | 7 | 0 | 0 | 0.91604 | 37.466 | 0 | 0 | 0 | 0 | 37.466 | 0 | 137600 | 0 | 435511.1026 | 260.5376 | 0
4632 | 7 | 0 | 0 | 0.55761 | 22.8064 | 0 | 0 | 0 | 0 | 22.8064 | 0 | 137600 | 0 | 435511.1026 | 280.3062 | 0
4633 | 7 | 0 | 0 | 0.50067 | 20.4772 | 0 | 0 | 0 | 0 | 20.4772 | 0 | 137600 | 0 | 435511.1026 | 298.0558 | 0
4634 | 7 | 0 | 0 | 0.71611 | 29.2889 | 0 | 0 | 0 | 0 | 29.2889 | 0 | 137600 | 0 | 435511.1026 | 323.4435 | 0
4635 | 7 | 0 | 0 | 0.66762 | 27.3057 | 0 | 0 | 0 | 0 | 27.3057 | 0 | 137600 | 0 | 435511.1026 | 347.112 | 0
4636 | 7 | 0 | 0 | 0.55694 | 22.7789 | 0 | 0 | 0 | 0 | 22.7789 | 0 | 137600 | 0 | 435511.1026 | 366.8568 | 0
4637 | 7 | 0 | 0 | 0.50664 | 20.7215 | 0 | 0 | 0 | 0 | 20.7215 | 0 | 137600 | 0 | 435511.1026 | 384.8182 | 0
4638 | 7 | 0 | 0 | 0.52592 | 21.5102 | 0 | 0 | 0 | 0 | 21.5102 | 0 | 137600 | 0 | 435511.1026 | 403.4632 | 0
4639 | 7 | 0 | 0.07795 | 0.39334 | 38.5996 | 0 | 0 | 0 | 0 | 38.5996 | 0 | 137600 | 0 | 435511.1026 | 436.9214 | 0
4640 | 7 | 1 | 0.25065 | 0.58052 | 96.1308 | 200 | 96.1308 | 103.8692 | 200 | 0 | 0 | 137400 | 200 | 435711.1026 | 333.0522 | 0
4641 | 7 | 1 | 0.44281 | 0.78359 | 159.9319 | 200 | 159.9319 | 40.0681 | 200 | 0 | 0 | 137200 | 200 | 435911.1026 | 292.984 | 0
4642 | 7 | 0 | 0.62398 | 0.6489 | 206.7456 | 0 | 0 | 0 | 0 | 180 | 26.7456 | 137200 | 26.7456 | 435937.8482 | 449.008 | 0
4643 | 7 | 0 | 0.77098 | 0.76825 | 254.0801 | 0 | 0 | 0 | 0 | 71.299 | 182.7811 | 137200 | 182.7811 | 436120.6293 | 510.81 | 0
4644 | 7 | 0 | 0.86645 | 0.78058 | 282.1558 | 0 | 0 | 0 | 0 | 0 | 200 | 137200 | 200 | 436320.6293 | 510.81 | 82.1558
4645 | 7 | 0 | 0.89951 | 0.8834 | 295.9091 | 0 | 0 | 0 | 0 | 0 | 200 | 137200 | 200 | 436520.6293 | 510.81 | 95.9091
4646 | 7 | 0 | 0.86645 | 0.52468 | 271.6894 | 0 | 0 | 0 | 0 | 0 | 200 | 137200 | 200 | 436720.6293 | 510.81 | 71.6894
4647 | 7 | 0 | 0.77098 | 0.5554 | 245.3745 | 0 | 0 | 0 | 0 | 0 | 200 | 137200 | 200 | 436920.6293 | 510.81 | 45.3745
4648 | 7 | 0 | 0.62398 | 0.52583 | 201.7122 | 0 | 0 | 0 | 0 | 0 | 200 | 137200 | 200 | 437120.6293 | 510.81 | 1.7122
4649 | 7 | 0 | 0.44281 | 0.58923 | 151.9823 | 0 | 0 | 0 | 0 | 0 | 151.9823 | 137200 | 151.9823 | 437272.6116 | 510.81 | 0
4650 | 7 | 0 | 0.25065 | 0.4884 | 92.3629 | 0 | 0 | 0 | 0 | 0 | 92.3629 | 137200 | 92.3629 | 437364.9744 | 510.81 | 0
4651 | 7 | 0 | 0.07795 | 0.61303 | 47.5851 | 0 | 0 | 0 | 0 | 0 | 47.5851 | 137200 | 47.5851 | 437412.5595 | 510.81 | 0
4652 | 7 | 1 | 0 | 0.5899 | 24.127 | 200 | 24.127 | 175.873 | 200 | 0 | 0 | 137000 | 200 | 437612.5595 | 334.937 | 0
4653 | 7 | 1 | 0 | 0.54199 | 22.1675 | 200 | 22.1675 | 177.8325 | 200 | 0 | 0 | 136800 | 200 | 437812.5595 | 157.1045 | 0
4654 | 7 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 136800 | 0 | 437812.5595 | 192.5567 | 0
4655 | 7 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 136800 | 0 | 437812.5595 | 228.0088 | 0
4656 | 7 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 136800 | 0 | 437812.5595 | 263.4609 | 0
4657 | 7 | 0 | 0 | 0.70329 | 28.7646 | 0 | 0 | 0 | 0 | 28.7646 | 0 | 136800 | 0 | 437812.5595 | 288.3941 | 0
4658 | 7 | 0 | 0 | 0.98849 | 40.4294 | 0 | 0 | 0 | 0 | 40.4294 | 0 | 136800 | 0 | 437812.5595 | 323.4382 | 0
4659 | 7 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 136800 | 0 | 437812.5595 | 358.8904 | 0
4660 | 7 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 136800 | 0 | 437812.5595 | 394.3425 | 0
4661 | 7 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 136800 | 0 | 437812.5595 | 429.7946 | 0
4662 | 7 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 136800 | 0 | 437812.5595 | 465.2467 | 0
4663 | 7 | 0 | 0.079687 | 1 | 63.9136 | 0 | 0 | 0 | 0 | 52.5649 | 11.3487 | 136800 | 11.3487 | 437823.9081 | 510.81 | 0
4664 | 7 | 1 | 0.25624 | 1 | 114.9012 | 200 | 114.9012 | 85.0988 | 200 | 0 | 0 | 136600 | 200 | 438023.9081 | 425.7112 | 0
4665 | 7 | 1 | 0.45268 | 1 | 171.634 | 200 | 171.634 | 28.366 | 200 | 0 | 0 | 136400 | 200 | 438223.9081 | 397.3452 | 0
4666 | 7 | 0 | 0.63789 | 1 | 225.1232 | 0 | 0 | 0 | 0 | 130.9008 | 94.2225 | 136400 | 94.2225 | 438318.1306 | 510.81 | 0
4667 | 7 | 0 | 0.78817 | 1 | 268.5226 | 0 | 0 | 0 | 0 | 0 | 200 | 136400 | 200 | 438518.1306 | 510.81 | 68.5226
4668 | 7 | 0 | 0.88576 | 1 | 296.7086 | 0 | 0 | 0 | 0 | 0 | 200 | 136400 | 200 | 438718.1306 | 510.81 | 96.7086
4669 | 7 | 0 | 0.91956 | 1 | 306.4695 | 0 | 0 | 0 | 0 | 0 | 200 | 136400 | 200 | 438918.1306 | 510.81 | 106.4695
4670 | 7 | 0 | 0.88576 | 1 | 296.7086 | 0 | 0 | 0 | 0 | 0 | 200 | 136400 | 200 | 439118.1306 | 510.81 | 96.7086
4671 | 7 | 0 | 0.78817 | 1 | 268.5226 | 0 | 0 | 0 | 0 | 0 | 200 | 136400 | 200 | 439318.1306 | 510.81 | 68.5226
4672 | 7 | 0 | 0.63789 | 1 | 225.1232 | 0 | 0 | 0 | 0 | 0 | 200 | 136400 | 200 | 439518.1306 | 510.81 | 25.1232
4673 | 7 | 0 | 0.45268 | 1 | 171.634 | 0 | 0 | 0 | 0 | 0 | 171.634 | 136400 | 171.634 | 439689.7646 | 510.81 | 0
4674 | 7 | 0 | 0.25624 | 0.83528 | 108.1642 | 0 | 0 | 0 | 0 | 0 | 108.1642 | 136400 | 108.1642 | 439797.9287 | 510.81 | 0
4675 | 7 | 0 | 0.079687 | 0.5987 | 47.5006 | 0 | 0 | 0 | 0 | 0 | 47.5006 | 136400 | 47.5006 | 439845.4293 | 510.81 | 0
4676 | 7 | 1 | 0 | 0.61614 | 25.2 | 200 | 25.2 | 174.8 | 200 | 0 | 0 | 136200 | 200 | 440045.4293 | 336.01 | 0
4677 | 7 | 1 | 0 | 0.75962 | 31.0686 | 200 | 31.0686 | 168.9314 | 200 | 0 | 0 | 136000 | 200 | 440245.4293 | 167.0787 | 0
4678 | 7 | 0 | 0 | 0.57396 | 23.475 | 0 | 0 | 0 | 0 | 23.475 | 0 | 136000 | 0 | 440245.4293 | 187.4268 | 0
4679 | 7 | 0 | 0 | 0.55975 | 22.8939 | 0 | 0 | 0 | 0 | 22.8939 | 0 | 136000 | 0 | 440245.4293 | 207.2713 | 0
4680 | 7 | 0 | 0 | 0.57021 | 23.3215 | 0 | 0 | 0 | 0 | 23.3215 | 0 | 136000 | 0 | 440245.4293 | 227.4863 | 0
4681 | 7 | 0 | 0 | 0.47202 | 19.3055 | 0 | 0 | 0 | 0 | 19.3055 | 0 | 136000 | 0 | 440245.4293 | 244.2204 | 0
4682 | 7 | 0 | 0 | 0.59879 | 24.4907 | 0 | 0 | 0 | 0 | 24.4907 | 0 | 136000 | 0 | 440245.4293 | 265.4489 | 0
4683 | 7 | 0 | 0 | 0.48168 | 19.7008 | 0 | 0 | 0 | 0 | 19.7008 | 0 | 136000 | 0 | 440245.4293 | 282.5256 | 0
4684 | 7 | 0 | 0 | 0.29305 | 11.9858 | 0 | 0 | 0 | 0 | 11.9858 | 0 | 136000 | 0 | 440245.4293 | 292.9149 | 0
4685 | 7 | 0 | 0 | 0.30223 | 12.3614 | 0 | 0 | 0 | 0 | 12.3614 | 0 | 136000 | 0 | 440245.4293 | 303.6297 | 0
4686 | 7 | 0 | 0 | 0.34563 | 14.1362 | 0 | 0 | 0 | 0 | 14.1362 | 0 | 136000 | 0 | 440245.4293 | 315.883 | 0
4687 | 7 | 0 | 0.077594 | 0.40106 | 38.8127 | 0 | 0 | 0 | 0 | 38.8127 | 0 | 136000 | 0 | 440245.4293 | 349.5258 | 0
4688 | 7 | 1 | 0.24951 | 0.46142 | 90.9299 | 200 | 90.9299 | 109.0701 | 200 | 0 | 0 | 135800 | 200 | 440445.4293 | 240.4557 | 0
4689 | 7 | 1 | 0.44079 | 0.33563 | 141.0276 | 200 | 141.0276 | 58.9724 | 200 | 0 | 0 | 135600 | 200 | 440645.4293 | 181.4833 | 0
4690 | 7 | 0 | 0.62114 | 0.45108 | 197.8338 | 0 | 0 | 0 | 0 | 180 | 17.8338 | 135600 | 17.8338 | 440663.2631 | 337.5073 | 0
4691 | 7 | 0 | 0.76747 | 0.38667 | 237.4588 | 0 | 0 | 0 | 0 | 180 | 57.4588 | 135600 | 57.4588 | 440720.7219 | 493.5313 | 0
4692 | 7 | 0 | 0.8625 | 0.27899 | 260.5009 | 0 | 0 | 0 | 0 | 19.9339 | 200 | 135600 | 200 | 440920.7219 | 510.81 | 40.567
4693 | 7 | 0 | 0.89541 | 0.17601 | 265.7931 | 0 | 0 | 0 | 0 | 0 | 200 | 135600 | 200 | 441120.7219 | 510.81 | 65.7931
4694 | 7 | 0 | 0.8625 | 0.15725 | 255.5214 | 0 | 0 | 0 | 0 | 0 | 200 | 135600 | 200 | 441320.7219 | 510.81 | 55.5214
4695 | 7 | 0 | 0.76747 | 0.21775 | 230.5503 | 0 | 0 | 0 | 0 | 0 | 200 | 135600 | 200 | 441520.7219 | 510.81 | 30.5503
4696 | 7 | 0 | 0.62114 | 0.19391 | 187.3156 | 0 | 0 | 0 | 0 | 0 | 187.3156 | 135600 | 187.3156 | 441708.0376 | 510.81 | 0
4697 | 7 | 0 | 0.44079 | 0.24261 | 137.2231 | 0 | 0 | 0 | 0 | 0 | 137.2231 | 135600 | 137.2231 | 441845.2607 | 510.81 | 0
4698 | 7 | 0 | 0.24951 | 0.24709 | 82.1635 | 0 | 0 | 0 | 0 | 0 | 82.1635 | 135600 | 82.1635 | 441927.4241 | 510.81 | 0
4699 | 7 | 0 | 0.077594 | 0.20579 | 30.826 | 0 | 0 | 0 | 0 | 0 | 30.826 | 135600 | 30.826 | 441958.2501 | 510.81 | 0
4700 | 7 | 1 | 0 | 0.19147 | 7.831 | 200 | 7.831 | 180 | 187.831 | 0 | 0 | 135400 | 187.831 | 442146.0811 | 330.81 | 0
4701 | 7 | 1 | 0 | 0.20744 | 8.4841 | 200 | 8.4841 | 180 | 188.4841 | 0 | 0 | 135200 | 188.4841 | 442334.5652 | 150.81 | 0
4702 | 7 | 0 | 0 | 0.16357 | 6.6898 | 0 | 0 | 0 | 0 | 6.6898 | 0 | 135200 | 0 | 442334.5652 | 156.6088 | 0
4703 | 7 | 0 | 0 | 0.17816 | 7.2865 | 0 | 0 | 0 | 0 | 7.2865 | 0 | 135200 | 0 | 442334.5652 | 162.9247 | 0
4704 | 7 | 0 | 0 | 0.15319 | 6.2656 | 0 | 0 | 0 | 0 | 6.2656 | 0 | 135200 | 0 | 442334.5652 | 168.3558 | 0
4705 | 7 | 0 | 0 | 0.15986 | 6.5382 | 0 | 0 | 0 | 0 | 6.5382 | 0 | 135200 | 0 | 442334.5652 | 174.0231 | 0
4706 | 7 | 0 | 0 | 0.23674 | 9.6826 | 0 | 0 | 0 | 0 | 9.6826 | 0 | 135200 | 0 | 442334.5652 | 182.416 | 0
4707 | 7 | 0 | 0 | 0.33241 | 13.5956 | 0 | 0 | 0 | 0 | 13.5956 | 0 | 135200 | 0 | 442334.5652 | 194.2006 | 0
4708 | 7 | 0 | 0 | 0.36574 | 14.9589 | 0 | 0 | 0 | 0 | 14.9589 | 0 | 135200 | 0 | 442334.5652 | 207.167 | 0
4709 | 7 | 0 | 0 | 0.35049 | 14.3351 | 0 | 0 | 0 | 0 | 14.3351 | 0 | 135200 | 0 | 442334.5652 | 219.5926 | 0
4710 | 7 | 0 | 0 | 0.24876 | 10.1743 | 0 | 0 | 0 | 0 | 10.1743 | 0 | 135200 | 0 | 442334.5652 | 228.4117 | 0
4711 | 7 | 0 | 0.077198 | 0.29591 | 34.3976 | 0 | 0 | 0 | 0 | 34.3976 | 0 | 135200 | 0 | 442334.5652 | 258.2276 | 0
4712 | 7 | 1 | 0.24823 | 0.28947 | 83.529 | 200 | 83.529 | 116.471 | 200 | 0 | 0 | 135000 | 200 | 442534.5652 | 141.7565 | 0
4713 | 7 | 1 | 0.43854 | 0.42257 | 143.9335 | 200 | 143.9335 | 56.0665 | 200 | 0 | 0 | 134800 | 200 | 442734.5652 | 85.6901 | 0
4714 | 7 | 0 | 0.61797 | 0.30212 | 190.8254 | 0 | 0 | 0 | 0 | 180 | 10.8254 | 134800 | 10.8254 | 442745.3907 | 241.7141 | 0
4715 | 7 | 0 | 0.76355 | 0.24224 | 230.4199 | 0 | 0 | 0 | 0 | 180 | 50.4199 | 134800 | 50.4199 | 442795.8106 | 397.7381 | 0
4716 | 7 | 0 | 0.8581 | 0.2678 | 258.7709 | 0 | 0 | 0 | 0 | 130.4476 | 128.3234 | 134800 | 128.3234 | 442924.1339 | 510.81 | 0
4717 | 7 | 0 | 0.89084 | 0.2945 | 269.3188 | 0 | 0 | 0 | 0 | 0 | 200 | 134800 | 200 | 443124.1339 | 510.81 | 69.3188
4718 | 7 | 0 | 0.8581 | 0.32878 | 261.265 | 0 | 0 | 0 | 0 | 0 | 200 | 134800 | 200 | 443324.1339 | 510.81 | 61.265
4719 | 7 | 0 | 0.76355 | 0.51904 | 241.7413 | 0 | 0 | 0 | 0 | 0 | 200 | 134800 | 200 | 443524.1339 | 510.81 | 41.7413
4720 | 7 | 0 | 0.61797 | 0.31808 | 191.4781 | 0 | 0 | 0 | 0 | 0 | 191.4781 | 134800 | 191.4781 | 443715.612 | 510.81 | 0
4721 | 7 | 0 | 0.43854 | 0.32787 | 140.0602 | 0 | 0 | 0 | 0 | 0 | 140.0602 | 134800 | 140.0602 | 443855.6722 | 510.81 | 0
4722 | 7 | 0 | 0.24823 | 0.2846 | 83.33 | 0 | 0 | 0 | 0 | 0 | 83.33 | 134800 | 83.33 | 443939.0023 | 510.81 | 0
4723 | 7 | 0 | 0.077198 | 0.35198 | 36.6906 | 0 | 0 | 0 | 0 | 0 | 36.6906 | 134800 | 36.6906 | 443975.6929 | 510.81 | 0
4724 | 7 | 1 | 0 | 0.35815 | 14.6484 | 200 | 14.6484 | 180 | 194.6484 | 0 | 0 | 134600 | 194.6484 | 444170.3413 | 330.81 | 0
4725 | 7 | 1 | 0 | 0.45682 | 18.6839 | 200 | 18.6839 | 180 | 198.6839 | 0 | 0 | 134400 | 198.6839 | 444369.0253 | 150.81 | 0
4726 | 7 | 0 | 0 | 0.55668 | 22.7681 | 0 | 0 | 0 | 0 | 22.7681 | 0 | 134400 | 0 | 444369.0253 | 170.5454 | 0
4727 | 7 | 0 | 0 | 0.51119 | 20.9078 | 0 | 0 | 0 | 0 | 20.9078 | 0 | 134400 | 0 | 444369.0253 | 188.6683 | 0
4728 | 7 | 0 | 0 | 0.49954 | 20.4312 | 0 | 0 | 0 | 0 | 20.4312 | 0 | 134400 | 0 | 444369.0253 | 206.378 | 0
4729 | 7 | 0 | 0 | 0.69939 | 28.605 | 0 | 0 | 0 | 0 | 28.605 | 0 | 134400 | 0 | 444369.0253 | 231.1729 | 0
4730 | 7 | 0 | 0 | 0.70535 | 28.849 | 0 | 0 | 0 | 0 | 28.849 | 0 | 134400 | 0 | 444369.0253 | 256.1792 | 0
4731 | 7 | 0 | 0 | 0.69083 | 28.2552 | 0 | 0 | 0 | 0 | 28.2552 | 0 | 134400 | 0 | 444369.0253 | 280.6708 | 0
4732 | 7 | 0 | 0 | 0.74418 | 30.4368 | 0 | 0 | 0 | 0 | 30.4368 | 0 | 134400 | 0 | 444369.0253 | 307.0534 | 0
4733 | 7 | 0 | 0 | 0.78439 | 32.0816 | 0 | 0 | 0 | 0 | 32.0816 | 0 | 134400 | 0 | 444369.0253 | 334.8617 | 0
4734 | 7 | 0 | 0 | 0.65154 | 26.648 | 0 | 0 | 0 | 0 | 26.648 | 0 | 134400 | 0 | 444369.0253 | 357.9602 | 0
4735 | 7 | 0 | 0.068535 | 0.79458 | 52.2911 | 0 | 0 | 0 | 0 | 52.2911 | 0 | 134400 | 0 | 444369.0253 | 403.2861 | 0
4736 | 7 | 1 | 0.22038 | 1 | 104.5452 | 200 | 104.5452 | 95.4548 | 200 | 0 | 0 | 134200 | 200 | 444569.0253 | 307.8313 | 0
4737 | 7 | 1 | 0.38933 | 1 | 153.3382 | 200 | 153.3382 | 46.6618 | 200 | 0 | 0 | 134000 | 200 | 444769.0253 | 261.1695 | 0
4738 | 7 | 0 | 0.54862 | 1 | 199.3417 | 0 | 0 | 0 | 0 | 180 | 19.3417 | 134000 | 19.3417 | 444788.367 | 417.1935 | 0
4739 | 7 | 0 | 0.67787 | 1 | 236.6677 | 0 | 0 | 0 | 0 | 108.0024 | 128.6653 | 134000 | 128.6653 | 444917.0323 | 510.81 | 0
4740 | 7 | 0 | 0.7618 | 1 | 260.909 | 0 | 0 | 0 | 0 | 0 | 200 | 134000 | 200 | 445117.0323 | 510.81 | 60.909
4741 | 7 | 0 | 0.79087 | 1 | 269.3038 | 0 | 0 | 0 | 0 | 0 | 200 | 134000 | 200 | 445317.0323 | 510.81 | 69.3038
4742 | 7 | 0 | 0.7618 | 1 | 260.909 | 0 | 0 | 0 | 0 | 0 | 200 | 134000 | 200 | 445517.0323 | 510.81 | 60.909
4743 | 7 | 0 | 0.67787 | 1 | 236.6677 | 0 | 0 | 0 | 0 | 0 | 200 | 134000 | 200 | 445717.0323 | 510.81 | 36.6677
4744 | 7 | 0 | 0.54862 | 1 | 199.3417 | 0 | 0 | 0 | 0 | 0 | 199.3417 | 134000 | 199.3417 | 445916.374 | 510.81 | 0
4745 | 7 | 0 | 0.38933 | 1 | 153.3382 | 0 | 0 | 0 | 0 | 0 | 153.3382 | 134000 | 153.3382 | 446069.7122 | 510.81 | 0
4746 | 7 | 0 | 0.22038 | 1 | 104.5452 | 0 | 0 | 0 | 0 | 0 | 104.5452 | 134000 | 104.5452 | 446174.2574 | 510.81 | 0
4747 | 7 | 0 | 0.068535 | 1 | 60.6929 | 0 | 0 | 0 | 0 | 0 | 60.6929 | 134000 | 60.6929 | 446234.9503 | 510.81 | 0
4748 | 7 | 1 | 0 | 1 | 40.9 | 200 | 40.9 | 159.1 | 200 | 0 | 0 | 133800 | 200 | 446434.9503 | 351.71 | 0
4749 | 7 | 1 | 0 | 1 | 40.9 | 200 | 40.9 | 159.1 | 200 | 0 | 0 | 133600 | 200 | 446634.9503 | 192.61 | 0
4750 | 7 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 133600 | 0 | 446634.9503 | 228.0621 | 0
4751 | 7 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 133600 | 0 | 446634.9503 | 263.5142 | 0
4752 | 7 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 133600 | 0 | 446634.9503 | 298.9664 | 0
4753 | 7 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 133600 | 0 | 446634.9503 | 334.4185 | 0
4754 | 7 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 133600 | 0 | 446634.9503 | 369.8706 | 0
4755 | 7 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 133600 | 0 | 446634.9503 | 405.3227 | 0
4756 | 7 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 133600 | 0 | 446634.9503 | 440.7748 | 0
4757 | 7 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 133600 | 0 | 446634.9503 | 476.227 | 0
4758 | 7 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 39.8974 | 1.0026 | 133600 | 1.0026 | 446635.9529 | 510.81 | 0
4759 | 7 | 0 | 0.079369 | 1 | 63.8218 | 0 | 0 | 0 | 0 | 0 | 63.8218 | 133600 | 63.8218 | 446699.7747 | 510.81 | 0
4760 | 7 | 1 | 0.25521 | 1 | 114.6058 | 200 | 114.6058 | 85.3942 | 200 | 0 | 0 | 133400 | 200 | 446899.7747 | 425.4158 | 0
4761 | 7 | 1 | 0.45087 | 1 | 171.1118 | 200 | 171.1118 | 28.8882 | 200 | 0 | 0 | 133200 | 200 | 447099.7747 | 396.5276 | 0
4762 | 7 | 0 | 0.63535 | 1 | 224.3876 | 0 | 0 | 0 | 0 | 131.844 | 92.5437 | 133200 | 92.5437 | 447192.3183 | 510.81 | 0
4763 | 7 | 0 | 0.78502 | 1 | 267.6138 | 0 | 0 | 0 | 0 | 0 | 200 | 133200 | 200 | 447392.3183 | 510.81 | 67.6138
4764 | 7 | 0 | 0.88223 | 1 | 295.6872 | 0 | 0 | 0 | 0 | 0 | 200 | 133200 | 200 | 447592.3183 | 510.81 | 95.6872
4765 | 7 | 0 | 0.91589 | 1 | 305.409 | 0 | 0 | 0 | 0 | 0 | 200 | 133200 | 200 | 447792.3183 | 510.81 | 105.409
4766 | 7 | 0 | 0.88223 | 1 | 295.6872 | 0 | 0 | 0 | 0 | 0 | 200 | 133200 | 200 | 447992.3183 | 510.81 | 95.6872
4767 | 7 | 0 | 0.78502 | 1 | 267.6138 | 0 | 0 | 0 | 0 | 0 | 200 | 133200 | 200 | 448192.3183 | 510.81 | 67.6138
4768 | 7 | 0 | 0.63535 | 1 | 224.3876 | 0 | 0 | 0 | 0 | 0 | 200 | 133200 | 200 | 448392.3183 | 510.81 | 24.3876
4769 | 7 | 0 | 0.45087 | 0.96955 | 169.8666 | 0 | 0 | 0 | 0 | 0 | 169.8666 | 133200 | 169.8666 | 448562.1849 | 510.81 | 0
4770 | 7 | 0 | 0.25521 | 1 | 114.6058 | 0 | 0 | 0 | 0 | 0 | 114.6058 | 133200 | 114.6058 | 448676.7907 | 510.81 | 0
4771 | 7 | 0 | 0.079369 | 1 | 63.8218 | 0 | 0 | 0 | 0 | 0 | 63.8218 | 133200 | 63.8218 | 448740.6125 | 510.81 | 0
4772 | 7 | 1 | 0 | 0.99422 | 40.6634 | 200 | 40.6634 | 159.3366 | 200 | 0 | 0 | 133000 | 200 | 448940.6125 | 351.4734 | 0
4773 | 7 | 1 | 0 | 0.84647 | 34.6208 | 200 | 34.6208 | 165.3792 | 200 | 0 | 0 | 132800 | 200 | 449140.6125 | 186.0942 | 0
4774 | 7 | 0 | 0 | 0.88798 | 36.3183 | 0 | 0 | 0 | 0 | 36.3183 | 0 | 132800 | 0 | 449140.6125 | 217.5749 | 0
4775 | 7 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 132800 | 0 | 449140.6125 | 253.027 | 0
4776 | 7 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 132800 | 0 | 449140.6125 | 288.4792 | 0
4777 | 7 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 132800 | 0 | 449140.6125 | 323.9313 | 0
4778 | 7 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 132800 | 0 | 449140.6125 | 359.3834 | 0
4779 | 7 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 132800 | 0 | 449140.6125 | 394.8355 | 0
4780 | 7 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 132800 | 0 | 449140.6125 | 430.2876 | 0
4781 | 7 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 132800 | 0 | 449140.6125 | 465.7398 | 0
4782 | 7 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 132800 | 0 | 449140.6125 | 501.1919 | 0
4783 | 7 | 0 | 0.07723 | 1 | 63.204 | 0 | 0 | 0 | 0 | 11.0961 | 52.1079 | 132800 | 52.1079 | 449192.7204 | 510.81 | 0
4784 | 7 | 1 | 0.24833 | 1 | 112.6189 | 200 | 112.6189 | 87.3811 | 200 | 0 | 0 | 132600 | 200 | 449392.7204 | 423.4289 | 0
4785 | 7 | 1 | 0.43872 | 1 | 167.6018 | 200 | 167.6018 | 32.3982 | 200 | 0 | 0 | 132400 | 200 | 449592.7204 | 391.0306 | 0
4786 | 7 | 0 | 0.61822 | 1 | 219.4411 | 0 | 0 | 0 | 0 | 138.1857 | 81.2553 | 132400 | 81.2553 | 449673.9758 | 510.81 | 0
4787 | 7 | 0 | 0.76386 | 1 | 261.5019 | 0 | 0 | 0 | 0 | 0 | 200 | 132400 | 200 | 449873.9758 | 510.81 | 61.5019
4788 | 7 | 0 | 0.85844 | 1 | 288.8186 | 0 | 0 | 0 | 0 | 0 | 200 | 132400 | 200 | 450073.9758 | 510.81 | 88.8186
4789 | 7 | 0 | 0.8912 | 1 | 298.2783 | 0 | 0 | 0 | 0 | 0 | 200 | 132400 | 200 | 450273.9758 | 510.81 | 98.2783
4790 | 7 | 0 | 0.85844 | 1 | 288.8186 | 0 | 0 | 0 | 0 | 0 | 200 | 132400 | 200 | 450473.9758 | 510.81 | 88.8186
4791 | 7 | 0 | 0.76386 | 1 | 261.5019 | 0 | 0 | 0 | 0 | 0 | 200 | 132400 | 200 | 450673.9758 | 510.81 | 61.5019
4792 | 7 | 0 | 0.61822 | 1 | 219.4411 | 0 | 0 | 0 | 0 | 0 | 200 | 132400 | 200 | 450873.9758 | 510.81 | 19.4411
4793 | 7 | 0 | 0.43872 | 0.99646 | 167.457 | 0 | 0 | 0 | 0 | 0 | 167.457 | 132400 | 167.457 | 451041.4327 | 510.81 | 0
4794 | 7 | 0 | 0.24833 | 0.69489 | 100.14 | 0 | 0 | 0 | 0 | 0 | 100.14 | 132400 | 100.14 | 451141.5728 | 510.81 | 0
4795 | 7 | 0 | 0.07723 | 0.47987 | 41.9305 | 0 | 0 | 0 | 0 | 0 | 41.9305 | 132400 | 41.9305 | 451183.5033 | 510.81 | 0
4796 | 7 | 1 | 0 | 0.43797 | 17.9131 | 200 | 17.9131 | 180 | 197.9131 | 0 | 0 | 132200 | 197.9131 | 451381.4164 | 330.81 | 0
4797 | 7 | 1 | 0 | 0.38185 | 15.6176 | 200 | 15.6176 | 180 | 195.6176 | 0 | 0 | 132000 | 195.6176 | 451577.034 | 150.81 | 0
4798 | 7 | 0 | 0 | 0.3733 | 15.2681 | 0 | 0 | 0 | 0 | 15.2681 | 0 | 132000 | 0 | 451577.034 | 164.0443 | 0
4799 | 7 | 0 | 0 | 0.35952 | 14.7044 | 0 | 0 | 0 | 0 | 14.7044 | 0 | 132000 | 0 | 451577.034 | 176.7901 | 0
4800 | 7 | 0 | 0 | 0.29058 | 11.8846 | 0 | 0 | 0 | 0 | 11.8846 | 0 | 132000 | 0 | 451577.034 | 187.0917 | 0
4801 | 7 | 0 | 0 | 0.17596 | 7.1969 | 0 | 0 | 0 | 0 | 7.1969 | 0 | 132000 | 0 | 451577.034 | 193.3299 | 0
4802 | 7 | 0 | 0 | 0.1509 | 6.1717 | 0 | 0 | 0 | 0 | 6.1717 | 0 | 132000 | 0 | 451577.034 | 198.6795 | 0
4803 | 7 | 0 | 0 | 0.16721 | 6.8387 | 0 | 0 | 0 | 0 | 6.8387 | 0 | 132000 | 0 | 451577.034 | 204.6074 | 0
4804 | 7 | 0 | 0 | 0.16935 | 6.9265 | 0 | 0 | 0 | 0 | 6.9265 | 0 | 132000 | 0 | 451577.034 | 210.6112 | 0
4805 | 7 | 0 | 0 | 0.25133 | 10.2793 | 0 | 0 | 0 | 0 | 10.2793 | 0 | 132000 | 0 | 451577.034 | 219.5213 | 0
4806 | 7 | 0 | 0 | 0.20359 | 8.3267 | 0 | 0 | 0 | 0 | 8.3267 | 0 | 132000 | 0 | 451577.034 | 226.7389 | 0
4807 | 7 | 0 | 0.077125 | 0.24981 | 32.491 | 0 | 0 | 0 | 0 | 32.491 | 0 | 132000 | 0 | 451577.034 | 254.9021 | 0
4808 | 7 | 1 | 0.248 | 0.39569 | 87.8052 | 200 | 87.8052 | 112.1948 | 200 | 0 | 0 | 131800 | 200 | 451777.034 | 142.7073 | 0
4809 | 7 | 1 | 0.43812 | 0.51102 | 147.43 | 200 | 147.43 | 52.57 | 200 | 0 | 0 | 131600 | 200 | 451977.034 | 90.1373 | 0
4810 | 7 | 0 | 0.61738 | 0.75267 | 209.0826 | 0 | 0 | 0 | 0 | 180 | 29.0826 | 131600 | 29.0826 | 452006.1166 | 246.1613 | 0
4811 | 7 | 0 | 0.76282 | 0.95123 | 259.2074 | 0 | 0 | 0 | 0 | 180 | 79.2074 | 131600 | 79.2074 | 452085.324 | 402.1853 | 0
4812 | 7 | 0 | 0.85728 | 0.81397 | 280.873 | 0 | 0 | 0 | 0 | 125.3169 | 155.5561 | 131600 | 155.5561 | 452240.88 | 510.81 | 0
4813 | 7 | 0 | 0.88999 | 0.84348 | 291.527 | 0 | 0 | 0 | 0 | 0 | 200 | 131600 | 200 | 452440.88 | 510.81 | 91.527
4814 | 7 | 0 | 0.85728 | 0.91372 | 284.9528 | 0 | 0 | 0 | 0 | 0 | 200 | 131600 | 200 | 452640.88 | 510.81 | 84.9528
4815 | 7 | 0 | 0.76282 | 0.99803 | 261.1213 | 0 | 0 | 0 | 0 | 0 | 200 | 131600 | 200 | 452840.88 | 510.81 | 61.1213
4816 | 7 | 0 | 0.61738 | 0.67845 | 206.047 | 0 | 0 | 0 | 0 | 0 | 200 | 131600 | 200 | 453040.88 | 510.81 | 6.047
4817 | 7 | 0 | 0.43812 | 0.88255 | 162.6254 | 0 | 0 | 0 | 0 | 0 | 162.6254 | 131600 | 162.6254 | 453203.5055 | 510.81 | 0
4818 | 7 | 0 | 0.248 | 1 | 112.5215 | 0 | 0 | 0 | 0 | 0 | 112.5215 | 131600 | 112.5215 | 453316.027 | 510.81 | 0
4819 | 7 | 0 | 0.077125 | 1 | 63.1737 | 0 | 0 | 0 | 0 | 0 | 63.1737 | 131600 | 63.1737 | 453379.2007 | 510.81 | 0
4820 | 7 | 1 | 0 | 0.86513 | 35.3837 | 200 | 35.3837 | 164.6163 | 200 | 0 | 0 | 131400 | 200 | 453579.2007 | 346.1937 | 0
4821 | 7 | 1 | 0 | 0.98496 | 40.2849 | 200 | 40.2849 | 159.7151 | 200 | 0 | 0 | 131200 | 200 | 453779.2007 | 186.4786 | 0
4822 | 7 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 131200 | 0 | 453779.2007 | 221.9307 | 0
4823 | 7 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 131200 | 0 | 453779.2007 | 257.3828 | 0
4824 | 7 | 0 | 0 | 0.70358 | 28.7763 | 0 | 0 | 0 | 0 | 28.7763 | 0 | 131200 | 0 | 453779.2007 | 282.3261 | 0
4825 | 7 | 0 | 0 | 0.82778 | 33.856 | 0 | 0 | 0 | 0 | 33.856 | 0 | 131200 | 0 | 453779.2007 | 311.6725 | 0
4826 | 7 | 0 | 0 | 0.37579 | 15.3697 | 0 | 0 | 0 | 0 | 15.3697 | 0 | 131200 | 0 | 453779.2007 | 324.995 | 0
4827 | 7 | 0 | 0 | 0.36338 | 14.862 | 0 | 0 | 0 | 0 | 14.862 | 0 | 131200 | 0 | 453779.2007 | 337.8774 | 0
4828 | 7 | 0 | 0 | 0.34756 | 14.2151 | 0 | 0 | 0 | 0 | 14.2151 | 0 | 131200 | 0 | 453779.2007 | 350.199 | 0
4829 | 7 | 0 | 0 | 0.39287 | 16.0682 | 0 | 0 | 0 | 0 | 16.0682 | 0 | 131200 | 0 | 453779.2007 | 364.127 | 0
4830 | 7 | 0 | 0 | 0.41055 | 16.7915 | 0 | 0 | 0 | 0 | 16.7915 | 0 | 131200 | 0 | 453779.2007 | 378.6819 | 0
4831 | 7 | 0 | 0.08922 | 0.76338 | 56.989 | 0 | 0 | 0 | 0 | 56.989 | 0 | 131200 | 0 | 453779.2007 | 428.0799 | 0
4832 | 7 | 1 | 0.28689 | 0.96383 | 122.2746 | 200 | 122.2746 | 77.7254 | 200 | 0 | 0 | 131000 | 200 | 453979.2007 | 350.3545 | 0
4833 | 7 | 1 | 0.50683 | 1 | 187.2734 | 200 | 187.2734 | 12.7266 | 200 | 0 | 0 | 130800 | 200 | 454179.2007 | 337.6278 | 0
4834 | 7 | 0 | 0.7142 | 0.72742 | 236.0126 | 0 | 0 | 0 | 0 | 180 | 56.0126 | 130800 | 56.0126 | 454235.2134 | 493.6518 | 0
4835 | 7 | 0 | 0.88245 | 0.95542 | 293.9293 | 0 | 0 | 0 | 0 | 19.7948 | 200 | 130800 | 200 | 454435.2134 | 510.81 | 74.1344
4836 | 7 | 0 | 0.99172 | 0.97755 | 326.3919 | 0 | 0 | 0 | 0 | 0 | 200 | 130800 | 200 | 454635.2134 | 510.81 | 126.3919
4837 | 7 | 0 | 1 | 0.79555 | 321.3382 | 0 | 0 | 0 | 0 | 0 | 200 | 130800 | 200 | 454835.2134 | 510.81 | 121.3382
4838 | 7 | 0 | 0.99172 | 0.65287 | 313.1125 | 0 | 0 | 0 | 0 | 0 | 200 | 130800 | 200 | 455035.2134 | 510.81 | 113.1125
4839 | 7 | 0 | 0.88245 | 0.70804 | 283.8111 | 0 | 0 | 0 | 0 | 0 | 200 | 130800 | 200 | 455235.2134 | 510.81 | 83.8111
4840 | 7 | 0 | 0.7142 | 0.43619 | 224.1015 | 0 | 0 | 0 | 0 | 0 | 200 | 130800 | 200 | 455435.2134 | 510.81 | 24.1015
4841 | 7 | 0 | 0.50683 | 0.39428 | 162.4993 | 0 | 0 | 0 | 0 | 0 | 162.4993 | 130800 | 162.4993 | 455597.7126 | 510.81 | 0
4842 | 7 | 0 | 0.28689 | 0.4929 | 103.0136 | 0 | 0 | 0 | 0 | 0 | 103.0136 | 130800 | 103.0136 | 455700.7262 | 510.81 | 0
4843 | 7 | 0 | 0.08922 | 0.58158 | 49.5534 | 0 | 0 | 0 | 0 | 0 | 49.5534 | 130800 | 49.5534 | 455750.2796 | 510.81 | 0
4844 | 7 | 1 | 0 | 0.53573 | 21.9114 | 200 | 21.9114 | 178.0886 | 200 | 0 | 0 | 130600 | 200 | 455950.2796 | 332.7214 | 0
4845 | 7 | 1 | 0 | 0.37394 | 15.2941 | 200 | 15.2941 | 180 | 195.2941 | 0 | 0 | 130400 | 195.2941 | 456145.5737 | 152.7214 | 0
4846 | 7 | 0 | 0 | 0.43931 | 17.9677 | 0 | 0 | 0 | 0 | 17.9677 | 0 | 130400 | 0 | 456145.5737 | 168.2958 | 0
4847 | 7 | 0 | 0 | 0.3626 | 14.8303 | 0 | 0 | 0 | 0 | 14.8303 | 0 | 130400 | 0 | 456145.5737 | 181.1507 | 0
4848 | 7 | 0 | 0 | 0.29277 | 11.9744 | 0 | 0 | 0 | 0 | 11.9744 | 0 | 130400 | 0 | 456145.5737 | 191.5301 | 0
4849 | 7 | 0 | 0 | 0.27491 | 11.2438 | 0 | 0 | 0 | 0 | 11.2438 | 0 | 130400 | 0 | 456145.5737 | 201.2762 | 0
4850 | 7 | 0 | 0 | 0.2275 | 9.3047 | 0 | 0 | 0 | 0 | 9.3047 | 0 | 130400 | 0 | 456145.5737 | 209.3415 | 0
4851 | 7 | 0 | 0 | 0.25266 | 10.3338 | 0 | 0 | 0 | 0 | 10.3338 | 0 | 130400 | 0 | 456145.5737 | 218.2988 | 0
4852 | 7 | 0 | 0 | 0.38641 | 15.804 | 0 | 0 | 0 | 0 | 15.804 | 0 | 130400 | 0 | 456145.5737 | 231.9977 | 0
4853 | 7 | 0 | 0 | 0.20168 | 8.2489 | 0 | 0 | 0 | 0 | 8.2489 | 0 | 130400 | 0 | 456145.5737 | 239.1479 | 0
4854 | 7 | 0 | 0 | 0.13661 | 5.5872 | 0 | 0 | 0 | 0 | 5.5872 | 0 | 130400 | 0 | 456145.5737 | 243.9908 | 0
4855 | 7 | 0 | 0.084216 | 0.24405 | 34.3033 | 0 | 0 | 0 | 0 | 34.3033 | 0 | 130400 | 0 | 456145.5737 | 273.7249 | 0
4856 | 7 | 1 | 0.2708 | 0.12169 | 83.1831 | 200 | 83.1831 | 116.8169 | 200 | 0 | 0 | 130200 | 200 | 456345.5737 | 156.908 | 0
4857 | 7 | 1 | 0.4784 | 0.14663 | 144.1598 | 200 | 144.1598 | 55.8402 | 200 | 0 | 0 | 130000 | 200 | 456545.5737 | 101.0678 | 0
4858 | 7 | 0 | 0.67414 | 0.17801 | 201.972 | 0 | 0 | 0 | 0 | 180 | 21.972 | 130000 | 21.972 | 456567.5457 | 257.0918 | 0
4859 | 7 | 0 | 0.83295 | 0.26543 | 251.4128 | 0 | 0 | 0 | 0 | 180 | 71.4128 | 130000 | 71.4128 | 456638.9585 | 413.1158 | 0
4860 | 7 | 0 | 0.9361 | 0.35621 | 284.9134 | 0 | 0 | 0 | 0 | 112.7067 | 172.2067 | 130000 | 172.2067 | 456811.1652 | 510.81 | 0
4861 | 7 | 0 | 0.97181 | 0.26576 | 291.5296 | 0 | 0 | 0 | 0 | 0 | 200 | 130000 | 200 | 457011.1652 | 510.81 | 91.5296
4862 | 7 | 0 | 0.9361 | 0.30048 | 282.6337 | 0 | 0 | 0 | 0 | 0 | 200 | 130000 | 200 | 457211.1652 | 510.81 | 82.6337
4863 | 7 | 0 | 0.83295 | 0.22257 | 249.6598 | 0 | 0 | 0 | 0 | 0 | 200 | 130000 | 200 | 457411.1652 | 510.81 | 49.6598
4864 | 7 | 0 | 0.67414 | 0.18643 | 202.3165 | 0 | 0 | 0 | 0 | 0 | 200 | 130000 | 200 | 457611.1652 | 510.81 | 2.3165
4865 | 7 | 0 | 0.4784 | 0.16324 | 144.8393 | 0 | 0 | 0 | 0 | 0 | 144.8393 | 130000 | 144.8393 | 457756.0045 | 510.81 | 0
4866 | 7 | 0 | 0.2708 | 0.20464 | 86.5761 | 0 | 0 | 0 | 0 | 0 | 86.5761 | 130000 | 86.5761 | 457842.5806 | 510.81 | 0
4867 | 7 | 0 | 0.084216 | 0.17625 | 31.5301 | 0 | 0 | 0 | 0 | 0 | 31.5301 | 130000 | 31.5301 | 457874.1107 | 510.81 | 0
4868 | 7 | 1 | 0 | 0.17867 | 7.3078 | 200 | 7.3078 | 180 | 187.3078 | 0 | 0 | 129800 | 187.3078 | 458061.4185 | 330.81 | 0
4869 | 7 | 1 | 0 | 0.18586 | 7.6015 | 200 | 7.6015 | 180 | 187.6015 | 0 | 0 | 129600 | 187.6015 | 458249.02 | 150.81 | 0
4870 | 7 | 0 | 0 | 0.16428 | 6.7189 | 0 | 0 | 0 | 0 | 6.7189 | 0 | 129600 | 0 | 458249.02 | 156.6339 | 0
4871 | 7 | 0 | 0 | 0.098228 | 4.0175 | 0 | 0 | 0 | 0 | 4.0175 | 0 | 129600 | 0 | 458249.02 | 160.1163 | 0
4872 | 7 | 0 | 0 | 0.1231 | 5.0349 | 0 | 0 | 0 | 0 | 5.0349 | 0 | 129600 | 0 | 458249.02 | 164.4806 | 0
4873 | 7 | 0 | 0 | 0.11057 | 4.5222 | 0 | 0 | 0 | 0 | 4.5222 | 0 | 129600 | 0 | 458249.02 | 168.4005 | 0
4874 | 7 | 0 | 0 | 0.096569 | 3.9497 | 0 | 0 | 0 | 0 | 3.9497 | 0 | 129600 | 0 | 458249.02 | 171.824 | 0
4875 | 7 | 0 | 0 | 0.10623 | 4.3449 | 0 | 0 | 0 | 0 | 4.3449 | 0 | 129600 | 0 | 458249.02 | 175.5902 | 0
4876 | 7 | 0 | 0 | 0.1829 | 7.4805 | 0 | 0 | 0 | 0 | 7.4805 | 0 | 129600 | 0 | 458249.02 | 182.0743 | 0
4877 | 7 | 0 | 0 | 0.28778 | 11.77 | 0 | 0 | 0 | 0 | 11.77 | 0 | 129600 | 0 | 458249.02 | 192.2765 | 0
4878 | 7 | 0 | 0 | 0.23807 | 9.7369 | 0 | 0 | 0 | 0 | 9.7369 | 0 | 129600 | 0 | 458249.02 | 200.7165 | 0
4879 | 7 | 0 | 0.085505 | 0.24648 | 34.7748 | 0 | 0 | 0 | 0 | 34.7748 | 0 | 129600 | 0 | 458249.02 | 230.8593 | 0
4880 | 7 | 1 | 0.27494 | 0.2572 | 89.9234 | 200 | 89.9234 | 110.0766 | 200 | 0 | 0 | 129400 | 200 | 458449.02 | 120.7827 | 0
4881 | 7 | 1 | 0.48573 | 0.38041 | 155.8374 | 200 | 155.8374 | 44.1626 | 200 | 0 | 0 | 129200 | 200 | 458649.02 | 76.6202 | 0
4882 | 7 | 0 | 0.68446 | 0.36845 | 212.7425 | 0 | 0 | 0 | 0 | 180 | 32.7425 | 129200 | 32.7425 | 458681.7625 | 232.6442 | 0
4883 | 7 | 0 | 0.84571 | 0.48642 | 264.1355 | 0 | 0 | 0 | 0 | 180 | 84.1355 | 129200 | 84.1355 | 458765.8979 | 388.6682 | 0
4884 | 7 | 0 | 0.95043 | 0.50438 | 295.1137 | 0 | 0 | 0 | 0 | 140.9112 | 154.2025 | 129200 | 154.2025 | 458920.1005 | 510.81 | 0
4885 | 7 | 0 | 0.9867 | 0.46614 | 304.0234 | 0 | 0 | 0 | 0 | 0 | 200 | 129200 | 200 | 459120.1005 | 510.81 | 104.0234
4886 | 7 | 0 | 0.95043 | 0.61344 | 299.5744 | 0 | 0 | 0 | 0 | 0 | 200 | 129200 | 200 | 459320.1005 | 510.81 | 99.5744
4887 | 7 | 0 | 0.84571 | 0.8146 | 277.5582 | 0 | 0 | 0 | 0 | 0 | 200 | 129200 | 200 | 459520.1005 | 510.81 | 77.5582
4888 | 7 | 0 | 0.68446 | 0.82115 | 231.2577 | 0 | 0 | 0 | 0 | 0 | 200 | 129200 | 200 | 459720.1005 | 510.81 | 31.2577
4889 | 7 | 0 | 0.48573 | 0.65683 | 167.1429 | 0 | 0 | 0 | 0 | 0 | 167.1429 | 129200 | 167.1429 | 459887.2434 | 510.81 | 0
4890 | 7 | 0 | 0.27494 | 0.45461 | 97.9977 | 0 | 0 | 0 | 0 | 0 | 97.9977 | 129200 | 97.9977 | 459985.2411 | 510.81 | 0
4891 | 7 | 0 | 0.085505 | 0.46956 | 43.8989 | 0 | 0 | 0 | 0 | 0 | 43.8989 | 129200 | 43.8989 | 460029.14 | 510.81 | 0
4892 | 7 | 1 | 0 | 0.41941 | 17.154 | 200 | 17.154 | 180 | 197.154 | 0 | 0 | 129000 | 197.154 | 460226.294 | 330.81 | 0
4893 | 7 | 1 | 0 | 0.39749 | 16.2574 | 200 | 16.2574 | 180 | 196.2574 | 0 | 0 | 128800 | 196.2574 | 460422.5514 | 150.81 | 0
4894 | 7 | 0 | 0 | 0.38861 | 15.8941 | 0 | 0 | 0 | 0 | 15.8941 | 0 | 128800 | 0 | 460422.5514 | 164.587 | 0
4895 | 7 | 0 | 0 | 0.33943 | 13.8828 | 0 | 0 | 0 | 0 | 13.8828 | 0 | 128800 | 0 | 460422.5514 | 176.6207 | 0
4896 | 7 | 0 | 0 | 0.40152 | 16.4223 | 0 | 0 | 0 | 0 | 16.4223 | 0 | 128800 | 0 | 460422.5514 | 190.8555 | 0
4897 | 7 | 0 | 0 | 0.42692 | 17.4609 | 0 | 0 | 0 | 0 | 17.4609 | 0 | 128800 | 0 | 460422.5514 | 205.9907 | 0
4898 | 7 | 0 | 0 | 0.38753 | 15.8498 | 0 | 0 | 0 | 0 | 15.8498 | 0 | 128800 | 0 | 460422.5514 | 219.7293 | 0
4899 | 7 | 0 | 0 | 0.43818 | 17.9215 | 0 | 0 | 0 | 0 | 17.9215 | 0 | 128800 | 0 | 460422.5514 | 235.2637 | 0
4900 | 7 | 0 | 0 | 0.59751 | 24.4383 | 0 | 0 | 0 | 0 | 24.4383 | 0 | 128800 | 0 | 460422.5514 | 256.4468 | 0
4901 | 7 | 0 | 0 | 0.50005 | 20.452 | 0 | 0 | 0 | 0 | 20.452 | 0 | 128800 | 0 | 460422.5514 | 274.1746 | 0
4902 | 7 | 0 | 0 | 0.65896 | 26.9515 | 0 | 0 | 0 | 0 | 26.9515 | 0 | 128800 | 0 | 460422.5514 | 297.5361 | 0
4903 | 7 | 0 | 0.079801 | 0.74725 | 53.6092 | 0 | 0 | 0 | 0 | 53.6092 | 0 | 128800 | 0 | 460422.5514 | 344.0046 | 0
4904 | 7 | 1 | 0.2566 | 0.6435 | 100.4257 | 200 | 100.4257 | 99.5743 | 200 | 0 | 0 | 128600 | 200 | 460622.5514 | 244.4303 | 0
4905 | 7 | 1 | 0.45332 | 0.98373 | 171.1547 | 200 | 171.1547 | 28.8453 | 200 | 0 | 0 | 128400 | 200 | 460822.5514 | 215.5851 | 0
4906 | 7 | 0 | 0.6388 | 1 | 225.3854 | 0 | 0 | 0 | 0 | 180 | 45.3854 | 128400 | 45.3854 | 460867.9368 | 371.6091 | 0
4907 | 7 | 0 | 0.78929 | 1 | 268.8467 | 0 | 0 | 0 | 0 | 160.5917 | 108.2549 | 128400 | 108.2549 | 460976.1917 | 510.81 | 0
4908 | 7 | 0 | 0.88702 | 0.78356 | 288.2202 | 0 | 0 | 0 | 0 | 0 | 200 | 128400 | 200 | 461176.1917 | 510.81 | 88.2202
4909 | 7 | 0 | 0.92087 | 0.66105 | 292.9844 | 0 | 0 | 0 | 0 | 0 | 200 | 128400 | 200 | 461376.1917 | 510.81 | 92.9844
4910 | 7 | 0 | 0.88702 | 0.69633 | 284.6526 | 0 | 0 | 0 | 0 | 0 | 200 | 128400 | 200 | 461576.1917 | 510.81 | 84.6526
4911 | 7 | 0 | 0.78929 | 0.77951 | 259.8286 | 0 | 0 | 0 | 0 | 0 | 200 | 128400 | 200 | 461776.1917 | 510.81 | 59.8286
4912 | 7 | 0 | 0.6388 | 0.69754 | 213.015 | 0 | 0 | 0 | 0 | 0 | 200 | 128400 | 200 | 461976.1917 | 510.81 | 13.015
4913 | 7 | 0 | 0.45332 | 0.57841 | 154.5774 | 0 | 0 | 0 | 0 | 0 | 154.5774 | 128400 | 154.5774 | 462130.7691 | 510.81 | 0
4914 | 7 | 0 | 0.2566 | 0.50079 | 94.5891 | 0 | 0 | 0 | 0 | 0 | 94.5891 | 128400 | 94.5891 | 462225.3581 | 510.81 | 0
4915 | 7 | 0 | 0.079801 | 0.54665 | 45.4043 | 0 | 0 | 0 | 0 | 0 | 45.4043 | 128400 | 45.4043 | 462270.7624 | 510.81 | 0
4916 | 7 | 1 | 0 | 0.35417 | 14.4854 | 200 | 14.4854 | 180 | 194.4854 | 0 | 0 | 128200 | 194.4854 | 462465.2479 | 330.81 | 0
4917 | 7 | 1 | 0 | 0.35926 | 14.6938 | 200 | 14.6938 | 180 | 194.6938 | 0 | 0 | 128000 | 194.6938 | 462659.9416 | 150.81 | 0
4918 | 7 | 0 | 0 | 0.34555 | 14.1332 | 0 | 0 | 0 | 0 | 14.1332 | 0 | 128000 | 0 | 462659.9416 | 163.0606 | 0
4919 | 7 | 0 | 0 | 0.30095 | 12.3089 | 0 | 0 | 0 | 0 | 12.3089 | 0 | 128000 | 0 | 462659.9416 | 173.7299 | 0
4920 | 7 | 0 | 0 | 0.32451 | 13.2725 | 0 | 0 | 0 | 0 | 13.2725 | 0 | 128000 | 0 | 462659.9416 | 185.2346 | 0
4921 | 7 | 0 | 0 | 0.21142 | 8.6472 | 0 | 0 | 0 | 0 | 8.6472 | 0 | 128000 | 0 | 462659.9416 | 192.73 | 0
4922 | 7 | 0 | 0 | 0.26075 | 10.6648 | 0 | 0 | 0 | 0 | 10.6648 | 0 | 128000 | 0 | 462659.9416 | 201.9743 | 0
4923 | 7 | 0 | 0 | 0.22004 | 8.9994 | 0 | 0 | 0 | 0 | 8.9994 | 0 | 128000 | 0 | 462659.9416 | 209.775 | 0
4924 | 7 | 0 | 0 | 0.24402 | 9.9806 | 0 | 0 | 0 | 0 | 9.9806 | 0 | 128000 | 0 | 462659.9416 | 218.4262 | 0
4925 | 7 | 0 | 0 | 0.26748 | 10.9397 | 0 | 0 | 0 | 0 | 10.9397 | 0 | 128000 | 0 | 462659.9416 | 227.9087 | 0
4926 | 7 | 0 | 0 | 0.25792 | 10.5491 | 0 | 0 | 0 | 0 | 10.5491 | 0 | 128000 | 0 | 462659.9416 | 237.0527 | 0
4927 | 7 | 0 | 0.093275 | 0.22281 | 36.0507 | 0 | 0 | 0 | 0 | 36.0507 | 0 | 128000 | 0 | 462659.9416 | 268.3014 | 0
4928 | 7 | 1 | 0.29993 | 0.34252 | 100.6281 | 200 | 100.6281 | 99.3719 | 200 | 0 | 0 | 127800 | 200 | 462859.9416 | 168.9295 | 0
4929 | 7 | 1 | 0.52987 | 0.40088 | 169.4213 | 200 | 169.4213 | 30.5787 | 200 | 0 | 0 | 127600 | 200 | 463059.9416 | 138.3508 | 0
4930 | 7 | 0 | 0.74666 | 0.46138 | 234.5053 | 0 | 0 | 0 | 0 | 180 | 54.5053 | 127600 | 54.5053 | 463114.447 | 294.3748 | 0
4931 | 7 | 0 | 0.92256 | 0.4557 | 285.0725 | 0 | 0 | 0 | 0 | 180 | 105.0725 | 127600 | 105.0725 | 463219.5194 | 450.3988 | 0
4932 | 7 | 0 | 1 | 0.64674 | 315.2516 | 0 | 0 | 0 | 0 | 69.6945 | 200 | 127600 | 200 | 463419.5194 | 510.81 | 45.5571
4933 | 7 | 0 | 1 | 0.87516 | 324.594 | 0 | 0 | 0 | 0 | 0 | 200 | 127600 | 200 | 463619.5194 | 510.81 | 124.594
4934 | 7 | 0 | 1 | 0.98276 | 328.9949 | 0 | 0 | 0 | 0 | 0 | 200 | 127600 | 200 | 463819.5194 | 510.81 | 128.9949
4935 | 7 | 0 | 0.92256 | 0.79092 | 298.783 | 0 | 0 | 0 | 0 | 0 | 200 | 127600 | 200 | 464019.5194 | 510.81 | 98.783
4936 | 7 | 0 | 0.74666 | 0.52125 | 236.954 | 0 | 0 | 0 | 0 | 0 | 200 | 127600 | 200 | 464219.5194 | 510.81 | 36.954
4937 | 7 | 0 | 0.52987 | 0.66904 | 180.389 | 0 | 0 | 0 | 0 | 0 | 180.389 | 127600 | 180.389 | 464399.9084 | 510.81 | 0
4938 | 7 | 0 | 0.29993 | 0.83274 | 120.6783 | 0 | 0 | 0 | 0 | 0 | 120.6783 | 127600 | 120.6783 | 464520.5867 | 510.81 | 0
4939 | 7 | 0 | 0.093275 | 1 | 67.8378 | 0 | 0 | 0 | 0 | 0 | 67.8378 | 127600 | 67.8378 | 464588.4245 | 510.81 | 0
4940 | 7 | 1 | 0 | 1 | 40.9 | 200 | 40.9 | 159.1 | 200 | 0 | 0 | 127400 | 200 | 464788.4245 | 351.71 | 0
4941 | 7 | 1 | 0 | 1 | 40.9 | 200 | 40.9 | 159.1 | 200 | 0 | 0 | 127200 | 200 | 464988.4245 | 192.61 | 0
4942 | 7 | 0 | 0 | 0.74588 | 30.5065 | 0 | 0 | 0 | 0 | 30.5065 | 0 | 127200 | 0 | 464988.4245 | 219.053 | 0
4943 | 7 | 0 | 0 | 0.72451 | 29.6326 | 0 | 0 | 0 | 0 | 29.6326 | 0 | 127200 | 0 | 464988.4245 | 244.7386 | 0
4944 | 7 | 0 | 0 | 0.66816 | 27.3278 | 0 | 0 | 0 | 0 | 27.3278 | 0 | 127200 | 0 | 464988.4245 | 268.4263 | 0
4945 | 7 | 0 | 0 | 0.55793 | 22.8195 | 0 | 0 | 0 | 0 | 22.8195 | 0 | 127200 | 0 | 464988.4245 | 288.2063 | 0
4946 | 7 | 0 | 0 | 0.84414 | 34.5252 | 0 | 0 | 0 | 0 | 34.5252 | 0 | 127200 | 0 | 464988.4245 | 318.1328 | 0
4947 | 7 | 0 | 0 | 0.78276 | 32.015 | 0 | 0 | 0 | 0 | 32.015 | 0 | 127200 | 0 | 464988.4245 | 345.8834 | 0
4948 | 7 | 0 | 0 | 0.49757 | 20.3505 | 0 | 0 | 0 | 0 | 20.3505 | 0 | 127200 | 0 | 464988.4245 | 363.5232 | 0
4949 | 7 | 0 | 0 | 0.64097 | 26.2155 | 0 | 0 | 0 | 0 | 26.2155 | 0 | 127200 | 0 | 464988.4245 | 386.2468 | 0
4950 | 7 | 0 | 0 | 0.81687 | 33.4101 | 0 | 0 | 0 | 0 | 33.4101 | 0 | 127200 | 0 | 464988.4245 | 415.2066 | 0
4951 | 7 | 0 | 0.067932 | 0.92631 | 57.5047 | 0 | 0 | 0 | 0 | 57.5047 | 0 | 127200 | 0 | 464988.4245 | 465.0517 | 0
4952 | 7 | 1 | 0.21844 | 0.69593 | 91.5479 | 200 | 91.5479 | 108.4521 | 200 | 0 | 0 | 127000 | 200 | 465188.4245 | 356.5995 | 0
4953 | 7 | 1 | 0.3859 | 0.82799 | 145.312 | 200 | 145.312 | 54.688 | 200 | 0 | 0 | 126800 | 200 | 465388.4245 | 301.9115 | 0
4954 | 7 | 0 | 0.54379 | 0.7153 | 186.3013 | 0 | 0 | 0 | 0 | 180 | 6.3013 | 126800 | 6.3013 | 465394.7258 | 457.9355 | 0
4955 | 7 | 0 | 0.67189 | 0.70546 | 222.896 | 0 | 0 | 0 | 0 | 60.9996 | 161.8964 | 126800 | 161.8964 | 465556.6221 | 510.81 | 0
4956 | 7 | 0 | 0.75509 | 0.86103 | 253.2867 | 0 | 0 | 0 | 0 | 0 | 200 | 126800 | 200 | 465756.6221 | 510.81 | 53.2867
4957 | 7 | 0 | 0.7839 | 0.74418 | 256.8281 | 0 | 0 | 0 | 0 | 0 | 200 | 126800 | 200 | 465956.6221 | 510.81 | 56.8281
4958 | 7 | 0 | 0.75509 | 0.68275 | 245.995 | 0 | 0 | 0 | 0 | 0 | 200 | 126800 | 200 | 466156.6221 | 510.81 | 45.995
4959 | 7 | 0 | 0.67189 | 0.72896 | 223.8572 | 0 | 0 | 0 | 0 | 0 | 200 | 126800 | 200 | 466356.6221 | 510.81 | 23.8572
4960 | 7 | 0 | 0.54379 | 0.72581 | 186.7315 | 0 | 0 | 0 | 0 | 0 | 186.7315 | 126800 | 186.7315 | 466543.3536 | 510.81 | 0
4961 | 7 | 0 | 0.3859 | 0.77779 | 143.2591 | 0 | 0 | 0 | 0 | 0 | 143.2591 | 126800 | 143.2591 | 466686.6127 | 510.81 | 0
4962 | 7 | 0 | 0.21844 | 1 | 103.9843 | 0 | 0 | 0 | 0 | 0 | 103.9843 | 126800 | 103.9843 | 466790.5971 | 510.81 | 0
4963 | 7 | 0 | 0.067932 | 0.85049 | 54.4036 | 0 | 0 | 0 | 0 | 0 | 54.4036 | 126800 | 54.4036 | 466845.0007 | 510.81 | 0
4964 | 7 | 1 | 0 | 1 | 40.9 | 200 | 40.9 | 159.1 | 200 | 0 | 0 | 126600 | 200 | 467045.0007 | 351.71 | 0
4965 | 7 | 1 | 0 | 0.71138 | 29.0953 | 200 | 29.0953 | 170.9047 | 200 | 0 | 0 | 126400 | 200 | 467245.0007 | 180.8053 | 0
4966 | 7 | 0 | 0 | 0.42655 | 17.4458 | 0 | 0 | 0 | 0 | 17.4458 | 0 | 126400 | 0 | 467245.0007 | 195.9273 | 0
4967 | 7 | 0 | 0 | 0.51427 | 21.0338 | 0 | 0 | 0 | 0 | 21.0338 | 0 | 126400 | 0 | 467245.0007 | 214.1594 | 0
4968 | 7 | 0 | 0 | 0.68719 | 28.1061 | 0 | 0 | 0 | 0 | 28.1061 | 0 | 126400 | 0 | 467245.0007 | 238.5218 | 0
4969 | 7 | 0 | 0 | 0.81587 | 33.3689 | 0 | 0 | 0 | 0 | 33.3689 | 0 | 126400 | 0 | 467245.0007 | 267.4459 | 0
4970 | 7 | 0 | 0 | 0.83933 | 34.3284 | 0 | 0 | 0 | 0 | 34.3284 | 0 | 126400 | 0 | 467245.0007 | 297.2018 | 0
4971 | 7 | 0 | 0 | 0.74781 | 30.5856 | 0 | 0 | 0 | 0 | 30.5856 | 0 | 126400 | 0 | 467245.0007 | 323.7134 | 0
4972 | 7 | 0 | 0 | 0.75698 | 30.9606 | 0 | 0 | 0 | 0 | 30.9606 | 0 | 126400 | 0 | 467245.0007 | 350.5501 | 0
4973 | 7 | 0 | 0 | 0.77436 | 31.6712 | 0 | 0 | 0 | 0 | 31.6712 | 0 | 126400 | 0 | 467245.0007 | 378.0026 | 0
4974 | 7 | 0 | 0 | 0.85738 | 35.0668 | 0 | 0 | 0 | 0 | 35.0668 | 0 | 126400 | 0 | 467245.0007 | 408.3985 | 0
4975 | 7 | 0 | 0.091205 | 0.95954 | 65.5854 | 0 | 0 | 0 | 0 | 65.5854 | 0 | 126400 | 0 | 467245.0007 | 465.2479 | 0
4976 | 7 | 1 | 0.29327 | 0.92031 | 122.3373 | 200 | 122.3373 | 77.6627 | 200 | 0 | 0 | 126200 | 200 | 467445.0007 | 387.5852 | 0
4977 | 7 | 1 | 0.51811 | 0.53748 | 171.6117 | 200 | 171.6117 | 28.3883 | 200 | 0 | 0 | 126000 | 200 | 467645.0007 | 359.1969 | 0
4978 | 7 | 0 | 0.73009 | 0.58447 | 234.7536 | 0 | 0 | 0 | 0 | 174.9113 | 59.8423 | 126000 | 59.8423 | 467704.843 | 510.81 | 0
4979 | 7 | 0 | 0.90208 | 0.73359 | 290.5247 | 0 | 0 | 0 | 0 | 0 | 200 | 126000 | 200 | 467904.843 | 510.81 | 90.5247
4980 | 7 | 0 | 1 | 0.5645 | 311.8881 | 0 | 0 | 0 | 0 | 0 | 200 | 126000 | 200 | 468104.843 | 510.81 | 111.8881
4981 | 7 | 0 | 1 | 0.46798 | 307.9405 | 0 | 0 | 0 | 0 | 0 | 200 | 126000 | 200 | 468304.843 | 510.81 | 107.9405
4982 | 7 | 0 | 1 | 0.48355 | 308.5772 | 0 | 0 | 0 | 0 | 0 | 200 | 126000 | 200 | 468504.843 | 510.81 | 108.5772
4983 | 7 | 0 | 0.90208 | 0.48277 | 280.2662 | 0 | 0 | 0 | 0 | 0 | 200 | 126000 | 200 | 468704.843 | 510.81 | 80.2662
4984 | 7 | 0 | 0.73009 | 0.36732 | 225.8721 | 0 | 0 | 0 | 0 | 0 | 200 | 126000 | 200 | 468904.843 | 510.81 | 25.8721
4985 | 7 | 0 | 0.51811 | 0.38572 | 165.4048 | 0 | 0 | 0 | 0 | 0 | 165.4048 | 126000 | 165.4048 | 469070.2478 | 510.81 | 0
4986 | 7 | 0 | 0.29327 | 0.39736 | 100.9485 | 0 | 0 | 0 | 0 | 0 | 100.9485 | 126000 | 100.9485 | 469171.1964 | 510.81 | 0
4987 | 7 | 0 | 0.091205 | 0.45002 | 44.746 | 0 | 0 | 0 | 0 | 0 | 44.746 | 126000 | 44.746 | 469215.9423 | 510.81 | 0
4988 | 7 | 1 | 0 | 0.27741 | 11.3461 | 200 | 11.3461 | 180 | 191.3461 | 0 | 0 | 125800 | 191.3461 | 469407.2885 | 330.81 | 0
4989 | 7 | 1 | 0 | 0.30076 | 12.3011 | 200 | 12.3011 | 180 | 192.3011 | 0 | 0 | 125600 | 192.3011 | 469599.5895 | 150.81 | 0
4990 | 7 | 0 | 0 | 0.35026 | 14.3256 | 0 | 0 | 0 | 0 | 14.3256 | 0 | 125600 | 0 | 469599.5895 | 163.2274 | 0
4991 | 7 | 0 | 0 | 0.25007 | 10.228 | 0 | 0 | 0 | 0 | 10.228 | 0 | 125600 | 0 | 469599.5895 | 172.093 | 0
4992 | 7 | 0 | 0 | 0.17158 | 7.0175 | 0 | 0 | 0 | 0 | 7.0175 | 0 | 125600 | 0 | 469599.5895 | 178.1758 | 0
4993 | 7 | 0 | 0 | 0.2367 | 9.681 | 0 | 0 | 0 | 0 | 9.681 | 0 | 125600 | 0 | 469599.5895 | 186.5673 | 0
4994 | 7 | 0 | 0 | 0.22603 | 9.2446 | 0 | 0 | 0 | 0 | 9.2446 | 0 | 125600 | 0 | 469599.5895 | 194.5805 | 0
4995 | 7 | 0 | 0 | 0.30266 | 12.3789 | 0 | 0 | 0 | 0 | 12.3789 | 0 | 125600 | 0 | 469599.5895 | 205.3105 | 0
4996 | 7 | 0 | 0 | 0.27492 | 11.2441 | 0 | 0 | 0 | 0 | 11.2441 | 0 | 125600 | 0 | 469599.5895 | 215.0569 | 0
4997 | 7 | 0 | 0 | 0.38482 | 15.7391 | 0 | 0 | 0 | 0 | 15.7391 | 0 | 125600 | 0 | 469599.5895 | 228.6995 | 0
4998 | 7 | 0 | 0 | 0.59938 | 24.5145 | 0 | 0 | 0 | 0 | 24.5145 | 0 | 125600 | 0 | 469599.5895 | 249.9487 | 0
4999 | 7 | 0 | 0.065072 | 0.48604 | 38.6717 | 0 | 0 | 0 | 0 | 38.6717 | 0 | 125600 | 0 | 469599.5895 | 283.4694 | 0
5000 | 7 | 1 | 0.20924 | 0.52594 | 81.9397 | 200 | 81.9397 | 118.0603 | 200 | 0 | 0 | 125400 | 200 | 469799.5895 | 165.4091 | 0
5001 | 7 | 1 | 0.36966 | 0.70942 | 135.7716 | 200 | 135.7716 | 64.2284 | 200 | 0 | 0 | 125200 | 200 | 469999.5895 | 101.1807 | 0
5002 | 7 | 0 | 0.5209 | 0.66006 | 177.4315 | 0 | 0 | 0 | 0 | 177.4315 | 0 | 125200 | 0 | 469999.5895 | 254.9783 | 0
5003 | 7 | 0 | 0.64361 | 0.48924 | 205.8846 | 0 | 0 | 0 | 0 | 180 | 25.8846 | 125200 | 25.8846 | 470025.4741 | 411.0023 | 0
5004 | 7 | 0 | 0.72331 | 0.61861 | 234.1924 | 0 | 0 | 0 | 0 | 115.145 | 119.0474 | 125200 | 119.0474 | 470144.5216 | 510.81 | 0
5005 | 7 | 0 | 0.75091 | 0.51024 | 237.7308 | 0 | 0 | 0 | 0 | 0 | 200 | 125200 | 200 | 470344.5216 | 510.81 | 37.7308
5006 | 7 | 0 | 0.72331 | 0.53193 | 230.6472 | 0 | 0 | 0 | 0 | 0 | 200 | 125200 | 200 | 470544.5216 | 510.81 | 30.6472
5007 | 7 | 0 | 0.64361 | 0.47057 | 205.121 | 0 | 0 | 0 | 0 | 0 | 200 | 125200 | 200 | 470744.5216 | 510.81 | 5.121
5008 | 7 | 0 | 0.5209 | 0.43878 | 168.381 | 0 | 0 | 0 | 0 | 0 | 168.381 | 125200 | 168.381 | 470912.9026 | 510.81 | 0
5009 | 7 | 0 | 0.36966 | 0.49066 | 126.8243 | 0 | 0 | 0 | 0 | 0 | 126.8243 | 125200 | 126.8243 | 471039.7268 | 510.81 | 0
5010 | 7 | 0 | 0.20924 | 0.49979 | 80.8703 | 0 | 0 | 0 | 0 | 0 | 80.8703 | 125200 | 80.8703 | 471120.5972 | 510.81 | 0
5011 | 7 | 0 | 0.065072 | 0.59931 | 43.3044 | 0 | 0 | 0 | 0 | 0 | 43.3044 | 125200 | 43.3044 | 471163.9016 | 510.81 | 0
5012 | 7 | 1 | 0 | 0.62312 | 25.4854 | 200 | 25.4854 | 174.5146 | 200 | 0 | 0 | 125000 | 200 | 471363.9016 | 336.2954 | 0
5013 | 7 | 1 | 0 | 0.61565 | 25.18 | 200 | 25.18 | 174.82 | 200 | 0 | 0 | 124800 | 200 | 471563.9016 | 161.4755 | 0
5014 | 7 | 0 | 0 | 0.48248 | 19.7334 | 0 | 0 | 0 | 0 | 19.7334 | 0 | 124800 | 0 | 471563.9016 | 178.5804 | 0
5015 | 7 | 0 | 0 | 0.40377 | 16.5141 | 0 | 0 | 0 | 0 | 16.5141 | 0 | 124800 | 0 | 471563.9016 | 192.8948 | 0
5016 | 7 | 0 | 0 | 0.32938 | 13.4717 | 0 | 0 | 0 | 0 | 13.4717 | 0 | 124800 | 0 | 471563.9016 | 204.572 | 0
5017 | 7 | 0 | 0 | 0.40207 | 16.4447 | 0 | 0 | 0 | 0 | 16.4447 | 0 | 124800 | 0 | 471563.9016 | 218.8263 | 0
5018 | 7 | 0 | 0 | 0.34133 | 13.9604 | 0 | 0 | 0 | 0 | 13.9604 | 0 | 124800 | 0 | 471563.9016 | 230.9272 | 0
5019 | 7 | 0 | 0 | 0.16415 | 6.7139 | 0 | 0 | 0 | 0 | 6.7139 | 0 | 124800 | 0 | 471563.9016 | 236.7468 | 0
5020 | 7 | 0 | 0 | 0.20257 | 8.2852 | 0 | 0 | 0 | 0 | 8.2852 | 0 | 124800 | 0 | 471563.9016 | 243.9284 | 0
5021 | 7 | 0 | 0 | 0.18929 | 7.7418 | 0 | 0 | 0 | 0 | 7.7418 | 0 | 124800 | 0 | 471563.9016 | 250.6391 | 0
5022 | 7 | 0 | 0 | 0.22539 | 9.2185 | 0 | 0 | 0 | 0 | 9.2185 | 0 | 124800 | 0 | 471563.9016 | 258.6296 | 0
5023 | 7 | 0 | 0.089109 | 0.19928 | 33.8852 | 0 | 0 | 0 | 0 | 33.8852 | 0 | 124800 | 0 | 471563.9016 | 288.0013 | 0
5024 | 7 | 1 | 0.28653 | 0.23807 | 92.4877 | 200 | 92.4877 | 107.5123 | 200 | 0 | 0 | 124600 | 200 | 471763.9016 | 180.489 | 0
5025 | 7 | 1 | 0.5062 | 0.20987 | 154.7745 | 200 | 154.7745 | 45.2255 | 200 | 0 | 0 | 124400 | 200 | 471963.9016 | 135.2635 | 0
5026 | 7 | 0 | 0.71331 | 0.20241 | 214.2828 | 0 | 0 | 0 | 0 | 180 | 34.2828 | 124400 | 34.2828 | 471998.1844 | 291.2875 | 0
5027 | 7 | 0 | 0.88135 | 0.20938 | 263.0985 | 0 | 0 | 0 | 0 | 180 | 83.0985 | 124400 | 83.0985 | 472081.2829 | 447.3115 | 0
5028 | 7 | 0 | 0.99049 | 0.2138 | 294.7974 | 0 | 0 | 0 | 0 | 73.2563 | 200 | 124400 | 200 | 472281.2829 | 510.81 | 21.5412
5029 | 7 | 0 | 1 | 0.26776 | 299.7512 | 0 | 0 | 0 | 0 | 0 | 200 | 124400 | 200 | 472481.2829 | 510.81 | 99.7512
5030 | 7 | 0 | 0.99049 | 0.30453 | 298.5084 | 0 | 0 | 0 | 0 | 0 | 200 | 124400 | 200 | 472681.2829 | 510.81 | 98.5084
5031 | 7 | 0 | 0.88135 | 0.24784 | 264.6717 | 0 | 0 | 0 | 0 | 0 | 200 | 124400 | 200 | 472881.2829 | 510.81 | 64.6717
5032 | 7 | 0 | 0.71331 | 0.29668 | 218.1382 | 0 | 0 | 0 | 0 | 0 | 200 | 124400 | 200 | 473081.2829 | 510.81 | 18.1382
5033 | 7 | 0 | 0.5062 | 0.22216 | 155.2774 | 0 | 0 | 0 | 0 | 0 | 155.2774 | 124400 | 155.2774 | 473236.5602 | 510.81 | 0
5034 | 7 | 0 | 0.28653 | 0.32359 | 95.9856 | 0 | 0 | 0 | 0 | 0 | 95.9856 | 124400 | 95.9856 | 473332.5458 | 510.81 | 0
5035 | 7 | 0 | 0.089109 | 0.16183 | 32.3535 | 0 | 0 | 0 | 0 | 0 | 32.3535 | 124400 | 32.3535 | 473364.8993 | 510.81 | 0
5036 | 7 | 1 | 0 | 0.28059 | 11.476 | 200 | 11.476 | 180 | 191.476 | 0 | 0 | 124200 | 191.476 | 473556.3753 | 330.81 | 0
5037 | 7 | 1 | 0 | 0.38343 | 15.6821 | 200 | 15.6821 | 180 | 195.6821 | 0 | 0 | 124000 | 195.6821 | 473752.0574 | 150.81 | 0
5038 | 7 | 0 | 0 | 0.3607 | 14.7527 | 0 | 0 | 0 | 0 | 14.7527 | 0 | 124000 | 0 | 473752.0574 | 163.5977 | 0
5039 | 7 | 0 | 0 | 0.34528 | 14.1221 | 0 | 0 | 0 | 0 | 14.1221 | 0 | 124000 | 0 | 473752.0574 | 175.8387 | 0
5040 | 7 | 0 | 0 | 0.3785 | 15.4807 | 0 | 0 | 0 | 0 | 15.4807 | 0 | 124000 | 0 | 473752.0574 | 189.2573 | 0
5041 | 7 | 0 | 0 | 0.35046 | 14.3337 | 0 | 0 | 0 | 0 | 14.3337 | 0 | 124000 | 0 | 473752.0574 | 201.6817 | 0
5042 | 7 | 0 | 0 | 0.3044 | 12.4498 | 0 | 0 | 0 | 0 | 12.4498 | 0 | 124000 | 0 | 473752.0574 | 212.4732 | 0
5043 | 7 | 0 | 0 | 0.24547 | 10.0399 | 0 | 0 | 0 | 0 | 10.0399 | 0 | 124000 | 0 | 473752.0574 | 221.1758 | 0
5044 | 7 | 0 | 0 | 0.25977 | 10.6245 | 0 | 0 | 0 | 0 | 10.6245 | 0 | 124000 | 0 | 473752.0574 | 230.3851 | 0
5045 | 7 | 0 | 0 | 0.18279 | 7.4761 | 0 | 0 | 0 | 0 | 7.4761 | 0 | 124000 | 0 | 473752.0574 | 236.8653 | 0
5046 | 7 | 0 | 0 | 0.23329 | 9.5414 | 0 | 0 | 0 | 0 | 9.5414 | 0 | 124000 | 0 | 473752.0574 | 245.1359 | 0
5047 | 7 | 0 | 0.10068 | 0.37081 | 44.2421 | 0 | 0 | 0 | 0 | 44.2421 | 0 | 124000 | 0 | 473752.0574 | 283.4849 | 0
5048 | 7 | 1 | 0.32374 | 0.42596 | 110.9169 | 200 | 110.9169 | 89.0831 | 200 | 0 | 0 | 123800 | 200 | 473952.0574 | 194.4019 | 0
5049 | 7 | 1 | 0.57193 | 0.55174 | 187.7381 | 200 | 187.7381 | 12.2619 | 200 | 0 | 0 | 123600 | 200 | 474152.0574 | 182.1399 | 0
5050 | 7 | 0 | 0.80593 | 0.46036 | 251.5803 | 0 | 0 | 0 | 0 | 180 | 71.5803 | 123600 | 71.5803 | 474223.6377 | 338.1639 | 0
5051 | 7 | 0 | 0.99579 | 0.35274 | 302.0105 | 0 | 0 | 0 | 0 | 180 | 122.0105 | 123600 | 122.0105 | 474345.6482 | 494.1879 | 0
5052 | 7 | 0 | 1 | 0.46771 | 307.9295 | 0 | 0 | 0 | 0 | 19.1764 | 200 | 123600 | 200 | 474545.6482 | 510.81 | 88.7531
5053 | 7 | 0 | 1 | 0.38784 | 304.6627 | 0 | 0 | 0 | 0 | 0 | 200 | 123600 | 200 | 474745.6482 | 510.81 | 104.6627
5054 | 7 | 0 | 1 | 0.38445 | 304.5242 | 0 | 0 | 0 | 0 | 0 | 200 | 123600 | 200 | 474945.6482 | 510.81 | 104.5242
5055 | 7 | 0 | 0.99579 | 0.45956 | 306.3792 | 0 | 0 | 0 | 0 | 0 | 200 | 123600 | 200 | 475145.6482 | 510.81 | 106.3792
5056 | 7 | 0 | 0.80593 | 0.42562 | 250.1594 | 0 | 0 | 0 | 0 | 0 | 200 | 123600 | 200 | 475345.6482 | 510.81 | 50.1594
5057 | 7 | 0 | 0.57193 | 0.38069 | 180.7422 | 0 | 0 | 0 | 0 | 0 | 180.7422 | 123600 | 180.7422 | 475526.3904 | 510.81 | 0
5058 | 7 | 0 | 0.32374 | 0.42102 | 110.7149 | 0 | 0 | 0 | 0 | 0 | 110.7149 | 123600 | 110.7149 | 475637.1053 | 510.81 | 0
5059 | 7 | 0 | 0.10068 | 0.56176 | 52.0522 | 0 | 0 | 0 | 0 | 0 | 52.0522 | 123600 | 52.0522 | 475689.1575 | 510.81 | 0
5060 | 7 | 1 | 0 | 0.42804 | 17.5068 | 200 | 17.5068 | 180 | 197.5068 | 0 | 0 | 123400 | 197.5068 | 475886.6643 | 330.81 | 0
5061 | 7 | 1 | 0 | 0.35633 | 14.5739 | 200 | 14.5739 | 180 | 194.5739 | 0 | 0 | 123200 | 194.5739 | 476081.2382 | 150.81 | 0
5062 | 7 | 0 | 0 | 0.38303 | 15.6658 | 0 | 0 | 0 | 0 | 15.6658 | 0 | 123200 | 0 | 476081.2382 | 164.3891 | 0
5063 | 7 | 0 | 0 | 0.33379 | 13.652 | 0 | 0 | 0 | 0 | 13.652 | 0 | 123200 | 0 | 476081.2382 | 176.2226 | 0
5064 | 7 | 0 | 0 | 0.35157 | 14.3793 | 0 | 0 | 0 | 0 | 14.3793 | 0 | 123200 | 0 | 476081.2382 | 188.6867 | 0
5065 | 7 | 0 | 0 | 0.33804 | 13.8258 | 0 | 0 | 0 | 0 | 13.8258 | 0 | 123200 | 0 | 476081.2382 | 200.6709 | 0
5066 | 7 | 0 | 0 | 0.31075 | 12.7098 | 0 | 0 | 0 | 0 | 12.7098 | 0 | 123200 | 0 | 476081.2382 | 211.6877 | 0
5067 | 7 | 0 | 0 | 0.42005 | 17.18 | 0 | 0 | 0 | 0 | 17.18 | 0 | 123200 | 0 | 476081.2382 | 226.5794 | 0
5068 | 7 | 0 | 0 | 0.27609 | 11.2922 | 0 | 0 | 0 | 0 | 11.2922 | 0 | 123200 | 0 | 476081.2382 | 236.3674 | 0
5069 | 7 | 0 | 0 | 0.25636 | 10.4853 | 0 | 0 | 0 | 0 | 10.4853 | 0 | 123200 | 0 | 476081.2382 | 245.4561 | 0
5070 | 7 | 0 | 0 | 0.30492 | 12.4712 | 0 | 0 | 0 | 0 | 12.4712 | 0 | 123200 | 0 | 476081.2382 | 256.2661 | 0
5071 | 7 | 0 | 0.08483 | 0.38794 | 40.3657 | 0 | 0 | 0 | 0 | 40.3657 | 0 | 123200 | 0 | 476081.2382 | 291.2551 | 0
5072 | 7 | 1 | 0.27277 | 0.45424 | 97.3554 | 200 | 97.3554 | 102.6446 | 200 | 0 | 0 | 123000 | 200 | 476281.2382 | 188.6105 | 0
5073 | 7 | 1 | 0.4819 | 0.54613 | 161.508 | 200 | 161.508 | 38.492 | 200 | 0 | 0 | 122800 | 200 | 476481.2382 | 150.1185 | 0
5074 | 7 | 0 | 0.67906 | 0.42885 | 213.6523 | 0 | 0 | 0 | 0 | 180 | 33.6523 | 122800 | 33.6523 | 476514.8905 | 306.1425 | 0
5075 | 7 | 0 | 0.83903 | 0.59593 | 266.6862 | 0 | 0 | 0 | 0 | 180 | 86.6862 | 122800 | 86.6862 | 476601.5767 | 462.1665 | 0
5076 | 7 | 0 | 0.94293 | 0.8014 | 305.0949 | 0 | 0 | 0 | 0 | 56.1184 | 200 | 122800 | 200 | 476801.5767 | 510.81 | 48.9765
5077 | 7 | 0 | 0.97891 | 0.82502 | 316.4515 | 0 | 0 | 0 | 0 | 0 | 200 | 122800 | 200 | 477001.5767 | 510.81 | 116.4515
5078 | 7 | 0 | 0.94293 | 0.84242 | 306.7726 | 0 | 0 | 0 | 0 | 0 | 200 | 122800 | 200 | 477201.5767 | 510.81 | 106.7726
5079 | 7 | 0 | 0.83903 | 0.90321 | 279.2541 | 0 | 0 | 0 | 0 | 0 | 200 | 122800 | 200 | 477401.5767 | 510.81 | 79.2541
5080 | 7 | 0 | 0.67906 | 0.68075 | 223.9548 | 0 | 0 | 0 | 0 | 0 | 200 | 122800 | 200 | 477601.5767 | 510.81 | 23.9548
5081 | 7 | 0 | 0.4819 | 0.54177 | 161.3298 | 0 | 0 | 0 | 0 | 0 | 161.3298 | 122800 | 161.3298 | 477762.9065 | 510.81 | 0
5082 | 7 | 0 | 0.27277 | 0.81747 | 112.2116 | 0 | 0 | 0 | 0 | 0 | 112.2116 | 122800 | 112.2116 | 477875.1181 | 510.81 | 0
5083 | 7 | 0 | 0.08483 | 0.566 | 47.6485 | 0 | 0 | 0 | 0 | 0 | 47.6485 | 122800 | 47.6485 | 477922.7666 | 510.81 | 0
5084 | 7 | 1 | 0 | 0.54429 | 22.2614 | 200 | 22.2614 | 177.7386 | 200 | 0 | 0 | 122600 | 200 | 478122.7666 | 333.0714 | 0
5085 | 7 | 1 | 0 | 0.45608 | 18.6538 | 200 | 18.6538 | 180 | 198.6538 | 0 | 0 | 122400 | 198.6538 | 478321.4204 | 153.0714 | 0
5086 | 7 | 0 | 0 | 0.5348 | 21.8732 | 0 | 0 | 0 | 0 | 21.8732 | 0 | 122400 | 0 | 478321.4204 | 172.0311 | 0
5087 | 7 | 0 | 0 | 0.50414 | 20.6193 | 0 | 0 | 0 | 0 | 20.6193 | 0 | 122400 | 0 | 478321.4204 | 189.904 | 0
5088 | 7 | 0 | 0 | 0.55699 | 22.7811 | 0 | 0 | 0 | 0 | 22.7811 | 0 | 122400 | 0 | 478321.4204 | 209.6506 | 0
5089 | 8 | 0 | 0 | 0.46419 | 18.9854 | 0 | 0 | 0 | 0 | 18.9854 | 0 | 122400 | 0 | 478321.4204 | 226.1071 | 0
5090 | 8 | 0 | 0 | 0.50823 | 20.7868 | 0 | 0 | 0 | 0 | 20.7868 | 0 | 122400 | 0 | 478321.4204 | 244.1251 | 0
5091 | 8 | 0 | 0 | 0.53685 | 21.9572 | 0 | 0 | 0 | 0 | 21.9572 | 0 | 122400 | 0 | 478321.4204 | 263.1576 | 0
5092 | 8 | 0 | 0 | 0.58147 | 23.7819 | 0 | 0 | 0 | 0 | 23.7819 | 0 | 122400 | 0 | 478321.4204 | 283.7718 | 0
5093 | 8 | 0 | 0 | 0.75688 | 30.9564 | 0 | 0 | 0 | 0 | 30.9564 | 0 | 122400 | 0 | 478321.4204 | 310.6048 | 0
5094 | 8 | 0 | 0 | 0.96748 | 39.57 | 0 | 0 | 0 | 0 | 39.57 | 0 | 122400 | 0 | 478321.4204 | 344.904 | 0
5095 | 8 | 0 | 0.045947 | 1 | 54.1695 | 0 | 0 | 0 | 0 | 54.1695 | 0 | 122400 | 0 | 478321.4204 | 391.8581 | 0
5096 | 8 | 1 | 0.21737 | 1 | 103.677 | 200 | 103.677 | 96.323 | 200 | 0 | 0 | 122200 | 200 | 478521.4204 | 295.5352 | 0
5097 | 8 | 1 | 0.41856 | 1 | 161.7801 | 200 | 161.7801 | 38.2199 | 200 | 0 | 0 | 122000 | 200 | 478721.4204 | 257.3153 | 0
5098 | 8 | 0 | 0.61231 | 1 | 217.734 | 0 | 0 | 0 | 0 | 180 | 37.734 | 122000 | 37.734 | 478759.1544 | 413.3393 | 0
5099 | 8 | 0 | 0.77136 | 1 | 263.6673 | 0 | 0 | 0 | 0 | 112.4489 | 151.2184 | 122000 | 151.2184 | 478910.3728 | 510.81 | 0
5100 | 8 | 0 | 0.87534 | 0.87839 | 288.7238 | 0 | 0 | 0 | 0 | 0 | 200 | 122000 | 200 | 479110.3728 | 510.81 | 88.7238
5101 | 8 | 0 | 0.91146 | 0.69184 | 291.5257 | 0 | 0 | 0 | 0 | 0 | 200 | 122000 | 200 | 479310.3728 | 510.81 | 91.5257
5102 | 8 | 0 | 0.87534 | 0.79396 | 285.2706 | 0 | 0 | 0 | 0 | 0 | 200 | 122000 | 200 | 479510.3728 | 510.81 | 85.2706
5103 | 8 | 0 | 0.77136 | 0.92495 | 260.5976 | 0 | 0 | 0 | 0 | 0 | 200 | 122000 | 200 | 479710.3728 | 510.81 | 60.5976
5104 | 8 | 0 | 0.61231 | 0.7424 | 207.1979 | 0 | 0 | 0 | 0 | 0 | 200 | 122000 | 200 | 479910.3728 | 510.81 | 7.1979
5105 | 8 | 0 | 0.41856 | 0.66382 | 148.0305 | 0 | 0 | 0 | 0 | 0 | 148.0305 | 122000 | 148.0305 | 480058.4033 | 510.81 | 0
5106 | 8 | 0 | 0.21737 | 0.66399 | 89.934 | 0 | 0 | 0 | 0 | 0 | 89.934 | 122000 | 89.934 | 480148.3373 | 510.81 | 0
5107 | 8 | 0 | 0.045947 | 0.51282 | 34.2436 | 0 | 0 | 0 | 0 | 0 | 34.2436 | 122000 | 34.2436 | 480182.581 | 510.81 | 0
5108 | 8 | 1 | 0 | 0.46219 | 18.9037 | 200 | 18.9037 | 180 | 198.9037 | 0 | 0 | 121800 | 198.9037 | 480381.4847 | 330.81 | 0
5109 | 8 | 1 | 0 | 0.52616 | 21.5199 | 200 | 21.5199 | 178.4801 | 200 | 0 | 0 | 121600 | 200 | 480581.4847 | 152.3299 | 0
5110 | 8 | 0 | 0 | 0.55578 | 22.7315 | 0 | 0 | 0 | 0 | 22.7315 | 0 | 121600 | 0 | 480581.4847 | 172.0336 | 0
5111 | 8 | 0 | 0 | 0.46911 | 19.1867 | 0 | 0 | 0 | 0 | 19.1867 | 0 | 121600 | 0 | 480581.4847 | 188.6646 | 0
5112 | 8 | 0 | 0 | 0.35174 | 14.386 | 0 | 0 | 0 | 0 | 14.386 | 0 | 121600 | 0 | 480581.4847 | 201.1345 | 0
5113 | 8 | 0 | 0 | 0.33386 | 13.6549 | 0 | 0 | 0 | 0 | 13.6549 | 0 | 121600 | 0 | 480581.4847 | 212.9705 | 0
5114 | 8 | 0 | 0 | 0.36723 | 15.0196 | 0 | 0 | 0 | 0 | 15.0196 | 0 | 121600 | 0 | 480581.4847 | 225.9896 | 0
5115 | 8 | 0 | 0 | 0.41166 | 16.8369 | 0 | 0 | 0 | 0 | 16.8369 | 0 | 121600 | 0 | 480581.4847 | 240.5838 | 0
5116 | 8 | 0 | 0 | 0.42108 | 17.222 | 0 | 0 | 0 | 0 | 17.222 | 0 | 121600 | 0 | 480581.4847 | 255.5119 | 0
5117 | 8 | 0 | 0 | 0.32156 | 13.1519 | 0 | 0 | 0 | 0 | 13.1519 | 0 | 121600 | 0 | 480581.4847 | 266.9119 | 0
5118 | 8 | 0 | 0 | 0.33424 | 13.6703 | 0 | 0 | 0 | 0 | 13.6703 | 0 | 121600 | 0 | 480581.4847 | 278.7613 | 0
5119 | 8 | 0 | 0.04399 | 0.39856 | 29.0053 | 0 | 0 | 0 | 0 | 29.0053 | 0 | 121600 | 0 | 480581.4847 | 303.9031 | 0
5120 | 8 | 1 | 0.20811 | 0.55056 | 82.6216 | 200 | 82.6216 | 117.3784 | 200 | 0 | 0 | 121400 | 200 | 480781.4847 | 186.5247 | 0
5121 | 8 | 1 | 0.40074 | 0.39345 | 131.8244 | 200 | 131.8244 | 68.1756 | 200 | 0 | 0 | 121200 | 200 | 480981.4847 | 118.3491 | 0
5122 | 8 | 0 | 0.58623 | 0.41375 | 186.2257 | 0 | 0 | 0 | 0 | 180 | 6.2257 | 121200 | 6.2257 | 480987.7104 | 274.3731 | 0
5123 | 8 | 0 | 0.73851 | 0.43312 | 230.995 | 0 | 0 | 0 | 0 | 180 | 50.995 | 121200 | 50.995 | 481038.7054 | 430.3971 | 0
5124 | 8 | 0 | 0.83806 | 0.43438 | 259.798 | 0 | 0 | 0 | 0 | 92.7699 | 167.0281 | 121200 | 167.0281 | 481205.7335 | 510.81 | 0
5125 | 8 | 0 | 0.87264 | 0.41791 | 269.1119 | 0 | 0 | 0 | 0 | 0 | 200 | 121200 | 200 | 481405.7335 | 510.81 | 69.1119
5126 | 8 | 0 | 0.83806 | 0.52189 | 263.3775 | 0 | 0 | 0 | 0 | 0 | 200 | 121200 | 200 | 481605.7335 | 510.81 | 63.3775
5127 | 8 | 0 | 0.73851 | 0.51391 | 234.2995 | 0 | 0 | 0 | 0 | 0 | 200 | 121200 | 200 | 481805.7335 | 510.81 | 34.2995
5128 | 8 | 0 | 0.58623 | 0.376 | 184.6815 | 0 | 0 | 0 | 0 | 0 | 184.6815 | 121200 | 184.6815 | 481990.415 | 510.81 | 0
5129 | 8 | 0 | 0.40074 | 0.34541 | 129.8597 | 0 | 0 | 0 | 0 | 0 | 129.8597 | 121200 | 129.8597 | 482120.2747 | 510.81 | 0
5130 | 8 | 0 | 0.20811 | 0.63193 | 85.9495 | 0 | 0 | 0 | 0 | 0 | 85.9495 | 121200 | 85.9495 | 482206.2243 | 510.81 | 0
5131 | 8 | 0 | 0.04399 | 0.50704 | 33.4422 | 0 | 0 | 0 | 0 | 0 | 33.4422 | 121200 | 33.4422 | 482239.6665 | 510.81 | 0
5132 | 8 | 1 | 0 | 0.44207 | 18.0806 | 200 | 18.0806 | 180 | 198.0806 | 0 | 0 | 121000 | 198.0806 | 482437.7471 | 330.81 | 0
5133 | 8 | 1 | 0 | 0.40239 | 16.4578 | 200 | 16.4578 | 180 | 196.4578 | 0 | 0 | 120800 | 196.4578 | 482634.2049 | 150.81 | 0
5134 | 8 | 0 | 0 | 0.38527 | 15.7576 | 0 | 0 | 0 | 0 | 15.7576 | 0 | 120800 | 0 | 482634.2049 | 164.4687 | 0
5135 | 8 | 0 | 0 | 0.34722 | 14.2014 | 0 | 0 | 0 | 0 | 14.2014 | 0 | 120800 | 0 | 482634.2049 | 176.7784 | 0
5136 | 8 | 0 | 0 | 0.31176 | 12.7511 | 0 | 0 | 0 | 0 | 12.7511 | 0 | 120800 | 0 | 482634.2049 | 187.8311 | 0
5137 | 8 | 0 | 0 | 0.4614 | 18.8713 | 0 | 0 | 0 | 0 | 18.8713 | 0 | 120800 | 0 | 482634.2049 | 204.1887 | 0
5138 | 8 | 0 | 0 | 0.4824 | 19.7303 | 0 | 0 | 0 | 0 | 19.7303 | 0 | 120800 | 0 | 482634.2049 | 221.2909 | 0
5139 | 8 | 0 | 0 | 0.40568 | 16.5925 | 0 | 0 | 0 | 0 | 16.5925 | 0 | 120800 | 0 | 482634.2049 | 235.6733 | 0
5140 | 8 | 0 | 0 | 0.34805 | 14.2352 | 0 | 0 | 0 | 0 | 14.2352 | 0 | 120800 | 0 | 482634.2049 | 248.0124 | 0
5141 | 8 | 0 | 0 | 0.51354 | 21.0039 | 0 | 0 | 0 | 0 | 21.0039 | 0 | 120800 | 0 | 482634.2049 | 266.2186 | 0
5142 | 8 | 0 | 0 | 0.57949 | 23.7013 | 0 | 0 | 0 | 0 | 23.7013 | 0 | 120800 | 0 | 482634.2049 | 286.763 | 0
5143 | 8 | 0 | 0.053831 | 0.70936 | 44.5591 | 0 | 0 | 0 | 0 | 44.5591 | 0 | 120800 | 0 | 482634.2049 | 325.3867 | 0
5144 | 8 | 1 | 0.25467 | 1 | 114.4493 | 200 | 114.4493 | 85.5507 | 200 | 0 | 0 | 120600 | 200 | 482834.2049 | 239.836 | 0
5145 | 8 | 1 | 0.49038 | 0.56263 | 164.6341 | 200 | 164.6341 | 35.3659 | 200 | 0 | 0 | 120400 | 200 | 483034.2049 | 204.4701 | 0
5146 | 8 | 0 | 0.71737 | 0.60559 | 231.9463 | 0 | 0 | 0 | 0 | 180 | 51.9463 | 120400 | 51.9463 | 483086.1512 | 360.4941 | 0
5147 | 8 | 0 | 0.90372 | 0.71372 | 290.1841 | 0 | 0 | 0 | 0 | 173.4147 | 116.7694 | 120400 | 116.7694 | 483202.9205 | 510.81 | 0
5148 | 8 | 0 | 1 | 0.62001 | 314.1583 | 0 | 0 | 0 | 0 | 0 | 200 | 120400 | 200 | 483402.9205 | 510.81 | 114.1583
5149 | 8 | 0 | 1 | 0.80895 | 321.8863 | 0 | 0 | 0 | 0 | 0 | 200 | 120400 | 200 | 483602.9205 | 510.81 | 121.8863
5150 | 8 | 0 | 1 | 0.60893 | 313.7054 | 0 | 0 | 0 | 0 | 0 | 200 | 120400 | 200 | 483802.9205 | 510.81 | 113.7054
5151 | 8 | 0 | 0.90372 | 0.67794 | 288.7206 | 0 | 0 | 0 | 0 | 0 | 200 | 120400 | 200 | 484002.9205 | 510.81 | 88.7206
5152 | 8 | 0 | 0.71737 | 0.63004 | 232.9463 | 0 | 0 | 0 | 0 | 0 | 200 | 120400 | 200 | 484202.9205 | 510.81 | 32.9463
5153 | 8 | 0 | 0.49038 | 0.85352 | 176.5311 | 0 | 0 | 0 | 0 | 0 | 176.5311 | 120400 | 176.5311 | 484379.4516 | 510.81 | 0
5154 | 8 | 0 | 0.25467 | 0.7126 | 102.6946 | 0 | 0 | 0 | 0 | 0 | 102.6946 | 120400 | 102.6946 | 484482.1462 | 510.81 | 0
5155 | 8 | 0 | 0.053831 | 0.73572 | 45.6373 | 0 | 0 | 0 | 0 | 0 | 45.6373 | 120400 | 45.6373 | 484527.7835 | 510.81 | 0
5156 | 8 | 1 | 0 | 0.69729 | 28.519 | 200 | 28.519 | 171.481 | 200 | 0 | 0 | 120200 | 200 | 484727.7835 | 339.329 | 0
5157 | 8 | 1 | 0 | 0.70434 | 28.8075 | 200 | 28.8075 | 171.1925 | 200 | 0 | 0 | 120000 | 200 | 484927.7835 | 168.1365 | 0
5158 | 8 | 0 | 0 | 0.59984 | 24.5333 | 0 | 0 | 0 | 0 | 24.5333 | 0 | 120000 | 0 | 484927.7835 | 189.402 | 0
5159 | 8 | 0 | 0 | 0.66907 | 27.3652 | 0 | 0 | 0 | 0 | 27.3652 | 0 | 120000 | 0 | 484927.7835 | 213.1221 | 0
5160 | 8 | 0 | 0 | 0.67266 | 27.5117 | 0 | 0 | 0 | 0 | 27.5117 | 0 | 120000 | 0 | 484927.7835 | 236.9692 | 0
5161 | 8 | 0 | 0 | 0.49734 | 20.3412 | 0 | 0 | 0 | 0 | 20.3412 | 0 | 120000 | 0 | 484927.7835 | 254.601 | 0
5162 | 8 | 0 | 0 | 0.6555 | 26.8101 | 0 | 0 | 0 | 0 | 26.8101 | 0 | 120000 | 0 | 484927.7835 | 277.84 | 0
5163 | 8 | 0 | 0 | 0.82717 | 33.831 | 0 | 0 | 0 | 0 | 33.831 | 0 | 120000 | 0 | 484927.7835 | 307.1648 | 0
5164 | 8 | 0 | 0 | 0.9107 | 37.2478 | 0 | 0 | 0 | 0 | 37.2478 | 0 | 120000 | 0 | 484927.7835 | 339.4512 | 0
5165 | 8 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 120000 | 0 | 484927.7835 | 374.9033 | 0
5166 | 8 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 120000 | 0 | 484927.7835 | 410.3554 | 0
5167 | 8 | 0 | 0.05586 | 1 | 57.0324 | 0 | 0 | 0 | 0 | 57.0324 | 0 | 120000 | 0 | 484927.7835 | 459.7911 | 0
5168 | 8 | 1 | 0.26427 | 1 | 117.2218 | 200 | 117.2218 | 82.7782 | 200 | 0 | 0 | 119800 | 200 | 485127.7835 | 377.0128 | 0
5169 | 8 | 1 | 0.50887 | 1 | 187.8611 | 200 | 187.8611 | 12.1389 | 200 | 0 | 0 | 119600 | 200 | 485327.7835 | 364.8739 | 0
5170 | 8 | 0 | 0.74442 | 1 | 255.8873 | 0 | 0 | 0 | 0 | 168.3619 | 87.5254 | 119600 | 87.5254 | 485415.309 | 510.81 | 0
5171 | 8 | 0 | 0.93778 | 1 | 311.7312 | 0 | 0 | 0 | 0 | 0 | 200 | 119600 | 200 | 485615.309 | 510.81 | 111.7312
5172 | 8 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 0 | 200 | 119600 | 200 | 485815.309 | 510.81 | 129.7
5173 | 8 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 0 | 200 | 119600 | 200 | 486015.309 | 510.81 | 129.7
5174 | 8 | 0 | 1 | 0.68461 | 316.8006 | 0 | 0 | 0 | 0 | 0 | 200 | 119600 | 200 | 486215.309 | 510.81 | 116.8006
5175 | 8 | 0 | 0.93778 | 0.60423 | 295.5441 | 0 | 0 | 0 | 0 | 0 | 200 | 119600 | 200 | 486415.309 | 510.81 | 95.5441
5176 | 8 | 0 | 0.74442 | 0.88182 | 251.0537 | 0 | 0 | 0 | 0 | 0 | 200 | 119600 | 200 | 486615.309 | 510.81 | 51.0537
5177 | 8 | 0 | 0.50887 | 0.80656 | 179.9495 | 0 | 0 | 0 | 0 | 0 | 179.9495 | 119600 | 179.9495 | 486795.2584 | 510.81 | 0
5178 | 8 | 0 | 0.26427 | 0.88059 | 112.3379 | 0 | 0 | 0 | 0 | 0 | 112.3379 | 119600 | 112.3379 | 486907.5963 | 510.81 | 0
5179 | 8 | 0 | 0.05586 | 1 | 57.0324 | 0 | 0 | 0 | 0 | 0 | 57.0324 | 119600 | 57.0324 | 486964.6287 | 510.81 | 0
5180 | 8 | 1 | 0 | 1 | 40.9 | 200 | 40.9 | 159.1 | 200 | 0 | 0 | 119400 | 200 | 487164.6287 | 351.71 | 0
5181 | 8 | 1 | 0 | 1 | 40.9 | 200 | 40.9 | 159.1 | 200 | 0 | 0 | 119200 | 200 | 487364.6287 | 192.61 | 0
5182 | 8 | 0 | 0 | 0.80484 | 32.9178 | 0 | 0 | 0 | 0 | 32.9178 | 0 | 119200 | 0 | 487364.6287 | 221.1432 | 0
5183 | 8 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 119200 | 0 | 487364.6287 | 256.5953 | 0
5184 | 8 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 119200 | 0 | 487364.6287 | 292.0474 | 0
5185 | 8 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 119200 | 0 | 487364.6287 | 327.4995 | 0
5186 | 8 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 119200 | 0 | 487364.6287 | 362.9517 | 0
5187 | 8 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 119200 | 0 | 487364.6287 | 398.4038 | 0
5188 | 8 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 119200 | 0 | 487364.6287 | 433.8559 | 0
5189 | 8 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 119200 | 0 | 487364.6287 | 469.308 | 0
5190 | 8 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 119200 | 0 | 487364.6287 | 504.7601 | 0
5191 | 8 | 0 | 0.047433 | 0.87727 | 49.5791 | 0 | 0 | 0 | 0 | 6.9795 | 42.5995 | 119200 | 42.5995 | 487407.2282 | 510.81 | 0
5192 | 8 | 1 | 0.2244 | 0.77043 | 96.3186 | 200 | 96.3186 | 103.6814 | 200 | 0 | 0 | 119000 | 200 | 487607.2282 | 407.1286 | 0
5193 | 8 | 1 | 0.4321 | 1 | 165.6905 | 200 | 165.6905 | 34.3095 | 200 | 0 | 0 | 118800 | 200 | 487807.2282 | 372.8191 | 0
5194 | 8 | 0 | 0.63211 | 0.83792 | 216.8252 | 0 | 0 | 0 | 0 | 159.1958 | 57.6294 | 118800 | 57.6294 | 487864.8577 | 510.81 | 0
5195 | 8 | 0 | 0.79631 | 1 | 270.8735 | 0 | 0 | 0 | 0 | 0 | 200 | 118800 | 200 | 488064.8577 | 510.81 | 70.8735
5196 | 8 | 0 | 0.90365 | 1 | 301.8753 | 0 | 0 | 0 | 0 | 0 | 200 | 118800 | 200 | 488264.8577 | 510.81 | 101.8753
5197 | 8 | 0 | 0.94094 | 1 | 312.644 | 0 | 0 | 0 | 0 | 0 | 200 | 118800 | 200 | 488464.8577 | 510.81 | 112.644
5198 | 8 | 0 | 0.90365 | 1 | 301.8753 | 0 | 0 | 0 | 0 | 0 | 200 | 118800 | 200 | 488664.8577 | 510.81 | 101.8753
5199 | 8 | 0 | 0.79631 | 0.94344 | 268.5603 | 0 | 0 | 0 | 0 | 0 | 200 | 118800 | 200 | 488864.8577 | 510.81 | 68.5603
5200 | 8 | 0 | 0.63211 | 0.96815 | 222.1516 | 0 | 0 | 0 | 0 | 0 | 200 | 118800 | 200 | 489064.8577 | 510.81 | 22.1516
5201 | 8 | 0 | 0.4321 | 0.77788 | 156.6056 | 0 | 0 | 0 | 0 | 0 | 156.6056 | 118800 | 156.6056 | 489221.4633 | 510.81 | 0
5202 | 8 | 0 | 0.2244 | 1 | 105.7079 | 0 | 0 | 0 | 0 | 0 | 105.7079 | 118800 | 105.7079 | 489327.1712 | 510.81 | 0
5203 | 8 | 0 | 0.047433 | 1 | 54.5987 | 0 | 0 | 0 | 0 | 0 | 54.5987 | 118800 | 54.5987 | 489381.7698 | 510.81 | 0
5204 | 8 | 1 | 0 | 0.8069 | 33.0021 | 200 | 33.0021 | 166.9979 | 200 | 0 | 0 | 118600 | 200 | 489581.7698 | 343.8121 | 0
5205 | 8 | 1 | 0 | 0.80087 | 32.7555 | 200 | 32.7555 | 167.2445 | 200 | 0 | 0 | 118400 | 200 | 489781.7698 | 176.5676 | 0
5206 | 8 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 118400 | 0 | 489781.7698 | 212.0197 | 0
5207 | 8 | 0 | 0 | 0.95981 | 39.2561 | 0 | 0 | 0 | 0 | 39.2561 | 0 | 118400 | 0 | 489781.7698 | 246.0469 | 0
5208 | 8 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 118400 | 0 | 489781.7698 | 281.4991 | 0
5209 | 8 | 0 | 0 | 0.95988 | 39.2593 | 0 | 0 | 0 | 0 | 39.2593 | 0 | 118400 | 0 | 489781.7698 | 315.529 | 0
5210 | 8 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 118400 | 0 | 489781.7698 | 350.9811 | 0
5211 | 8 | 0 | 0 | 0.79589 | 32.5518 | 0 | 0 | 0 | 0 | 32.5518 | 0 | 118400 | 0 | 489781.7698 | 379.197 | 0
5212 | 8 | 0 | 0 | 0.83661 | 34.2173 | 0 | 0 | 0 | 0 | 34.2173 | 0 | 118400 | 0 | 489781.7698 | 408.8565 | 0
5213 | 8 | 0 | 0 | 0.70139 | 28.6866 | 0 | 0 | 0 | 0 | 28.6866 | 0 | 118400 | 0 | 489781.7698 | 433.7221 | 0
5214 | 8 | 0 | 0 | 0.50691 | 20.7325 | 0 | 0 | 0 | 0 | 20.7325 | 0 | 118400 | 0 | 489781.7698 | 451.6931 | 0
5215 | 8 | 0 | 0.04247 | 0.43478 | 30.0477 | 0 | 0 | 0 | 0 | 30.0477 | 0 | 118400 | 0 | 489781.7698 | 477.7384 | 0
5216 | 8 | 1 | 0.20092 | 0.40424 | 74.5604 | 200 | 74.5604 | 125.4396 | 200 | 0 | 0 | 118200 | 200 | 489981.7698 | 352.2988 | 0
5217 | 8 | 1 | 0.38689 | 0.42418 | 129.0828 | 200 | 129.0828 | 70.9172 | 200 | 0 | 0 | 118000 | 200 | 490181.7698 | 281.3815 | 0
5218 | 8 | 0 | 0.56598 | 0.47868 | 183.0318 | 0 | 0 | 0 | 0 | 180 | 3.0318 | 118000 | 3.0318 | 490184.8016 | 437.4055 | 0
5219 | 8 | 0 | 0.71299 | 0.46979 | 225.1263 | 0 | 0 | 0 | 0 | 84.6844 | 140.4419 | 118000 | 140.4419 | 490325.2435 | 510.81 | 0
5220 | 8 | 0 | 0.80911 | 0.47137 | 252.949 | 0 | 0 | 0 | 0 | 0 | 200 | 118000 | 200 | 490525.2435 | 510.81 | 52.949
5221 | 8 | 0 | 0.84249 | 0.52143 | 264.6383 | 0 | 0 | 0 | 0 | 0 | 200 | 118000 | 200 | 490725.2435 | 510.81 | 64.6383
5222 | 8 | 0 | 0.80911 | 0.72418 | 263.2887 | 0 | 0 | 0 | 0 | 0 | 200 | 118000 | 200 | 490925.2435 | 510.81 | 63.2887
5223 | 8 | 0 | 0.71299 | 0.73095 | 235.8077 | 0 | 0 | 0 | 0 | 0 | 200 | 118000 | 200 | 491125.2435 | 510.81 | 35.8077
5224 | 8 | 0 | 0.56598 | 0.43036 | 181.0556 | 0 | 0 | 0 | 0 | 0 | 181.0556 | 118000 | 181.0556 | 491306.2991 | 510.81 | 0
5225 | 8 | 0 | 0.38689 | 0.34269 | 125.7497 | 0 | 0 | 0 | 0 | 0 | 125.7497 | 118000 | 125.7497 | 491432.0488 | 510.81 | 0
5226 | 8 | 0 | 0.20092 | 0.39325 | 74.111 | 0 | 0 | 0 | 0 | 0 | 74.111 | 118000 | 74.111 | 491506.1598 | 510.81 | 0
5227 | 8 | 0 | 0.04247 | 0.52036 | 33.5479 | 0 | 0 | 0 | 0 | 0 | 33.5479 | 118000 | 33.5479 | 491539.7077 | 510.81 | 0
5228 | 8 | 1 | 0 | 0.48812 | 19.9643 | 200 | 19.9643 | 180 | 199.9643 | 0 | 0 | 117800 | 199.9643 | 491739.6719 | 330.81 | 0
5229 | 8 | 1 | 0 | 0.73846 | 30.203 | 200 | 30.203 | 169.797 | 200 | 0 | 0 | 117600 | 200 | 491939.6719 | 161.013 | 0
5230 | 8 | 0 | 0 | 0.5287 | 21.6239 | 0 | 0 | 0 | 0 | 21.6239 | 0 | 117600 | 0 | 491939.6719 | 179.7566 | 0
5231 | 8 | 0 | 0 | 0.40817 | 16.6941 | 0 | 0 | 0 | 0 | 16.6941 | 0 | 117600 | 0 | 491939.6719 | 194.227 | 0
5232 | 8 | 0 | 0 | 0.52146 | 21.3277 | 0 | 0 | 0 | 0 | 21.3277 | 0 | 117600 | 0 | 491939.6719 | 212.7138 | 0
5233 | 8 | 0 | 0 | 0.45503 | 18.6108 | 0 | 0 | 0 | 0 | 18.6108 | 0 | 117600 | 0 | 491939.6719 | 228.8457 | 0
5234 | 8 | 0 | 0 | 0.4786 | 19.5746 | 0 | 0 | 0 | 0 | 19.5746 | 0 | 117600 | 0 | 491939.6719 | 245.8129 | 0
5235 | 8 | 0 | 0 | 0.48516 | 19.843 | 0 | 0 | 0 | 0 | 19.843 | 0 | 117600 | 0 | 491939.6719 | 263.0129 | 0
5236 | 8 | 0 | 0 | 0.60906 | 24.9106 | 0 | 0 | 0 | 0 | 24.9106 | 0 | 117600 | 0 | 491939.6719 | 284.6053 | 0
5237 | 8 | 0 | 0 | 0.56197 | 22.9846 | 0 | 0 | 0 | 0 | 22.9846 | 0 | 117600 | 0 | 491939.6719 | 304.5284 | 0
5238 | 8 | 0 | 0 | 0.43222 | 17.6777 | 0 | 0 | 0 | 0 | 17.6777 | 0 | 117600 | 0 | 491939.6719 | 319.8514 | 0
5239 | 8 | 0 | 0.054453 | 0.49949 | 36.155 | 0 | 0 | 0 | 0 | 36.155 | 0 | 117600 | 0 | 491939.6719 | 351.1905 | 0
5240 | 8 | 1 | 0.25761 | 0.46514 | 93.4227 | 200 | 93.4227 | 106.5773 | 200 | 0 | 0 | 117400 | 200 | 492139.6719 | 244.6132 | 0
5241 | 8 | 1 | 0.49604 | 0.52141 | 164.5831 | 200 | 164.5831 | 35.4169 | 200 | 0 | 0 | 117200 | 200 | 492339.6719 | 209.1963 | 0
5242 | 8 | 0 | 0.72566 | 0.57178 | 232.9551 | 0 | 0 | 0 | 0 | 180 | 52.9551 | 117200 | 52.9551 | 492392.6271 | 365.2203 | 0
5243 | 8 | 0 | 0.91415 | 0.56094 | 286.9481 | 0 | 0 | 0 | 0 | 167.9623 | 118.9858 | 117200 | 118.9858 | 492511.6129 | 510.81 | 0
5244 | 8 | 0 | 1 | 0.73985 | 319.0598 | 0 | 0 | 0 | 0 | 0 | 200 | 117200 | 200 | 492711.6129 | 510.81 | 119.0598
5245 | 8 | 0 | 1 | 0.98533 | 329.1 | 0 | 0 | 0 | 0 | 0 | 200 | 117200 | 200 | 492911.6129 | 510.81 | 129.1
5246 | 8 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 0 | 200 | 117200 | 200 | 493111.6129 | 510.81 | 129.7
5247 | 8 | 0 | 0.91415 | 0.90817 | 301.1498 | 0 | 0 | 0 | 0 | 0 | 200 | 117200 | 200 | 493311.6129 | 510.81 | 101.1498
5248 | 8 | 0 | 0.72566 | 0.91963 | 247.1821 | 0 | 0 | 0 | 0 | 0 | 200 | 117200 | 200 | 493511.6129 | 510.81 | 47.1821
5249 | 8 | 0 | 0.49604 | 0.93973 | 181.6922 | 0 | 0 | 0 | 0 | 0 | 181.6922 | 117200 | 181.6922 | 493693.3051 | 510.81 | 0
5250 | 8 | 0 | 0.25761 | 0.82909 | 108.308 | 0 | 0 | 0 | 0 | 0 | 108.308 | 117200 | 108.308 | 493801.613 | 510.81 | 0
5251 | 8 | 0 | 0.054453 | 0.98279 | 55.9222 | 0 | 0 | 0 | 0 | 0 | 55.9222 | 117200 | 55.9222 | 493857.5353 | 510.81 | 0
5252 | 8 | 1 | 0 | 1 | 40.9 | 200 | 40.9 | 159.1 | 200 | 0 | 0 | 117000 | 200 | 494057.5353 | 351.71 | 0
5253 | 8 | 1 | 0 | 0.74633 | 30.525 | 200 | 30.525 | 169.475 | 200 | 0 | 0 | 116800 | 200 | 494257.5353 | 182.235 | 0
5254 | 8 | 0 | 0 | 0.81123 | 33.1793 | 0 | 0 | 0 | 0 | 33.1793 | 0 | 116800 | 0 | 494257.5353 | 210.9949 | 0
5255 | 8 | 0 | 0 | 0.88423 | 36.1649 | 0 | 0 | 0 | 0 | 36.1649 | 0 | 116800 | 0 | 494257.5353 | 242.3426 | 0
5256 | 8 | 0 | 0 | 0.96474 | 39.458 | 0 | 0 | 0 | 0 | 39.458 | 0 | 116800 | 0 | 494257.5353 | 276.5448 | 0
5257 | 8 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 116800 | 0 | 494257.5353 | 311.9969 | 0
5258 | 8 | 0 | 0 | 0.96656 | 39.5323 | 0 | 0 | 0 | 0 | 39.5323 | 0 | 116800 | 0 | 494257.5353 | 346.2636 | 0
5259 | 8 | 0 | 0 | 0.63004 | 25.7686 | 0 | 0 | 0 | 0 | 25.7686 | 0 | 116800 | 0 | 494257.5353 | 368.5998 | 0
5260 | 8 | 0 | 0 | 0.51806 | 21.1888 | 0 | 0 | 0 | 0 | 21.1888 | 0 | 116800 | 0 | 494257.5353 | 386.9663 | 0
5261 | 8 | 0 | 0 | 0.43502 | 17.7923 | 0 | 0 | 0 | 0 | 17.7923 | 0 | 116800 | 0 | 494257.5353 | 402.3886 | 0
5262 | 8 | 0 | 0 | 0.49673 | 20.3163 | 0 | 0 | 0 | 0 | 20.3163 | 0 | 116800 | 0 | 494257.5353 | 419.9987 | 0
5263 | 8 | 0 | 0.053648 | 0.4555 | 34.1236 | 0 | 0 | 0 | 0 | 34.1236 | 0 | 116800 | 0 | 494257.5353 | 449.5771 | 0
5264 | 8 | 1 | 0.25381 | 0.62096 | 98.6961 | 200 | 98.6961 | 101.3039 | 200 | 0 | 0 | 116600 | 200 | 494457.5353 | 348.2732 | 0
5265 | 8 | 1 | 0.48871 | 0.69148 | 169.4222 | 200 | 169.4222 | 30.5778 | 200 | 0 | 0 | 116400 | 200 | 494657.5353 | 317.6955 | 0
5266 | 8 | 0 | 0.71493 | 0.54658 | 228.8279 | 0 | 0 | 0 | 0 | 180 | 48.8279 | 116400 | 48.8279 | 494706.3632 | 473.7195 | 0
5267 | 8 | 0 | 0.90064 | 0.47912 | 279.7004 | 0 | 0 | 0 | 0 | 42.7902 | 200 | 116400 | 200 | 494906.3632 | 510.81 | 36.9102
5268 | 8 | 0 | 1 | 0.46031 | 307.6268 | 0 | 0 | 0 | 0 | 0 | 200 | 116400 | 200 | 495106.3632 | 510.81 | 107.6268
5269 | 8 | 0 | 1 | 0.38416 | 304.5123 | 0 | 0 | 0 | 0 | 0 | 200 | 116400 | 200 | 495306.3632 | 510.81 | 104.5123
5270 | 8 | 0 | 1 | 0.46065 | 307.6405 | 0 | 0 | 0 | 0 | 0 | 200 | 116400 | 200 | 495506.3632 | 510.81 | 107.6405
5271 | 8 | 0 | 0.90064 | 0.58673 | 284.1017 | 0 | 0 | 0 | 0 | 0 | 200 | 116400 | 200 | 495706.3632 | 510.81 | 84.1017
5272 | 8 | 0 | 0.71493 | 0.76437 | 237.7355 | 0 | 0 | 0 | 0 | 0 | 200 | 116400 | 200 | 495906.3632 | 510.81 | 37.7355
5273 | 8 | 0 | 0.48871 | 0.79607 | 173.7 | 0 | 0 | 0 | 0 | 0 | 173.7 | 116400 | 173.7 | 496080.0632 | 510.81 | 0
5274 | 8 | 0 | 0.25381 | 1 | 114.1989 | 0 | 0 | 0 | 0 | 0 | 114.1989 | 116400 | 114.1989 | 496194.2621 | 510.81 | 0
5275 | 8 | 0 | 0.053648 | 0.91506 | 52.9193 | 0 | 0 | 0 | 0 | 0 | 52.9193 | 116400 | 52.9193 | 496247.1814 | 510.81 | 0
5276 | 8 | 1 | 0 | 0.81298 | 33.2511 | 200 | 33.2511 | 166.7489 | 200 | 0 | 0 | 116200 | 200 | 496447.1814 | 344.0611 | 0
5277 | 8 | 1 | 0 | 0.73723 | 30.1526 | 200 | 30.1526 | 169.8474 | 200 | 0 | 0 | 116000 | 200 | 496647.1814 | 174.2137 | 0
5278 | 8 | 0 | 0 | 0.8244 | 33.7178 | 0 | 0 | 0 | 0 | 33.7178 | 0 | 116000 | 0 | 496647.1814 | 203.4403 | 0
5279 | 8 | 0 | 0 | 0.68982 | 28.2137 | 0 | 0 | 0 | 0 | 28.2137 | 0 | 116000 | 0 | 496647.1814 | 227.8959 | 0
5280 | 8 | 0 | 0 | 0.51227 | 20.9519 | 0 | 0 | 0 | 0 | 20.9519 | 0 | 116000 | 0 | 496647.1814 | 246.057 | 0
5281 | 8 | 0 | 0 | 0.72779 | 29.7667 | 0 | 0 | 0 | 0 | 29.7667 | 0 | 116000 | 0 | 496647.1814 | 271.8588 | 0
5282 | 8 | 0 | 0 | 0.77569 | 31.7259 | 0 | 0 | 0 | 0 | 31.7259 | 0 | 116000 | 0 | 496647.1814 | 299.3588 | 0
5283 | 8 | 0 | 0 | 0.60387 | 24.6984 | 0 | 0 | 0 | 0 | 24.6984 | 0 | 116000 | 0 | 496647.1814 | 320.7674 | 0
5284 | 8 | 0 | 0 | 0.4843 | 19.8077 | 0 | 0 | 0 | 0 | 19.8077 | 0 | 116000 | 0 | 496647.1814 | 337.9367 | 0
5285 | 8 | 0 | 0 | 0.67622 | 27.6574 | 0 | 0 | 0 | 0 | 27.6574 | 0 | 116000 | 0 | 496647.1814 | 361.9101 | 0
5286 | 8 | 0 | 0 | 0.56786 | 23.2254 | 0 | 0 | 0 | 0 | 23.2254 | 0 | 116000 | 0 | 496647.1814 | 382.0419 | 0
5287 | 8 | 0 | 0.044421 | 0.55468 | 35.515 | 0 | 0 | 0 | 0 | 35.515 | 0 | 116000 | 0 | 496647.1814 | 412.8263 | 0
5288 | 8 | 1 | 0.21015 | 0.70067 | 89.35 | 200 | 89.35 | 110.65 | 200 | 0 | 0 | 115800 | 200 | 496847.1814 | 302.1763 | 0
5289 | 8 | 1 | 0.40466 | 0.88446 | 153.0406 | 200 | 153.0406 | 46.9594 | 200 | 0 | 0 | 115600 | 200 | 497047.1814 | 255.2169 | 0
5290 | 8 | 0 | 0.59197 | 0.89855 | 207.7125 | 0 | 0 | 0 | 0 | 180 | 27.7125 | 115600 | 27.7125 | 497074.8939 | 411.2409 | 0
5291 | 8 | 0 | 0.74574 | 0.72041 | 244.8344 | 0 | 0 | 0 | 0 | 114.8698 | 129.9646 | 115600 | 129.9646 | 497204.8585 | 510.81 | 0
5292 | 8 | 0 | 0.84627 | 0.6278 | 270.0801 | 0 | 0 | 0 | 0 | 0 | 200 | 115600 | 200 | 497404.8585 | 510.81 | 70.0801
5293 | 8 | 0 | 0.88119 | 0.9136 | 291.8544 | 0 | 0 | 0 | 0 | 0 | 200 | 115600 | 200 | 497604.8585 | 510.81 | 91.8544
5294 | 8 | 0 | 0.84627 | 0.82592 | 278.1833 | 0 | 0 | 0 | 0 | 0 | 200 | 115600 | 200 | 497804.8585 | 510.81 | 78.1833
5295 | 8 | 0 | 0.74574 | 1 | 256.2697 | 0 | 0 | 0 | 0 | 0 | 200 | 115600 | 200 | 498004.8585 | 510.81 | 56.2697
5296 | 8 | 0 | 0.59197 | 0.97424 | 210.8084 | 0 | 0 | 0 | 0 | 0 | 200 | 115600 | 200 | 498204.8585 | 510.81 | 10.8084
5297 | 8 | 0 | 0.40466 | 1 | 157.7661 | 0 | 0 | 0 | 0 | 0 | 157.7661 | 115600 | 157.7661 | 498362.6246 | 510.81 | 0
5298 | 8 | 0 | 0.21015 | 0.95605 | 99.7949 | 0 | 0 | 0 | 0 | 0 | 99.7949 | 115600 | 99.7949 | 498462.4195 | 510.81 | 0
5299 | 8 | 0 | 0.044421 | 0.88102 | 48.8624 | 0 | 0 | 0 | 0 | 0 | 48.8624 | 115600 | 48.8624 | 498511.2819 | 510.81 | 0
5300 | 8 | 1 | 0 | 0.75161 | 30.7407 | 200 | 30.7407 | 169.2593 | 200 | 0 | 0 | 115400 | 200 | 498711.2819 | 341.5507 | 0
5301 | 8 | 1 | 0 | 0.93441 | 38.2175 | 200 | 38.2175 | 161.7825 | 200 | 0 | 0 | 115200 | 200 | 498911.2819 | 179.7682 | 0
5302 | 8 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 115200 | 0 | 498911.2819 | 215.2203 | 0
5303 | 8 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 115200 | 0 | 498911.2819 | 250.6724 | 0
5304 | 8 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 115200 | 0 | 498911.2819 | 286.1245 | 0
5305 | 8 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 115200 | 0 | 498911.2819 | 321.5767 | 0
5306 | 8 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 115200 | 0 | 498911.2819 | 357.0288 | 0
5307 | 8 | 0 | 0 | 0.77274 | 31.6051 | 0 | 0 | 0 | 0 | 31.6051 | 0 | 115200 | 0 | 498911.2819 | 384.4241 | 0
5308 | 8 | 0 | 0 | 0.78237 | 31.9989 | 0 | 0 | 0 | 0 | 31.9989 | 0 | 115200 | 0 | 498911.2819 | 412.1608 | 0
5309 | 8 | 0 | 0 | 0.71096 | 29.0782 | 0 | 0 | 0 | 0 | 29.0782 | 0 | 115200 | 0 | 498911.2819 | 437.3658 | 0
5310 | 8 | 0 | 0 | 0.58705 | 24.0105 | 0 | 0 | 0 | 0 | 24.0105 | 0 | 115200 | 0 | 498911.2819 | 458.1781 | 0
5311 | 8 | 0 | 0.051384 | 0.8121 | 48.0545 | 0 | 0 | 0 | 0 | 48.0545 | 0 | 115200 | 0 | 498911.2819 | 499.8317 | 0
5312 | 8 | 1 | 0.2431 | 1 | 111.1058 | 200 | 111.1058 | 88.8942 | 200 | 0 | 0 | 115000 | 200 | 499111.2819 | 410.9376 | 0
5313 | 8 | 1 | 0.46809 | 1 | 176.0847 | 200 | 176.0847 | 23.9153 | 200 | 0 | 0 | 114800 | 200 | 499311.2819 | 387.0222 | 0
5314 | 8 | 0 | 0.68476 | 1 | 238.6598 | 0 | 0 | 0 | 0 | 142.8101 | 95.8498 | 114800 | 95.8498 | 499407.1317 | 510.81 | 0
5315 | 8 | 0 | 0.86263 | 1 | 290.0284 | 0 | 0 | 0 | 0 | 0 | 200 | 114800 | 200 | 499607.1317 | 510.81 | 90.0284
5316 | 8 | 0 | 0.97892 | 1 | 323.6127 | 0 | 0 | 0 | 0 | 0 | 200 | 114800 | 200 | 499807.1317 | 510.81 | 123.6127
5317 | 8 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 0 | 200 | 114800 | 200 | 500007.1317 | 510.81 | 129.7
5318 | 8 | 0 | 0.97892 | 0.613 | 307.7844 | 0 | 0 | 0 | 0 | 0 | 200 | 114800 | 200 | 500207.1317 | 510.81 | 107.7844
5319 | 8 | 0 | 0.86263 | 0.79241 | 281.5381 | 0 | 0 | 0 | 0 | 0 | 200 | 114800 | 200 | 500407.1317 | 510.81 | 81.5381
5320 | 8 | 0 | 0.68476 | 0.43605 | 215.5945 | 0 | 0 | 0 | 0 | 0 | 200 | 114800 | 200 | 500607.1317 | 510.81 | 15.5945
5321 | 8 | 0 | 0.46809 | 0.5924 | 159.4137 | 0 | 0 | 0 | 0 | 0 | 159.4137 | 114800 | 159.4137 | 500766.5454 | 510.81 | 0
5322 | 8 | 0 | 0.2431 | 0.47092 | 89.4667 | 0 | 0 | 0 | 0 | 0 | 89.4667 | 114800 | 89.4667 | 500856.0121 | 510.81 | 0
5323 | 8 | 0 | 0.051384 | 0.57477 | 38.3478 | 0 | 0 | 0 | 0 | 0 | 38.3478 | 114800 | 38.3478 | 500894.3598 | 510.81 | 0
5324 | 8 | 1 | 0 | 0.59358 | 24.2773 | 200 | 24.2773 | 175.7227 | 200 | 0 | 0 | 114600 | 200 | 501094.3598 | 335.0873 | 0
5325 | 8 | 1 | 0 | 0.49996 | 20.4484 | 200 | 20.4484 | 179.5516 | 200 | 0 | 0 | 114400 | 200 | 501294.3598 | 155.5357 | 0
5326 | 8 | 0 | 0 | 0.42199 | 17.2595 | 0 | 0 | 0 | 0 | 17.2595 | 0 | 114400 | 0 | 501294.3598 | 170.4963 | 0
5327 | 8 | 0 | 0 | 0.44548 | 18.2201 | 0 | 0 | 0 | 0 | 18.2201 | 0 | 114400 | 0 | 501294.3598 | 186.2894 | 0
5328 | 8 | 0 | 0 | 0.36784 | 15.0447 | 0 | 0 | 0 | 0 | 15.0447 | 0 | 114400 | 0 | 501294.3598 | 199.3302 | 0
5329 | 8 | 0 | 0 | 0.59802 | 24.459 | 0 | 0 | 0 | 0 | 24.459 | 0 | 114400 | 0 | 501294.3598 | 220.5313 | 0
5330 | 8 | 0 | 0 | 0.47607 | 19.4713 | 0 | 0 | 0 | 0 | 19.4713 | 0 | 114400 | 0 | 501294.3598 | 237.409 | 0
5331 | 8 | 0 | 0 | 0.42996 | 17.5852 | 0 | 0 | 0 | 0 | 17.5852 | 0 | 114400 | 0 | 501294.3598 | 252.6519 | 0
5332 | 8 | 0 | 0 | 0.28661 | 11.7223 | 0 | 0 | 0 | 0 | 11.7223 | 0 | 114400 | 0 | 501294.3598 | 262.8128 | 0
5333 | 8 | 0 | 0 | 0.32668 | 13.3614 | 0 | 0 | 0 | 0 | 13.3614 | 0 | 114400 | 0 | 501294.3598 | 274.3945 | 0
5334 | 8 | 0 | 0 | 0.3196 | 13.0718 | 0 | 0 | 0 | 0 | 13.0718 | 0 | 114400 | 0 | 501294.3598 | 285.7251 | 0
5335 | 8 | 0 | 0.047378 | 0.29418 | 25.7147 | 0 | 0 | 0 | 0 | 25.7147 | 0 | 114400 | 0 | 501294.3598 | 308.0146 | 0
5336 | 8 | 1 | 0.22414 | 0.22946 | 74.1173 | 200 | 74.1173 | 125.8827 | 200 | 0 | 0 | 114200 | 200 | 501494.3598 | 182.1319 | 0
5337 | 8 | 1 | 0.4316 | 0.34469 | 138.7429 | 200 | 138.7429 | 61.2571 | 200 | 0 | 0 | 114000 | 200 | 501694.3598 | 120.8748 | 0
5338 | 8 | 0 | 0.63138 | 0.34288 | 196.3651 | 0 | 0 | 0 | 0 | 180 | 16.3651 | 114000 | 16.3651 | 501710.7249 | 276.8988 | 0
5339 | 8 | 0 | 0.79538 | 0.38324 | 245.3799 | 0 | 0 | 0 | 0 | 180 | 65.3799 | 114000 | 65.3799 | 501776.1048 | 432.9228 | 0
5340 | 8 | 0 | 0.9026 | 0.61143 | 285.6786 | 0 | 0 | 0 | 0 | 89.8561 | 195.8225 | 114000 | 195.8225 | 501971.9274 | 510.81 | 0
5341 | 8 | 0 | 0.93985 | 0.82669 | 305.2394 | 0 | 0 | 0 | 0 | 0 | 200 | 114000 | 200 | 502171.9274 | 510.81 | 105.2394
5342 | 8 | 0 | 0.9026 | 1 | 301.5712 | 0 | 0 | 0 | 0 | 0 | 200 | 114000 | 200 | 502371.9274 | 510.81 | 101.5712
5343 | 8 | 0 | 0.79538 | 0.66624 | 256.9546 | 0 | 0 | 0 | 0 | 0 | 200 | 114000 | 200 | 502571.9274 | 510.81 | 56.9546
5344 | 8 | 0 | 0.63138 | 1 | 223.2414 | 0 | 0 | 0 | 0 | 0 | 200 | 114000 | 200 | 502771.9274 | 510.81 | 23.2414
5345 | 8 | 0 | 0.4316 | 1 | 165.5449 | 0 | 0 | 0 | 0 | 0 | 165.5449 | 114000 | 165.5449 | 502937.4723 | 510.81 | 0
5346 | 8 | 0 | 0.22414 | 1 | 105.6322 | 0 | 0 | 0 | 0 | 0 | 105.6322 | 114000 | 105.6322 | 503043.1045 | 510.81 | 0
5347 | 8 | 0 | 0.047378 | 1 | 54.5828 | 0 | 0 | 0 | 0 | 0 | 54.5828 | 114000 | 54.5828 | 503097.6873 | 510.81 | 0
5348 | 8 | 1 | 0 | 0.87806 | 35.9125 | 200 | 35.9125 | 164.0875 | 200 | 0 | 0 | 113800 | 200 | 503297.6873 | 346.7225 | 0
5349 | 8 | 1 | 0 | 0.59831 | 24.4707 | 200 | 24.4707 | 175.5293 | 200 | 0 | 0 | 113600 | 200 | 503497.6873 | 171.1932 | 0
5350 | 8 | 0 | 0 | 0.44924 | 18.374 | 0 | 0 | 0 | 0 | 18.374 | 0 | 113600 | 0 | 503497.6873 | 187.1198 | 0
5351 | 8 | 0 | 0 | 0.22653 | 9.2652 | 0 | 0 | 0 | 0 | 9.2652 | 0 | 113600 | 0 | 503497.6873 | 195.1509 | 0
5352 | 8 | 0 | 0 | 0.30185 | 12.3459 | 0 | 0 | 0 | 0 | 12.3459 | 0 | 113600 | 0 | 503497.6873 | 205.8523 | 0
5353 | 8 | 0 | 0 | 0.27491 | 11.2437 | 0 | 0 | 0 | 0 | 11.2437 | 0 | 113600 | 0 | 503497.6873 | 215.5983 | 0
5354 | 8 | 0 | 0 | 0.38193 | 15.6208 | 0 | 0 | 0 | 0 | 15.6208 | 0 | 113600 | 0 | 503497.6873 | 229.1385 | 0
5355 | 8 | 0 | 0 | 0.47008 | 19.2264 | 0 | 0 | 0 | 0 | 19.2264 | 0 | 113600 | 0 | 503497.6873 | 245.8039 | 0
5356 | 8 | 0 | 0 | 0.58735 | 24.0225 | 0 | 0 | 0 | 0 | 24.0225 | 0 | 113600 | 0 | 503497.6873 | 266.6266 | 0
5357 | 8 | 0 | 0 | 0.75426 | 30.8491 | 0 | 0 | 0 | 0 | 30.8491 | 0 | 113600 | 0 | 503497.6873 | 293.3666 | 0
5358 | 8 | 0 | 0 | 0.54867 | 22.4406 | 0 | 0 | 0 | 0 | 22.4406 | 0 | 113600 | 0 | 503497.6873 | 312.818 | 0
5359 | 8 | 0 | 0.0551 | 0.97886 | 55.9482 | 0 | 0 | 0 | 0 | 55.9482 | 0 | 113600 | 0 | 503497.6873 | 361.314 | 0
5360 | 8 | 1 | 0.26067 | 1 | 116.1824 | 200 | 116.1824 | 83.8176 | 200 | 0 | 0 | 113400 | 200 | 503697.6873 | 277.4963 | 0
5361 | 8 | 1 | 0.50194 | 1 | 185.8597 | 200 | 185.8597 | 14.1403 | 200 | 0 | 0 | 113200 | 200 | 503897.6873 | 263.356 | 0
5362 | 8 | 0 | 0.73428 | 1 | 252.9595 | 0 | 0 | 0 | 0 | 180 | 72.9595 | 113200 | 72.9595 | 503970.6468 | 419.38 | 0
5363 | 8 | 0 | 0.92501 | 1 | 308.0426 | 0 | 0 | 0 | 0 | 105.4799 | 200 | 113200 | 200 | 504170.6468 | 510.81 | 2.5627
5364 | 8 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 0 | 200 | 113200 | 200 | 504370.6468 | 510.81 | 129.7
5365 | 8 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 0 | 200 | 113200 | 200 | 504570.6468 | 510.81 | 129.7
5366 | 8 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 0 | 200 | 113200 | 200 | 504770.6468 | 510.81 | 129.7
5367 | 8 | 0 | 0.92501 | 1 | 308.0426 | 0 | 0 | 0 | 0 | 0 | 200 | 113200 | 200 | 504970.6468 | 510.81 | 108.0426
5368 | 8 | 0 | 0.73428 | 0.84118 | 246.4638 | 0 | 0 | 0 | 0 | 0 | 200 | 113200 | 200 | 505170.6468 | 510.81 | 46.4638
5369 | 8 | 0 | 0.50194 | 0.76567 | 176.2755 | 0 | 0 | 0 | 0 | 0 | 176.2755 | 113200 | 176.2755 | 505346.9222 | 510.81 | 0
5370 | 8 | 0 | 0.26067 | 0.68917 | 103.4695 | 0 | 0 | 0 | 0 | 0 | 103.4695 | 113200 | 103.4695 | 505450.3917 | 510.81 | 0
5371 | 8 | 0 | 0.0551 | 0.50729 | 36.661 | 0 | 0 | 0 | 0 | 0 | 36.661 | 113200 | 36.661 | 505487.0528 | 510.81 | 0
5372 | 8 | 1 | 0 | 0.52585 | 21.5073 | 200 | 21.5073 | 178.4927 | 200 | 0 | 0 | 113000 | 200 | 505687.0528 | 332.3173 | 0
5373 | 8 | 1 | 0 | 0.73156 | 29.9208 | 200 | 29.9208 | 170.0792 | 200 | 0 | 0 | 112800 | 200 | 505887.0528 | 162.2381 | 0
5374 | 8 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 112800 | 0 | 505887.0528 | 197.6902 | 0
5375 | 8 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 112800 | 0 | 505887.0528 | 233.1423 | 0
5376 | 8 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 112800 | 0 | 505887.0528 | 268.5945 | 0
5377 | 8 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 112800 | 0 | 505887.0528 | 304.0466 | 0
5378 | 8 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 112800 | 0 | 505887.0528 | 339.4987 | 0
5379 | 8 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 112800 | 0 | 505887.0528 | 374.9508 | 0
5380 | 8 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 112800 | 0 | 505887.0528 | 410.4029 | 0
5381 | 8 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 112800 | 0 | 505887.0528 | 445.8551 | 0
5382 | 8 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 112800 | 0 | 505887.0528 | 481.3072 | 0
5383 | 8 | 0 | 0.05093 | 1 | 55.6086 | 0 | 0 | 0 | 0 | 34.0365 | 21.5721 | 112800 | 21.5721 | 505908.6249 | 510.81 | 0
5384 | 8 | 1 | 0.24095 | 1 | 110.4861 | 200 | 110.4861 | 89.5139 | 200 | 0 | 0 | 112600 | 200 | 506108.6249 | 421.2961 | 0
5385 | 8 | 1 | 0.46396 | 1 | 174.8911 | 200 | 174.8911 | 25.1089 | 200 | 0 | 0 | 112400 | 200 | 506308.6249 | 396.1871 | 0
5386 | 8 | 0 | 0.67872 | 1 | 236.9138 | 0 | 0 | 0 | 0 | 132.2368 | 104.677 | 112400 | 104.677 | 506413.3019 | 510.81 | 0
5387 | 8 | 0 | 0.85502 | 1 | 287.8289 | 0 | 0 | 0 | 0 | 0 | 200 | 112400 | 200 | 506613.3019 | 510.81 | 87.8289
5388 | 8 | 0 | 0.97028 | 1 | 321.1166 | 0 | 0 | 0 | 0 | 0 | 200 | 112400 | 200 | 506813.3019 | 510.81 | 121.1166
5389 | 8 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 0 | 200 | 112400 | 200 | 507013.3019 | 510.81 | 129.7
5390 | 8 | 0 | 0.97028 | 1 | 321.1166 | 0 | 0 | 0 | 0 | 0 | 200 | 112400 | 200 | 507213.3019 | 510.81 | 121.1166
5391 | 8 | 0 | 0.85502 | 1 | 287.8289 | 0 | 0 | 0 | 0 | 0 | 200 | 112400 | 200 | 507413.3019 | 510.81 | 87.8289
5392 | 8 | 0 | 0.67872 | 1 | 236.9138 | 0 | 0 | 0 | 0 | 0 | 200 | 112400 | 200 | 507613.3019 | 510.81 | 36.9138
5393 | 8 | 0 | 0.46396 | 1 | 174.8911 | 0 | 0 | 0 | 0 | 0 | 174.8911 | 112400 | 174.8911 | 507788.1929 | 510.81 | 0
5394 | 8 | 0 | 0.24095 | 1 | 110.4861 | 0 | 0 | 0 | 0 | 0 | 110.4861 | 112400 | 110.4861 | 507898.679 | 510.81 | 0
5395 | 8 | 0 | 0.05093 | 1 | 55.6086 | 0 | 0 | 0 | 0 | 0 | 55.6086 | 112400 | 55.6086 | 507954.2876 | 510.81 | 0
5396 | 8 | 1 | 0 | 1 | 40.9 | 200 | 40.9 | 159.1 | 200 | 0 | 0 | 112200 | 200 | 508154.2876 | 351.71 | 0
5397 | 8 | 1 | 0 | 1 | 40.9 | 200 | 40.9 | 159.1 | 200 | 0 | 0 | 112000 | 200 | 508354.2876 | 192.61 | 0
5398 | 8 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 112000 | 0 | 508354.2876 | 228.0621 | 0
5399 | 8 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 112000 | 0 | 508354.2876 | 263.5142 | 0
5400 | 8 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 112000 | 0 | 508354.2876 | 298.9664 | 0
5401 | 8 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 112000 | 0 | 508354.2876 | 334.4185 | 0
5402 | 8 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 112000 | 0 | 508354.2876 | 369.8706 | 0
5403 | 8 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 112000 | 0 | 508354.2876 | 405.3227 | 0
5404 | 8 | 0 | 0 | 0.75796 | 31.0007 | 0 | 0 | 0 | 0 | 31.0007 | 0 | 112000 | 0 | 508354.2876 | 432.1942 | 0
5405 | 8 | 0 | 0 | 0.87526 | 35.798 | 0 | 0 | 0 | 0 | 35.798 | 0 | 112000 | 0 | 508354.2876 | 463.2238 | 0
5406 | 8 | 0 | 0 | 0.84553 | 34.5822 | 0 | 0 | 0 | 0 | 34.5822 | 0 | 112000 | 0 | 508354.2876 | 493.1997 | 0
5407 | 8 | 0 | 0.05225 | 0.55575 | 37.8201 | 0 | 0 | 0 | 0 | 20.3165 | 17.5036 | 112000 | 17.5036 | 508371.7912 | 510.81 | 0
5408 | 8 | 1 | 0.24719 | 0.53308 | 93.192 | 200 | 93.192 | 106.808 | 200 | 0 | 0 | 111800 | 200 | 508571.7912 | 404.002 | 0
5409 | 8 | 1 | 0.47598 | 0.44993 | 155.865 | 200 | 155.865 | 44.135 | 200 | 0 | 0 | 111600 | 200 | 508771.7912 | 359.867 | 0
5410 | 8 | 0 | 0.6963 | 0.53663 | 223.0409 | 0 | 0 | 0 | 0 | 174.1382 | 48.9027 | 111600 | 48.9027 | 508820.6939 | 510.81 | 0
5411 | 8 | 0 | 0.87717 | 0.50112 | 273.8235 | 0 | 0 | 0 | 0 | 0 | 200 | 111600 | 200 | 509020.6939 | 510.81 | 73.8235
5412 | 8 | 0 | 0.99542 | 0.85856 | 322.593 | 0 | 0 | 0 | 0 | 0 | 200 | 111600 | 200 | 509220.6939 | 510.81 | 122.593
5413 | 8 | 0 | 1 | 0.95422 | 327.8276 | 0 | 0 | 0 | 0 | 0 | 200 | 111600 | 200 | 509420.6939 | 510.81 | 127.8276
5414 | 8 | 0 | 0.99542 | 1 | 328.3779 | 0 | 0 | 0 | 0 | 0 | 200 | 111600 | 200 | 509620.6939 | 510.81 | 128.3779
5415 | 8 | 0 | 0.87717 | 0.46889 | 272.5053 | 0 | 0 | 0 | 0 | 0 | 200 | 111600 | 200 | 509820.6939 | 510.81 | 72.5053
5416 | 8 | 0 | 0.6963 | 0.66251 | 228.1895 | 0 | 0 | 0 | 0 | 0 | 200 | 111600 | 200 | 510020.6939 | 510.81 | 28.1895
5417 | 8 | 0 | 0.47598 | 0.50727 | 158.2105 | 0 | 0 | 0 | 0 | 0 | 158.2105 | 111600 | 158.2105 | 510178.9044 | 510.81 | 0
5418 | 8 | 0 | 0.24719 | 0.38811 | 87.2627 | 0 | 0 | 0 | 0 | 0 | 87.2627 | 111600 | 87.2627 | 510266.1671 | 510.81 | 0
5419 | 8 | 0 | 0.05225 | 0.28801 | 26.8693 | 0 | 0 | 0 | 0 | 0 | 26.8693 | 111600 | 26.8693 | 510293.0364 | 510.81 | 0
5420 | 8 | 1 | 0 | 0.25941 | 10.61 | 200 | 10.61 | 180 | 190.61 | 0 | 0 | 111400 | 190.61 | 510483.6464 | 330.81 | 0
5421 | 8 | 1 | 0 | 0.42883 | 17.5389 | 200 | 17.5389 | 180 | 197.5389 | 0 | 0 | 111200 | 197.5389 | 510681.1853 | 150.81 | 0
5422 | 8 | 0 | 0 | 0.37214 | 15.2204 | 0 | 0 | 0 | 0 | 15.2204 | 0 | 111200 | 0 | 510681.1853 | 164.003 | 0
5423 | 8 | 0 | 0 | 0.31118 | 12.7271 | 0 | 0 | 0 | 0 | 12.7271 | 0 | 111200 | 0 | 510681.1853 | 175.0349 | 0
5424 | 8 | 0 | 0 | 0.20727 | 8.4774 | 0 | 0 | 0 | 0 | 8.4774 | 0 | 111200 | 0 | 510681.1853 | 182.3832 | 0
5425 | 8 | 0 | 0 | 0.23584 | 9.646 | 0 | 0 | 0 | 0 | 9.646 | 0 | 111200 | 0 | 510681.1853 | 190.7443 | 0
5426 | 8 | 0 | 0 | 0.21681 | 8.8677 | 0 | 0 | 0 | 0 | 8.8677 | 0 | 111200 | 0 | 510681.1853 | 198.4308 | 0
5427 | 8 | 0 | 0 | 0.22353 | 9.1425 | 0 | 0 | 0 | 0 | 9.1425 | 0 | 111200 | 0 | 510681.1853 | 206.3555 | 0
5428 | 8 | 0 | 0 | 0.19726 | 8.0681 | 0 | 0 | 0 | 0 | 8.0681 | 0 | 111200 | 0 | 510681.1853 | 213.349 | 0
5429 | 8 | 0 | 0 | 0.21216 | 8.6771 | 0 | 0 | 0 | 0 | 8.6771 | 0 | 111200 | 0 | 510681.1853 | 220.8703 | 0
5430 | 8 | 0 | 0 | 0.14853 | 6.0748 | 0 | 0 | 0 | 0 | 6.0748 | 0 | 111200 | 0 | 510681.1853 | 226.136 | 0
5431 | 8 | 0 | 0.042394 | 0.17923 | 19.5739 | 0 | 0 | 0 | 0 | 19.5739 | 0 | 111200 | 0 | 510681.1853 | 243.1026 | 0
5432 | 8 | 1 | 0.20056 | 0.18599 | 65.5297 | 200 | 65.5297 | 134.4703 | 200 | 0 | 0 | 111000 | 200 | 510881.1853 | 108.6323 | 0
5433 | 8 | 1 | 0.3862 | 0.25258 | 121.8637 | 200 | 121.8637 | 78.1363 | 200 | 0 | 0 | 110800 | 200 | 511081.1853 | 30.496 | 0
5434 | 8 | 0 | 0.56496 | 0.28011 | 174.6168 | 0 | 0 | 0 | 0 | 174.6168 | 0 | 110800 | 0 | 511081.1853 | 181.8538 | 0
5435 | 8 | 0 | 0.71171 | 0.42931 | 223.1006 | 0 | 0 | 0 | 0 | 180 | 43.1006 | 110800 | 43.1006 | 511124.2859 | 337.8778 | 0
5436 | 8 | 0 | 0.80765 | 0.4584 | 251.9989 | 0 | 0 | 0 | 0 | 180 | 71.9989 | 110800 | 71.9989 | 511196.2848 | 493.9018 | 0
5437 | 8 | 0 | 0.84098 | 0.61068 | 267.8519 | 0 | 0 | 0 | 0 | 19.5064 | 200 | 110800 | 200 | 511396.2848 | 510.81 | 48.3455
5438 | 8 | 0 | 0.80765 | 0.81005 | 266.3811 | 0 | 0 | 0 | 0 | 0 | 200 | 110800 | 200 | 511596.2848 | 510.81 | 66.3811
5439 | 8 | 0 | 0.71171 | 0.6091 | 230.4541 | 0 | 0 | 0 | 0 | 0 | 200 | 110800 | 200 | 511796.2848 | 510.81 | 30.4541
5440 | 8 | 0 | 0.56496 | 0.74483 | 193.624 | 0 | 0 | 0 | 0 | 0 | 193.624 | 110800 | 193.624 | 511989.9088 | 510.81 | 0
5441 | 8 | 0 | 0.3862 | 0.70506 | 140.3702 | 0 | 0 | 0 | 0 | 0 | 140.3702 | 110800 | 140.3702 | 512130.2791 | 510.81 | 0
5442 | 8 | 0 | 0.20056 | 0.36593 | 72.8895 | 0 | 0 | 0 | 0 | 0 | 72.8895 | 110800 | 72.8895 | 512203.1685 | 510.81 | 0
5443 | 8 | 0 | 0.042394 | 0.56517 | 35.3588 | 0 | 0 | 0 | 0 | 0 | 35.3588 | 110800 | 35.3588 | 512238.5274 | 510.81 | 0
5444 | 8 | 1 | 0 | 0.3904 | 15.9673 | 200 | 15.9673 | 180 | 195.9673 | 0 | 0 | 110600 | 195.9673 | 512434.4946 | 330.81 | 0
5445 | 8 | 1 | 0 | 0.32441 | 13.2684 | 200 | 13.2684 | 180 | 193.2684 | 0 | 0 | 110400 | 193.2684 | 512627.763 | 150.81 | 0
5446 | 8 | 0 | 0 | 0.33589 | 13.7379 | 0 | 0 | 0 | 0 | 13.7379 | 0 | 110400 | 0 | 512627.763 | 162.718 | 0
5447 | 8 | 0 | 0 | 0.29141 | 11.9188 | 0 | 0 | 0 | 0 | 11.9188 | 0 | 110400 | 0 | 512627.763 | 173.0493 | 0
5448 | 8 | 0 | 0 | 0.21654 | 8.8567 | 0 | 0 | 0 | 0 | 8.8567 | 0 | 110400 | 0 | 512627.763 | 180.7263 | 0
5449 | 8 | 0 | 0 | 0.24721 | 10.1108 | 0 | 0 | 0 | 0 | 10.1108 | 0 | 110400 | 0 | 512627.763 | 189.4904 | 0
5450 | 8 | 0 | 0 | 0.31392 | 12.8395 | 0 | 0 | 0 | 0 | 12.8395 | 0 | 110400 | 0 | 512627.763 | 200.6196 | 0
5451 | 8 | 0 | 0 | 0.24823 | 10.1528 | 0 | 0 | 0 | 0 | 10.1528 | 0 | 110400 | 0 | 512627.763 | 209.42 | 0
5452 | 8 | 0 | 0 | 0.24199 | 9.8972 | 0 | 0 | 0 | 0 | 9.8972 | 0 | 110400 | 0 | 512627.763 | 217.999 | 0
5453 | 8 | 0 | 0 | 0.25874 | 10.5825 | 0 | 0 | 0 | 0 | 10.5825 | 0 | 110400 | 0 | 512627.763 | 227.1719 | 0
5454 | 8 | 0 | 0 | 0.31414 | 12.8483 | 0 | 0 | 0 | 0 | 12.8483 | 0 | 110400 | 0 | 512627.763 | 238.3088 | 0
5455 | 8 | 0 | 0.055216 | 0.30693 | 28.4996 | 0 | 0 | 0 | 0 | 28.4996 | 0 | 110400 | 0 | 512627.763 | 263.0122 | 0
5456 | 8 | 1 | 0.26122 | 0.21129 | 84.0834 | 200 | 84.0834 | 115.9166 | 200 | 0 | 0 | 110200 | 200 | 512827.763 | 147.0956 | 0
5457 | 8 | 1 | 0.503 | 0.19735 | 153.3375 | 200 | 153.3375 | 46.6625 | 200 | 0 | 0 | 110000 | 200 | 513027.763 | 100.4331 | 0
5458 | 8 | 0 | 0.73583 | 0.25752 | 223.0401 | 0 | 0 | 0 | 0 | 180 | 43.0401 | 110000 | 43.0401 | 513070.8032 | 256.4571 | 0
5459 | 8 | 0 | 0.92696 | 0.27955 | 279.1407 | 0 | 0 | 0 | 0 | 180 | 99.1407 | 110000 | 99.1407 | 513169.9439 | 412.4811 | 0
5460 | 8 | 0 | 1 | 0.22746 | 298.1031 | 0 | 0 | 0 | 0 | 113.439 | 184.6641 | 110000 | 184.6641 | 513354.608 | 510.81 | 0
5461 | 8 | 0 | 1 | 0.26606 | 299.6818 | 0 | 0 | 0 | 0 | 0 | 200 | 110000 | 200 | 513554.608 | 510.81 | 99.6818
5462 | 8 | 0 | 1 | 0.3112 | 301.528 | 0 | 0 | 0 | 0 | 0 | 200 | 110000 | 200 | 513754.608 | 510.81 | 101.528
5463 | 8 | 0 | 0.92696 | 0.3012 | 280.0264 | 0 | 0 | 0 | 0 | 0 | 200 | 110000 | 200 | 513954.608 | 510.81 | 80.0264
5464 | 8 | 0 | 0.73583 | 0.36695 | 227.5158 | 0 | 0 | 0 | 0 | 0 | 200 | 110000 | 200 | 514154.608 | 510.81 | 27.5158
5465 | 8 | 0 | 0.503 | 0.40772 | 161.9414 | 0 | 0 | 0 | 0 | 0 | 161.9414 | 110000 | 161.9414 | 514316.5494 | 510.81 | 0
5466 | 8 | 0 | 0.26122 | 0.52501 | 96.9144 | 0 | 0 | 0 | 0 | 0 | 96.9144 | 110000 | 96.9144 | 514413.4639 | 510.81 | 0
5467 | 8 | 0 | 0.055216 | 0.49928 | 36.3667 | 0 | 0 | 0 | 0 | 0 | 36.3667 | 110000 | 36.3667 | 514449.8306 | 510.81 | 0
5468 | 8 | 1 | 0 | 0.49752 | 20.3485 | 200 | 20.3485 | 179.6515 | 200 | 0 | 0 | 109800 | 200 | 514649.8306 | 331.1585 | 0
5469 | 8 | 1 | 0 | 0.45683 | 18.6843 | 200 | 18.6843 | 180 | 198.6843 | 0 | 0 | 109600 | 198.6843 | 514848.5148 | 151.1585 | 0
5470 | 8 | 0 | 0 | 0.62689 | 25.64 | 0 | 0 | 0 | 0 | 25.64 | 0 | 109600 | 0 | 514848.5148 | 173.3833 | 0
5471 | 8 | 0 | 0 | 0.44999 | 18.4045 | 0 | 0 | 0 | 0 | 18.4045 | 0 | 109600 | 0 | 514848.5148 | 189.3363 | 0
5472 | 8 | 0 | 0 | 0.42707 | 17.4671 | 0 | 0 | 0 | 0 | 17.4671 | 0 | 109600 | 0 | 514848.5148 | 204.4767 | 0
5473 | 8 | 0 | 0 | 0.33195 | 13.5768 | 0 | 0 | 0 | 0 | 13.5768 | 0 | 109600 | 0 | 514848.5148 | 216.2451 | 0
5474 | 8 | 0 | 0 | 0.4071 | 16.6504 | 0 | 0 | 0 | 0 | 16.6504 | 0 | 109600 | 0 | 514848.5148 | 230.6777 | 0
5475 | 8 | 0 | 0 | 0.29608 | 12.1098 | 0 | 0 | 0 | 0 | 12.1098 | 0 | 109600 | 0 | 514848.5148 | 241.1744 | 0
5476 | 8 | 0 | 0 | 0.17429 | 7.1285 | 0 | 0 | 0 | 0 | 7.1285 | 0 | 109600 | 0 | 514848.5148 | 247.3534 | 0
5477 | 8 | 0 | 0 | 0.19059 | 7.7952 | 0 | 0 | 0 | 0 | 7.7952 | 0 | 109600 | 0 | 514848.5148 | 254.1103 | 0
5478 | 8 | 0 | 0 | 0.29936 | 12.2438 | 0 | 0 | 0 | 0 | 12.2438 | 0 | 109600 | 0 | 514848.5148 | 264.7232 | 0
5479 | 8 | 0 | 0.052246 | 0.28335 | 26.6778 | 0 | 0 | 0 | 0 | 26.6778 | 0 | 109600 | 0 | 514848.5148 | 287.8476 | 0
5480 | 8 | 1 | 0.24717 | 0.23991 | 81.196 | 200 | 81.196 | 118.804 | 200 | 0 | 0 | 109400 | 200 | 515048.5148 | 169.0436 | 0
5481 | 8 | 1 | 0.47594 | 0.16338 | 144.1343 | 200 | 144.1343 | 55.8657 | 200 | 0 | 0 | 109200 | 200 | 515248.5148 | 113.1778 | 0
5482 | 8 | 0 | 0.69625 | 0.17649 | 208.2956 | 0 | 0 | 0 | 0 | 180 | 28.2956 | 109200 | 28.2956 | 515276.8105 | 269.2018 | 0
5483 | 8 | 0 | 0.8771 | 0.12654 | 258.4829 | 0 | 0 | 0 | 0 | 180 | 78.4829 | 109200 | 78.4829 | 515355.2933 | 425.2258 | 0
5484 | 8 | 0 | 0.99534 | 0.11922 | 292.331 | 0 | 0 | 0 | 0 | 98.7358 | 193.5952 | 109200 | 193.5952 | 515548.8886 | 510.81 | 0
5485 | 8 | 0 | 1 | 0.11679 | 293.5765 | 0 | 0 | 0 | 0 | 0 | 200 | 109200 | 200 | 515748.8886 | 510.81 | 93.5765
5486 | 8 | 0 | 0.99534 | 0.14971 | 293.5778 | 0 | 0 | 0 | 0 | 0 | 200 | 109200 | 200 | 515948.8886 | 510.81 | 93.5778
5487 | 8 | 0 | 0.8771 | 0.13539 | 258.845 | 0 | 0 | 0 | 0 | 0 | 200 | 109200 | 200 | 516148.8886 | 510.81 | 58.845
5488 | 8 | 0 | 0.69625 | 0.19641 | 209.1103 | 0 | 0 | 0 | 0 | 0 | 200 | 109200 | 200 | 516348.8886 | 510.81 | 9.1103
5489 | 8 | 0 | 0.47594 | 0.18857 | 145.1646 | 0 | 0 | 0 | 0 | 0 | 145.1646 | 109200 | 145.1646 | 516494.0532 | 510.81 | 0
5490 | 8 | 0 | 0.24717 | 0.22698 | 80.6672 | 0 | 0 | 0 | 0 | 0 | 80.6672 | 109200 | 80.6672 | 516574.7203 | 510.81 | 0
5491 | 8 | 0 | 0.052246 | 0.31472 | 27.9607 | 0 | 0 | 0 | 0 | 0 | 27.9607 | 109200 | 27.9607 | 516602.681 | 510.81 | 0
5492 | 8 | 1 | 0 | 0.39989 | 16.3554 | 200 | 16.3554 | 180 | 196.3554 | 0 | 0 | 109000 | 196.3554 | 516799.0364 | 330.81 | 0
5493 | 8 | 1 | 0 | 0.45395 | 18.5667 | 200 | 18.5667 | 180 | 198.5667 | 0 | 0 | 108800 | 198.5667 | 516997.6031 | 150.81 | 0
5494 | 8 | 0 | 0 | 0.51339 | 20.9977 | 0 | 0 | 0 | 0 | 20.9977 | 0 | 108800 | 0 | 516997.6031 | 169.0108 | 0
5495 | 8 | 0 | 0 | 0.51641 | 21.1213 | 0 | 0 | 0 | 0 | 21.1213 | 0 | 108800 | 0 | 516997.6031 | 187.3187 | 0
5496 | 8 | 0 | 0 | 0.50733 | 20.7498 | 0 | 0 | 0 | 0 | 20.7498 | 0 | 108800 | 0 | 516997.6031 | 205.3047 | 0
5497 | 8 | 0 | 0 | 0.51017 | 20.866 | 0 | 0 | 0 | 0 | 20.866 | 0 | 108800 | 0 | 516997.6031 | 223.3913 | 0
5498 | 8 | 0 | 0 | 0.44938 | 18.3797 | 0 | 0 | 0 | 0 | 18.3797 | 0 | 108800 | 0 | 516997.6031 | 239.3228 | 0
5499 | 8 | 0 | 0 | 0.33263 | 13.6046 | 0 | 0 | 0 | 0 | 13.6046 | 0 | 108800 | 0 | 516997.6031 | 251.1153 | 0
5500 | 8 | 0 | 0 | 0.34373 | 14.0584 | 0 | 0 | 0 | 0 | 14.0584 | 0 | 108800 | 0 | 516997.6031 | 263.3011 | 0
5501 | 8 | 0 | 0 | 0.45817 | 18.739 | 0 | 0 | 0 | 0 | 18.739 | 0 | 108800 | 0 | 516997.6031 | 279.5441 | 0
5502 | 8 | 0 | 0 | 0.32842 | 13.4323 | 0 | 0 | 0 | 0 | 13.4323 | 0 | 108800 | 0 | 516997.6031 | 291.1872 | 0
5503 | 8 | 0 | 0.040829 | 0.34767 | 26.011 | 0 | 0 | 0 | 0 | 26.011 | 0 | 108800 | 0 | 516997.6031 | 313.7335 | 0
5504 | 8 | 1 | 0.19316 | 0.56966 | 79.0837 | 200 | 79.0837 | 120.9163 | 200 | 0 | 0 | 108600 | 200 | 517197.6031 | 192.8172 | 0
5505 | 8 | 1 | 0.37194 | 0.27405 | 118.6244 | 200 | 118.6244 | 81.3756 | 200 | 0 | 0 | 108400 | 200 | 517397.6031 | 111.4416 | 0
5506 | 8 | 0 | 0.5441 | 0.25414 | 167.5314 | 0 | 0 | 0 | 0 | 167.5314 | 0 | 108400 | 0 | 517397.6031 | 256.6579 | 0
5507 | 8 | 0 | 0.68544 | 0.36723 | 212.9737 | 0 | 0 | 0 | 0 | 180 | 32.9737 | 108400 | 32.9737 | 517430.5768 | 412.6819 | 0
5508 | 8 | 0 | 0.77784 | 0.57681 | 248.231 | 0 | 0 | 0 | 0 | 113.2074 | 135.0236 | 108400 | 135.0236 | 517565.6004 | 510.81 | 0
5509 | 8 | 0 | 0.80993 | 0.61123 | 258.9081 | 0 | 0 | 0 | 0 | 0 | 200 | 108400 | 200 | 517765.6004 | 510.81 | 58.9081
5510 | 8 | 0 | 0.77784 | 0.69033 | 252.8737 | 0 | 0 | 0 | 0 | 0 | 200 | 108400 | 200 | 517965.6004 | 510.81 | 52.8737
5511 | 8 | 0 | 0.68544 | 0.6217 | 223.3814 | 0 | 0 | 0 | 0 | 0 | 200 | 108400 | 200 | 518165.6004 | 510.81 | 23.3814
5512 | 8 | 0 | 0.5441 | 0.82227 | 190.768 | 0 | 0 | 0 | 0 | 0 | 190.768 | 108400 | 190.768 | 518356.3684 | 510.81 | 0
5513 | 8 | 0 | 0.37194 | 0.82697 | 141.2388 | 0 | 0 | 0 | 0 | 0 | 141.2388 | 108400 | 141.2388 | 518497.6072 | 510.81 | 0
5514 | 8 | 0 | 0.19316 | 1 | 96.6846 | 0 | 0 | 0 | 0 | 0 | 96.6846 | 108400 | 96.6846 | 518594.2918 | 510.81 | 0
5515 | 8 | 0 | 0.040829 | 0.95845 | 50.9921 | 0 | 0 | 0 | 0 | 0 | 50.9921 | 108400 | 50.9921 | 518645.2839 | 510.81 | 0
5516 | 8 | 1 | 0 | 1 | 40.9 | 200 | 40.9 | 159.1 | 200 | 0 | 0 | 108200 | 200 | 518845.2839 | 351.71 | 0
5517 | 8 | 1 | 0 | 1 | 40.9 | 200 | 40.9 | 159.1 | 200 | 0 | 0 | 108000 | 200 | 519045.2839 | 192.61 | 0
5518 | 8 | 0 | 0 | 0.9854 | 40.3029 | 0 | 0 | 0 | 0 | 40.3029 | 0 | 108000 | 0 | 519045.2839 | 227.5446 | 0
5519 | 8 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 108000 | 0 | 519045.2839 | 262.9967 | 0
5520 | 8 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 108000 | 0 | 519045.2839 | 298.4488 | 0
5521 | 8 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 108000 | 0 | 519045.2839 | 333.9009 | 0
5522 | 8 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 108000 | 0 | 519045.2839 | 369.353 | 0
5523 | 8 | 0 | 0 | 0.96404 | 39.4293 | 0 | 0 | 0 | 0 | 39.4293 | 0 | 108000 | 0 | 519045.2839 | 403.5304 | 0
5524 | 8 | 0 | 0 | 0.73473 | 30.0506 | 0 | 0 | 0 | 0 | 30.0506 | 0 | 108000 | 0 | 519045.2839 | 429.5782 | 0
5525 | 8 | 0 | 0 | 0.91902 | 37.5879 | 0 | 0 | 0 | 0 | 37.5879 | 0 | 108000 | 0 | 519045.2839 | 462.1594 | 0
5526 | 8 | 0 | 0 | 0.78587 | 32.1422 | 0 | 0 | 0 | 0 | 32.1422 | 0 | 108000 | 0 | 519045.2839 | 490.0203 | 0
5527 | 8 | 0 | 0.047137 | 0.90245 | 50.5232 | 0 | 0 | 0 | 0 | 23.9844 | 26.5387 | 108000 | 26.5387 | 519071.8226 | 510.81 | 0
5528 | 8 | 1 | 0.223 | 0.56448 | 87.4906 | 200 | 87.4906 | 112.5094 | 200 | 0 | 0 | 107800 | 200 | 519271.8226 | 398.3006 | 0
5529 | 8 | 1 | 0.4294 | 0.64071 | 150.2163 | 200 | 150.2163 | 49.7837 | 200 | 0 | 0 | 107600 | 200 | 519471.8226 | 348.5169 | 0
5530 | 8 | 0 | 0.62817 | 0.92021 | 219.0512 | 0 | 0 | 0 | 0 | 180 | 39.0512 | 107600 | 39.0512 | 519510.8738 | 504.5409 | 0
5531 | 8 | 0 | 0.79134 | 0.55532 | 251.2501 | 0 | 0 | 0 | 0 | 7.2325 | 200 | 107600 | 200 | 519710.8738 | 510.81 | 44.0176
5532 | 8 | 0 | 0.89801 | 0.4322 | 277.0227 | 0 | 0 | 0 | 0 | 0 | 200 | 107600 | 200 | 519910.8738 | 510.81 | 77.0227
5533 | 8 | 0 | 0.93507 | 0.43722 | 287.9298 | 0 | 0 | 0 | 0 | 0 | 200 | 107600 | 200 | 520110.8738 | 510.81 | 87.9298
5534 | 8 | 0 | 0.89801 | 0.79422 | 291.8293 | 0 | 0 | 0 | 0 | 0 | 200 | 107600 | 200 | 520310.8738 | 510.81 | 91.8293
5535 | 8 | 0 | 0.79134 | 0.72509 | 258.1939 | 0 | 0 | 0 | 0 | 0 | 200 | 107600 | 200 | 520510.8738 | 510.81 | 58.1939
5536 | 8 | 0 | 0.62817 | 0.77739 | 213.2101 | 0 | 0 | 0 | 0 | 0 | 200 | 107600 | 200 | 520710.8738 | 510.81 | 13.2101
5537 | 8 | 0 | 0.4294 | 0.75343 | 154.8267 | 0 | 0 | 0 | 0 | 0 | 154.8267 | 107600 | 154.8267 | 520865.7006 | 510.81 | 0
5538 | 8 | 0 | 0.223 | 0.58156 | 88.189 | 0 | 0 | 0 | 0 | 0 | 88.189 | 107600 | 88.189 | 520953.8896 | 510.81 | 0
5539 | 8 | 0 | 0.047137 | 0.61405 | 38.728 | 0 | 0 | 0 | 0 | 0 | 38.728 | 107600 | 38.728 | 520992.6175 | 510.81 | 0
5540 | 8 | 1 | 0 | 0.66838 | 27.3367 | 200 | 27.3367 | 172.6633 | 200 | 0 | 0 | 107400 | 200 | 521192.6175 | 338.1467 | 0
5541 | 8 | 1 | 0 | 0.52757 | 21.5776 | 200 | 21.5776 | 178.4224 | 200 | 0 | 0 | 107200 | 200 | 521392.6175 | 159.7244 | 0
5542 | 8 | 0 | 0 | 0.50018 | 20.4572 | 0 | 0 | 0 | 0 | 20.4572 | 0 | 107200 | 0 | 521392.6175 | 177.4566 | 0
5543 | 8 | 0 | 0 | 0.39443 | 16.1322 | 0 | 0 | 0 | 0 | 16.1322 | 0 | 107200 | 0 | 521392.6175 | 191.44 | 0
5544 | 8 | 0 | 0 | 0.41871 | 17.1252 | 0 | 0 | 0 | 0 | 17.1252 | 0 | 107200 | 0 | 521392.6175 | 206.2842 | 0
5545 | 8 | 0 | 0 | 0.33783 | 13.8171 | 0 | 0 | 0 | 0 | 13.8171 | 0 | 107200 | 0 | 521392.6175 | 218.2608 | 0
5546 | 8 | 0 | 0 | 0.37073 | 15.163 | 0 | 0 | 0 | 0 | 15.163 | 0 | 107200 | 0 | 521392.6175 | 231.4041 | 0
5547 | 8 | 0 | 0 | 0.38245 | 15.6424 | 0 | 0 | 0 | 0 | 15.6424 | 0 | 107200 | 0 | 521392.6175 | 244.9629 | 0
5548 | 8 | 0 | 0 | 0.34178 | 13.979 | 0 | 0 | 0 | 0 | 13.979 | 0 | 107200 | 0 | 521392.6175 | 257.0798 | 0
5549 | 8 | 0 | 0 | 0.45438 | 18.5843 | 0 | 0 | 0 | 0 | 18.5843 | 0 | 107200 | 0 | 521392.6175 | 273.1887 | 0
5550 | 8 | 0 | 0 | 0.41964 | 17.1635 | 0 | 0 | 0 | 0 | 17.1635 | 0 | 107200 | 0 | 521392.6175 | 288.066 | 0
5551 | 8 | 0 | 0.047307 | 0.42223 | 30.9315 | 0 | 0 | 0 | 0 | 30.9315 | 0 | 107200 | 0 | 521392.6175 | 314.8774 | 0
5552 | 8 | 1 | 0.22381 | 0.38665 | 80.4492 | 200 | 80.4492 | 119.5508 | 200 | 0 | 0 | 107000 | 200 | 521592.6175 | 195.3266 | 0
5553 | 8 | 1 | 0.43095 | 0.4497 | 142.8509 | 200 | 142.8509 | 57.1491 | 200 | 0 | 0 | 106800 | 200 | 521792.6175 | 138.1775 | 0
5554 | 8 | 0 | 0.63043 | 0.36138 | 196.8481 | 0 | 0 | 0 | 0 | 180 | 16.8481 | 106800 | 16.8481 | 521809.4657 | 294.2015 | 0
5555 | 8 | 0 | 0.79419 | 0.25446 | 239.7684 | 0 | 0 | 0 | 0 | 180 | 59.7684 | 106800 | 59.7684 | 521869.234 | 450.2255 | 0
5556 | 8 | 0 | 0.90125 | 0.44471 | 278.4688 | 0 | 0 | 0 | 0 | 69.8944 | 200 | 106800 | 200 | 522069.234 | 510.81 | 8.5744
5557 | 8 | 0 | 0.93844 | 0.36486 | 285.943 | 0 | 0 | 0 | 0 | 0 | 200 | 106800 | 200 | 522269.234 | 510.81 | 85.943
5558 | 8 | 0 | 0.90125 | 0.32066 | 273.3951 | 0 | 0 | 0 | 0 | 0 | 200 | 106800 | 200 | 522469.234 | 510.81 | 73.3951
5559 | 8 | 0 | 0.79419 | 0.17971 | 236.7111 | 0 | 0 | 0 | 0 | 0 | 200 | 106800 | 200 | 522669.234 | 510.81 | 36.7111
5560 | 8 | 0 | 0.63043 | 0.15879 | 188.5624 | 0 | 0 | 0 | 0 | 0 | 188.5624 | 106800 | 188.5624 | 522857.7965 | 510.81 | 0
5561 | 8 | 0 | 0.43095 | 0.23502 | 134.0705 | 0 | 0 | 0 | 0 | 0 | 134.0705 | 106800 | 134.0705 | 522991.867 | 510.81 | 0
5562 | 8 | 0 | 0.22381 | 0.19773 | 72.7223 | 0 | 0 | 0 | 0 | 0 | 72.7223 | 106800 | 72.7223 | 523064.5893 | 510.81 | 0
5563 | 8 | 0 | 0.047307 | 0.28194 | 25.1936 | 0 | 0 | 0 | 0 | 0 | 25.1936 | 106800 | 25.1936 | 523089.7829 | 510.81 | 0
5564 | 8 | 1 | 0 | 0.22912 | 9.3709 | 200 | 9.3709 | 180 | 189.3709 | 0 | 0 | 106600 | 189.3709 | 523279.1537 | 330.81 | 0
5565 | 8 | 1 | 0 | 0.33562 | 13.7267 | 200 | 13.7267 | 180 | 193.7267 | 0 | 0 | 106400 | 193.7267 | 523472.8805 | 150.81 | 0
5566 | 8 | 0 | 0 | 0.23702 | 9.694 | 0 | 0 | 0 | 0 | 9.694 | 0 | 106400 | 0 | 523472.8805 | 159.2128 | 0
5567 | 8 | 0 | 0 | 0.30995 | 12.677 | 0 | 0 | 0 | 0 | 12.677 | 0 | 106400 | 0 | 523472.8805 | 170.2012 | 0
5568 | 8 | 0 | 0 | 0.23336 | 9.5444 | 0 | 0 | 0 | 0 | 9.5444 | 0 | 106400 | 0 | 523472.8805 | 178.4743 | 0
5569 | 8 | 0 | 0 | 0.29976 | 12.2602 | 0 | 0 | 0 | 0 | 12.2602 | 0 | 106400 | 0 | 523472.8805 | 189.1014 | 0
5570 | 8 | 0 | 0 | 0.32624 | 13.3431 | 0 | 0 | 0 | 0 | 13.3431 | 0 | 106400 | 0 | 523472.8805 | 200.6672 | 0
5571 | 8 | 0 | 0 | 0.54033 | 22.0995 | 0 | 0 | 0 | 0 | 22.0995 | 0 | 106400 | 0 | 523472.8805 | 219.823 | 0
5572 | 8 | 0 | 0 | 0.87037 | 35.598 | 0 | 0 | 0 | 0 | 35.598 | 0 | 106400 | 0 | 523472.8805 | 250.6794 | 0
5573 | 8 | 0 | 0 | 0.83109 | 33.9917 | 0 | 0 | 0 | 0 | 33.9917 | 0 | 106400 | 0 | 523472.8805 | 280.1433 | 0
5574 | 8 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 106400 | 0 | 523472.8805 | 315.5955 | 0
5575 | 8 | 0 | 0.049815 | 1 | 55.2866 | 0 | 0 | 0 | 0 | 55.2866 | 0 | 106400 | 0 | 523472.8805 | 363.5179 | 0
5576 | 8 | 1 | 0.23567 | 0.91347 | 105.4234 | 200 | 105.4234 | 94.5766 | 200 | 0 | 0 | 106200 | 200 | 523672.8805 | 268.9413 | 0
5577 | 8 | 1 | 0.4538 | 0.88993 | 167.4554 | 200 | 167.4554 | 32.5446 | 200 | 0 | 0 | 106000 | 200 | 523872.8805 | 236.3966 | 0
5578 | 8 | 0 | 0.66386 | 0.7194 | 221.1455 | 0 | 0 | 0 | 0 | 180 | 41.1455 | 106000 | 41.1455 | 523914.026 | 392.4206 | 0
5579 | 8 | 0 | 0.8363 | 0.73276 | 271.492 | 0 | 0 | 0 | 0 | 136.5821 | 134.9099 | 106000 | 134.9099 | 524048.936 | 510.81 | 0
5580 | 8 | 0 | 0.94903 | 0.55957 | 296.9675 | 0 | 0 | 0 | 0 | 0 | 200 | 106000 | 200 | 524248.936 | 510.81 | 96.9675
5581 | 8 | 0 | 0.9882 | 0.67591 | 313.0356 | 0 | 0 | 0 | 0 | 0 | 200 | 106000 | 200 | 524448.936 | 510.81 | 113.0356
5582 | 8 | 0 | 0.94903 | 0.38068 | 289.6507 | 0 | 0 | 0 | 0 | 0 | 200 | 106000 | 200 | 524648.936 | 510.81 | 89.6507
5583 | 8 | 0 | 0.8363 | 0.27764 | 252.878 | 0 | 0 | 0 | 0 | 0 | 200 | 106000 | 200 | 524848.936 | 510.81 | 52.878
5584 | 8 | 0 | 0.66386 | 0.22328 | 200.8539 | 0 | 0 | 0 | 0 | 0 | 200 | 106000 | 200 | 525048.936 | 510.81 | 0.85393
5585 | 8 | 0 | 0.4538 | 0.23836 | 140.806 | 0 | 0 | 0 | 0 | 0 | 140.806 | 106000 | 140.806 | 525189.7419 | 510.81 | 0
5586 | 8 | 0 | 0.23567 | 0.26162 | 78.7625 | 0 | 0 | 0 | 0 | 0 | 78.7625 | 106000 | 78.7625 | 525268.5044 | 510.81 | 0
5587 | 8 | 0 | 0.049815 | 0.39807 | 30.6677 | 0 | 0 | 0 | 0 | 0 | 30.6677 | 106000 | 30.6677 | 525299.1722 | 510.81 | 0
5588 | 8 | 1 | 0 | 0.51238 | 20.9564 | 200 | 20.9564 | 179.0436 | 200 | 0 | 0 | 105800 | 200 | 525499.1722 | 331.7664 | 0
5589 | 8 | 1 | 0 | 0.42775 | 17.4952 | 200 | 17.4952 | 180 | 197.4952 | 0 | 0 | 105600 | 197.4952 | 525696.6673 | 151.7664 | 0
5590 | 8 | 0 | 0 | 0.44083 | 18.0299 | 0 | 0 | 0 | 0 | 18.0299 | 0 | 105600 | 0 | 525696.6673 | 167.3947 | 0
5591 | 8 | 0 | 0 | 0.36952 | 15.1135 | 0 | 0 | 0 | 0 | 15.1135 | 0 | 105600 | 0 | 525696.6673 | 180.4952 | 0
5592 | 8 | 0 | 0 | 0.30247 | 12.3709 | 0 | 0 | 0 | 0 | 12.3709 | 0 | 105600 | 0 | 525696.6673 | 191.2183 | 0
5593 | 8 | 0 | 0 | 0.20948 | 8.5677 | 0 | 0 | 0 | 0 | 8.5677 | 0 | 105600 | 0 | 525696.6673 | 198.6448 | 0
5594 | 8 | 0 | 0 | 0.16348 | 6.6865 | 0 | 0 | 0 | 0 | 6.6865 | 0 | 105600 | 0 | 525696.6673 | 204.4407 | 0
5595 | 8 | 0 | 0 | 0.15739 | 6.4374 | 0 | 0 | 0 | 0 | 6.4374 | 0 | 105600 | 0 | 525696.6673 | 210.0206 | 0
5596 | 8 | 0 | 0 | 0.20486 | 8.379 | 0 | 0 | 0 | 0 | 8.379 | 0 | 105600 | 0 | 525696.6673 | 217.2835 | 0
5597 | 8 | 0 | 0 | 0.19517 | 7.9823 | 0 | 0 | 0 | 0 | 7.9823 | 0 | 105600 | 0 | 525696.6673 | 224.2026 | 0
5598 | 8 | 0 | 0 | 0.24059 | 9.84 | 0 | 0 | 0 | 0 | 9.84 | 0 | 105600 | 0 | 525696.6673 | 232.7319 | 0
5599 | 8 | 0 | 0.052005 | 0.25986 | 25.6473 | 0 | 0 | 0 | 0 | 25.6473 | 0 | 105600 | 0 | 525696.6673 | 254.963 | 0
5600 | 8 | 1 | 0.24603 | 0.36118 | 85.8271 | 200 | 85.8271 | 114.1729 | 200 | 0 | 0 | 105400 | 200 | 525896.6673 | 140.7901 | 0
5601 | 8 | 1 | 0.47375 | 0.46703 | 155.9204 | 200 | 155.9204 | 44.0796 | 200 | 0 | 0 | 105200 | 200 | 526096.6673 | 96.7104 | 0
5602 | 8 | 0 | 0.69304 | 0.52928 | 221.7978 | 0 | 0 | 0 | 0 | 180 | 41.7978 | 105200 | 41.7978 | 526138.4651 | 252.7344 | 0
5603 | 8 | 0 | 0.87306 | 0.37883 | 267.6343 | 0 | 0 | 0 | 0 | 180 | 87.6343 | 105200 | 87.6343 | 526226.0994 | 408.7584 | 0
5604 | 8 | 0 | 0.99076 | 0.53898 | 308.1746 | 0 | 0 | 0 | 0 | 117.7337 | 190.4409 | 105200 | 190.4409 | 526416.5403 | 510.81 | 0
5605 | 8 | 0 | 1 | 0.5304 | 310.4932 | 0 | 0 | 0 | 0 | 0 | 200 | 105200 | 200 | 526616.5403 | 510.81 | 110.4932
5606 | 8 | 0 | 0.99076 | 0.50757 | 306.89 | 0 | 0 | 0 | 0 | 0 | 200 | 105200 | 200 | 526816.5403 | 510.81 | 106.89
5607 | 8 | 0 | 0.87306 | 0.30108 | 264.4543 | 0 | 0 | 0 | 0 | 0 | 200 | 105200 | 200 | 527016.5403 | 510.81 | 64.4543
5608 | 8 | 0 | 0.69304 | 0.42446 | 217.5107 | 0 | 0 | 0 | 0 | 0 | 200 | 105200 | 200 | 527216.5403 | 510.81 | 17.5107
5609 | 8 | 0 | 0.47375 | 0.6791 | 164.5939 | 0 | 0 | 0 | 0 | 0 | 164.5939 | 105200 | 164.5939 | 527381.1342 | 510.81 | 0
5610 | 8 | 0 | 0.24603 | 0.92521 | 108.8957 | 0 | 0 | 0 | 0 | 0 | 108.8957 | 105200 | 108.8957 | 527490.0298 | 510.81 | 0
5611 | 8 | 0 | 0.052005 | 1 | 55.919 | 0 | 0 | 0 | 0 | 0 | 55.919 | 105200 | 55.919 | 527545.9489 | 510.81 | 0
5612 | 8 | 1 | 0 | 1 | 40.9 | 200 | 40.9 | 159.1 | 200 | 0 | 0 | 105000 | 200 | 527745.9489 | 351.71 | 0
5613 | 8 | 1 | 0 | 0.89515 | 36.6118 | 200 | 36.6118 | 163.3882 | 200 | 0 | 0 | 104800 | 200 | 527945.9489 | 188.3218 | 0
5614 | 8 | 0 | 0 | 0.57054 | 23.3352 | 0 | 0 | 0 | 0 | 23.3352 | 0 | 104800 | 0 | 527945.9489 | 208.5487 | 0
5615 | 8 | 0 | 0 | 0.45686 | 18.6856 | 0 | 0 | 0 | 0 | 18.6856 | 0 | 104800 | 0 | 527945.9489 | 224.7454 | 0
5616 | 8 | 0 | 0 | 0.4422 | 18.0861 | 0 | 0 | 0 | 0 | 18.0861 | 0 | 104800 | 0 | 527945.9489 | 240.4224 | 0
5617 | 8 | 0 | 0 | 0.31382 | 12.8353 | 0 | 0 | 0 | 0 | 12.8353 | 0 | 104800 | 0 | 527945.9489 | 251.548 | 0
5618 | 8 | 0 | 0 | 0.4032 | 16.491 | 0 | 0 | 0 | 0 | 16.491 | 0 | 104800 | 0 | 527945.9489 | 265.8424 | 0
5619 | 8 | 0 | 0 | 0.46177 | 18.8863 | 0 | 0 | 0 | 0 | 18.8863 | 0 | 104800 | 0 | 527945.9489 | 282.213 | 0
5620 | 8 | 0 | 0 | 0.4479 | 18.319 | 0 | 0 | 0 | 0 | 18.319 | 0 | 104800 | 0 | 527945.9489 | 298.0919 | 0
5621 | 8 | 0 | 0 | 0.41122 | 16.8188 | 0 | 0 | 0 | 0 | 16.8188 | 0 | 104800 | 0 | 527945.9489 | 312.6705 | 0
5622 | 8 | 0 | 0 | 0.47182 | 19.2975 | 0 | 0 | 0 | 0 | 19.2975 | 0 | 104800 | 0 | 527945.9489 | 329.3975 | 0
5623 | 8 | 0 | 0.048975 | 0.44526 | 32.355 | 0 | 0 | 0 | 0 | 32.355 | 0 | 104800 | 0 | 527945.9489 | 357.4428 | 0
5624 | 8 | 1 | 0.2317 | 0.41248 | 83.7851 | 200 | 83.7851 | 116.2149 | 200 | 0 | 0 | 104600 | 200 | 528145.9489 | 241.2279 | 0
5625 | 8 | 1 | 0.44615 | 0.53354 | 150.6689 | 200 | 150.6689 | 49.3311 | 200 | 0 | 0 | 104400 | 200 | 528345.9489 | 191.8968 | 0
5626 | 8 | 0 | 0.65266 | 0.42676 | 205.9432 | 0 | 0 | 0 | 0 | 180 | 25.9432 | 104400 | 25.9432 | 528371.8921 | 347.9208 | 0
5627 | 8 | 0 | 0.82219 | 0.47411 | 256.8409 | 0 | 0 | 0 | 0 | 180 | 76.8409 | 104400 | 76.8409 | 528448.733 | 503.9448 | 0
5628 | 8 | 0 | 0.93303 | 0.44425 | 287.6291 | 0 | 0 | 0 | 0 | 7.9202 | 200 | 104400 | 200 | 528648.733 | 510.81 | 79.709
5629 | 8 | 0 | 0.97153 | 0.50909 | 301.3999 | 0 | 0 | 0 | 0 | 0 | 200 | 104400 | 200 | 528848.733 | 510.81 | 101.3999
5630 | 8 | 0 | 0.93303 | 0.54098 | 291.5855 | 0 | 0 | 0 | 0 | 0 | 200 | 104400 | 200 | 529048.733 | 510.81 | 91.5855
5631 | 8 | 0 | 0.82219 | 0.54372 | 259.6877 | 0 | 0 | 0 | 0 | 0 | 200 | 104400 | 200 | 529248.733 | 510.81 | 59.6877
5632 | 8 | 0 | 0.65266 | 0.77959 | 220.3741 | 0 | 0 | 0 | 0 | 0 | 200 | 104400 | 200 | 529448.733 | 510.81 | 20.3741
5633 | 8 | 0 | 0.44615 | 0.55241 | 151.4408 | 0 | 0 | 0 | 0 | 0 | 151.4408 | 104400 | 151.4408 | 529600.1738 | 510.81 | 0
5634 | 8 | 0 | 0.2317 | 0.48763 | 86.8586 | 0 | 0 | 0 | 0 | 0 | 86.8586 | 104400 | 86.8586 | 529687.0324 | 510.81 | 0
5635 | 8 | 0 | 0.048975 | 0.45695 | 32.8332 | 0 | 0 | 0 | 0 | 0 | 32.8332 | 104400 | 32.8332 | 529719.8656 | 510.81 | 0
5636 | 8 | 1 | 0 | 0.79799 | 32.6377 | 200 | 32.6377 | 167.3623 | 200 | 0 | 0 | 104200 | 200 | 529919.8656 | 343.4477 | 0
5637 | 8 | 1 | 0 | 0.71271 | 29.1496 | 200 | 29.1496 | 170.8504 | 200 | 0 | 0 | 104000 | 200 | 530119.8656 | 172.5973 | 0
5638 | 8 | 0 | 0 | 0.64452 | 26.3607 | 0 | 0 | 0 | 0 | 26.3607 | 0 | 104000 | 0 | 530119.8656 | 195.4468 | 0
5639 | 8 | 0 | 0 | 0.6268 | 25.636 | 0 | 0 | 0 | 0 | 25.636 | 0 | 104000 | 0 | 530119.8656 | 217.6681 | 0
5640 | 8 | 0 | 0 | 0.56989 | 23.3086 | 0 | 0 | 0 | 0 | 23.3086 | 0 | 104000 | 0 | 530119.8656 | 237.872 | 0
5641 | 8 | 0 | 0 | 0.76872 | 31.4405 | 0 | 0 | 0 | 0 | 31.4405 | 0 | 104000 | 0 | 530119.8656 | 265.1246 | 0
5642 | 8 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 104000 | 0 | 530119.8656 | 300.5767 | 0
5643 | 8 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 104000 | 0 | 530119.8656 | 336.0288 | 0
5644 | 8 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 104000 | 0 | 530119.8656 | 371.481 | 0
5645 | 8 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 104000 | 0 | 530119.8656 | 406.9331 | 0
5646 | 8 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 104000 | 0 | 530119.8656 | 442.3852 | 0
5647 | 8 | 0 | 0.048388 | 1 | 54.8745 | 0 | 0 | 0 | 0 | 54.8745 | 0 | 104000 | 0 | 530119.8656 | 489.9504 | 0
5648 | 8 | 1 | 0.22892 | 1 | 107.0118 | 200 | 107.0118 | 92.9882 | 200 | 0 | 0 | 103800 | 200 | 530319.8656 | 396.9622 | 0
5649 | 8 | 1 | 0.44079 | 1 | 168.2013 | 200 | 168.2013 | 31.7987 | 200 | 0 | 0 | 103600 | 200 | 530519.8656 | 365.1635 | 0
5650 | 8 | 0 | 0.64483 | 1 | 227.1275 | 0 | 0 | 0 | 0 | 168.0278 | 59.0997 | 103600 | 59.0997 | 530578.9653 | 510.81 | 0
5651 | 8 | 0 | 0.81233 | 1 | 275.5009 | 0 | 0 | 0 | 0 | 0 | 200 | 103600 | 200 | 530778.9653 | 510.81 | 75.5009
5652 | 8 | 0 | 0.92184 | 1 | 307.1265 | 0 | 0 | 0 | 0 | 0 | 200 | 103600 | 200 | 530978.9653 | 510.81 | 107.1265
5653 | 8 | 0 | 0.95988 | 1 | 318.1122 | 0 | 0 | 0 | 0 | 0 | 200 | 103600 | 200 | 531178.9653 | 510.81 | 118.1122
5654 | 8 | 0 | 0.92184 | 1 | 307.1265 | 0 | 0 | 0 | 0 | 0 | 200 | 103600 | 200 | 531378.9653 | 510.81 | 107.1265
5655 | 8 | 0 | 0.81233 | 1 | 275.5009 | 0 | 0 | 0 | 0 | 0 | 200 | 103600 | 200 | 531578.9653 | 510.81 | 75.5009
5656 | 8 | 0 | 0.64483 | 1 | 227.1275 | 0 | 0 | 0 | 0 | 0 | 200 | 103600 | 200 | 531778.9653 | 510.81 | 27.1275
5657 | 8 | 0 | 0.44079 | 1 | 168.2013 | 0 | 0 | 0 | 0 | 0 | 168.2013 | 103600 | 168.2013 | 531947.1666 | 510.81 | 0
5658 | 8 | 0 | 0.22892 | 0.93489 | 104.3489 | 0 | 0 | 0 | 0 | 0 | 104.3489 | 103600 | 104.3489 | 532051.5155 | 510.81 | 0
5659 | 8 | 0 | 0.048388 | 1 | 54.8745 | 0 | 0 | 0 | 0 | 0 | 54.8745 | 103600 | 54.8745 | 532106.39 | 510.81 | 0
5660 | 8 | 1 | 0 | 1 | 40.9 | 200 | 40.9 | 159.1 | 200 | 0 | 0 | 103400 | 200 | 532306.39 | 351.71 | 0
5661 | 8 | 1 | 0 | 0.96069 | 39.2923 | 200 | 39.2923 | 160.7077 | 200 | 0 | 0 | 103200 | 200 | 532506.39 | 191.0023 | 0
5662 | 8 | 0 | 0 | 0.82439 | 33.7176 | 0 | 0 | 0 | 0 | 33.7176 | 0 | 103200 | 0 | 532506.39 | 220.2287 | 0
5663 | 8 | 0 | 0 | 0.85664 | 35.0366 | 0 | 0 | 0 | 0 | 35.0366 | 0 | 103200 | 0 | 532506.39 | 250.5984 | 0
5664 | 8 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 103200 | 0 | 532506.39 | 286.0505 | 0
5665 | 8 | 0 | 0 | 0.92498 | 37.8319 | 0 | 0 | 0 | 0 | 37.8319 | 0 | 103200 | 0 | 532506.39 | 318.8432 | 0
5666 | 8 | 0 | 0 | 0.76699 | 31.3698 | 0 | 0 | 0 | 0 | 31.3698 | 0 | 103200 | 0 | 532506.39 | 346.0346 | 0
5667 | 8 | 0 | 0 | 0.66844 | 27.3392 | 0 | 0 | 0 | 0 | 27.3392 | 0 | 103200 | 0 | 532506.39 | 369.7322 | 0
5668 | 8 | 0 | 0 | 0.71552 | 29.2646 | 0 | 0 | 0 | 0 | 29.2646 | 0 | 103200 | 0 | 532506.39 | 395.0987 | 0
5669 | 8 | 0 | 0 | 0.9532 | 38.9857 | 0 | 0 | 0 | 0 | 38.9857 | 0 | 103200 | 0 | 532506.39 | 428.8915 | 0
5670 | 8 | 0 | 0 | 0.9236 | 37.7754 | 0 | 0 | 0 | 0 | 37.7754 | 0 | 103200 | 0 | 532506.39 | 461.6352 | 0
5671 | 8 | 0 | 0.04362 | 0.67235 | 40.0965 | 0 | 0 | 0 | 0 | 40.0965 | 0 | 103200 | 0 | 532506.39 | 496.3909 | 0
5672 | 8 | 1 | 0.20636 | 0.87037 | 95.1956 | 200 | 95.1956 | 104.8044 | 200 | 0 | 0 | 103000 | 200 | 532706.39 | 391.5866 | 0
5673 | 8 | 1 | 0.39736 | 0.55293 | 137.3729 | 200 | 137.3729 | 62.6271 | 200 | 0 | 0 | 102800 | 200 | 532906.39 | 328.9595 | 0
5674 | 8 | 0 | 0.58129 | 0.85586 | 202.8822 | 0 | 0 | 0 | 0 | 180 | 22.8822 | 102800 | 22.8822 | 532929.2722 | 484.9835 | 0
5675 | 8 | 0 | 0.73229 | 0.80086 | 244.2398 | 0 | 0 | 0 | 0 | 29.7953 | 200 | 102800 | 200 | 533129.2722 | 510.81 | 14.4446
5676 | 8 | 0 | 0.831 | 0.80927 | 273.0931 | 0 | 0 | 0 | 0 | 0 | 200 | 102800 | 200 | 533329.2722 | 510.81 | 73.0931
5677 | 8 | 0 | 0.8653 | 0.58297 | 273.7408 | 0 | 0 | 0 | 0 | 0 | 200 | 102800 | 200 | 533529.2722 | 510.81 | 73.7408
5678 | 8 | 0 | 0.831 | 0.66746 | 267.2932 | 0 | 0 | 0 | 0 | 0 | 200 | 102800 | 200 | 533729.2722 | 510.81 | 67.2932
5679 | 8 | 0 | 0.73229 | 0.60752 | 236.332 | 0 | 0 | 0 | 0 | 0 | 200 | 102800 | 200 | 533929.2722 | 510.81 | 36.332
5680 | 8 | 0 | 0.58129 | 0.68173 | 195.7605 | 0 | 0 | 0 | 0 | 0 | 195.7605 | 102800 | 195.7605 | 534125.0326 | 510.81 | 0
5681 | 8 | 0 | 0.39736 | 0.5581 | 137.5843 | 0 | 0 | 0 | 0 | 0 | 137.5843 | 102800 | 137.5843 | 534262.617 | 510.81 | 0
5682 | 8 | 0 | 0.20636 | 0.6395 | 85.7532 | 0 | 0 | 0 | 0 | 0 | 85.7532 | 102800 | 85.7532 | 534348.3702 | 510.81 | 0
5683 | 8 | 0 | 0.04362 | 1 | 53.4975 | 0 | 0 | 0 | 0 | 0 | 53.4975 | 102800 | 53.4975 | 534401.8676 | 510.81 | 0
5684 | 8 | 1 | 0 | 1 | 40.9 | 200 | 40.9 | 159.1 | 200 | 0 | 0 | 102600 | 200 | 534601.8676 | 351.71 | 0
5685 | 8 | 1 | 0 | 1 | 40.9 | 200 | 40.9 | 159.1 | 200 | 0 | 0 | 102400 | 200 | 534801.8676 | 192.61 | 0
5686 | 8 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 102400 | 0 | 534801.8676 | 228.0621 | 0
5687 | 8 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 102400 | 0 | 534801.8676 | 263.5142 | 0
5688 | 8 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 102400 | 0 | 534801.8676 | 298.9664 | 0
5689 | 8 | 0 | 0 | 0.92433 | 37.8052 | 0 | 0 | 0 | 0 | 37.8052 | 0 | 102400 | 0 | 534801.8676 | 331.7359 | 0
5690 | 8 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 102400 | 0 | 534801.8676 | 367.188 | 0
5691 | 8 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 102400 | 0 | 534801.8676 | 402.6402 | 0
5692 | 8 | 0 | 0 | 0.98505 | 40.2887 | 0 | 0 | 0 | 0 | 40.2887 | 0 | 102400 | 0 | 534801.8676 | 437.5624 | 0
5693 | 8 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 102400 | 0 | 534801.8676 | 473.0145 | 0
5694 | 8 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 102400 | 0 | 534801.8676 | 508.4666 | 0
5695 | 8 | 0 | 0.047689 | 1 | 54.6726 | 0 | 0 | 0 | 0 | 2.7035 | 51.9691 | 102400 | 51.9691 | 534853.8367 | 510.81 | 0
5696 | 8 | 1 | 0.22561 | 1 | 106.0573 | 200 | 106.0573 | 93.9427 | 200 | 0 | 0 | 102200 | 200 | 535053.8367 | 416.8673 | 0
5697 | 8 | 1 | 0.43443 | 1 | 166.3637 | 200 | 166.3637 | 33.6363 | 200 | 0 | 0 | 102000 | 200 | 535253.8367 | 383.231 | 0
5698 | 8 | 0 | 0.63552 | 1 | 224.439 | 0 | 0 | 0 | 0 | 147.1839 | 77.2551 | 102000 | 77.2551 | 535331.0919 | 510.81 | 0
5699 | 8 | 0 | 0.8006 | 0.81761 | 264.6543 | 0 | 0 | 0 | 0 | 0 | 200 | 102000 | 200 | 535531.0919 | 510.81 | 64.6543
5700 | 8 | 0 | 0.90853 | 0.87643 | 298.229 | 0 | 0 | 0 | 0 | 0 | 200 | 102000 | 200 | 535731.0919 | 510.81 | 98.229
5701 | 8 | 0 | 0.94602 | 0.67487 | 300.8121 | 0 | 0 | 0 | 0 | 0 | 200 | 102000 | 200 | 535931.0919 | 510.81 | 100.8121
5702 | 8 | 0 | 0.90853 | 0.76573 | 293.7017 | 0 | 0 | 0 | 0 | 0 | 200 | 102000 | 200 | 536131.0919 | 510.81 | 93.7017
5703 | 8 | 0 | 0.8006 | 0.85685 | 266.2591 | 0 | 0 | 0 | 0 | 0 | 200 | 102000 | 200 | 536331.0919 | 510.81 | 66.2591
5704 | 8 | 0 | 0.63552 | 0.79507 | 216.0576 | 0 | 0 | 0 | 0 | 0 | 200 | 102000 | 200 | 536531.0919 | 510.81 | 16.0576
5705 | 8 | 0 | 0.43443 | 0.61104 | 150.455 | 0 | 0 | 0 | 0 | 0 | 150.455 | 102000 | 150.455 | 536681.5469 | 510.81 | 0
5706 | 8 | 0 | 0.22561 | 0.52396 | 86.5873 | 0 | 0 | 0 | 0 | 0 | 86.5873 | 102000 | 86.5873 | 536768.1343 | 510.81 | 0
5707 | 8 | 0 | 0.047689 | 0.37508 | 29.1134 | 0 | 0 | 0 | 0 | 0 | 29.1134 | 102000 | 29.1134 | 536797.2476 | 510.81 | 0
5708 | 8 | 1 | 0 | 0.27984 | 11.4455 | 200 | 11.4455 | 180 | 191.4455 | 0 | 0 | 101800 | 191.4455 | 536988.6931 | 330.81 | 0
5709 | 8 | 1 | 0 | 0.23752 | 9.7147 | 200 | 9.7147 | 180 | 189.7147 | 0 | 0 | 101600 | 189.7147 | 537178.4079 | 150.81 | 0
5710 | 8 | 0 | 0 | 0.21368 | 8.7396 | 0 | 0 | 0 | 0 | 8.7396 | 0 | 101600 | 0 | 537178.4079 | 158.3855 | 0
5711 | 8 | 0 | 0 | 0.19203 | 7.8541 | 0 | 0 | 0 | 0 | 7.8541 | 0 | 101600 | 0 | 537178.4079 | 165.1934 | 0
5712 | 8 | 0 | 0 | 0.11812 | 4.8311 | 0 | 0 | 0 | 0 | 4.8311 | 0 | 101600 | 0 | 537178.4079 | 169.381 | 0
5713 | 8 | 0 | 0 | 0.12444 | 5.0895 | 0 | 0 | 0 | 0 | 5.0895 | 0 | 101600 | 0 | 537178.4079 | 173.7926 | 0
5714 | 8 | 0 | 0 | 0.14185 | 5.8018 | 0 | 0 | 0 | 0 | 5.8018 | 0 | 101600 | 0 | 537178.4079 | 178.8216 | 0
5715 | 8 | 0 | 0 | 0.097326 | 3.9806 | 0 | 0 | 0 | 0 | 3.9806 | 0 | 101600 | 0 | 537178.4079 | 182.272 | 0
5716 | 8 | 0 | 0 | 0.082866 | 3.3892 | 0 | 0 | 0 | 0 | 3.3892 | 0 | 101600 | 0 | 537178.4079 | 185.2098 | 0
5717 | 8 | 0 | 0 | 0.11676 | 4.7754 | 0 | 0 | 0 | 0 | 4.7754 | 0 | 101600 | 0 | 537178.4079 | 189.3491 | 0
5718 | 8 | 0 | 0 | 0.21733 | 8.8889 | 0 | 0 | 0 | 0 | 8.8889 | 0 | 101600 | 0 | 537178.4079 | 197.0541 | 0
5719 | 8 | 0 | 0.048901 | 0.20725 | 22.5991 | 0 | 0 | 0 | 0 | 22.5991 | 0 | 101600 | 0 | 537178.4079 | 216.643 | 0
5720 | 8 | 1 | 0.23135 | 0.32284 | 80.0177 | 200 | 80.0177 | 119.9823 | 200 | 0 | 0 | 101400 | 200 | 537378.4079 | 96.6607 | 0
5721 | 8 | 1 | 0.44547 | 0.3489 | 142.9225 | 200 | 142.9225 | 57.0775 | 200 | 0 | 0 | 101200 | 200 | 537578.4079 | 39.5832 | 0
5722 | 8 | 0 | 0.65168 | 0.26731 | 199.1369 | 0 | 0 | 0 | 0 | 180 | 19.1369 | 101200 | 19.1369 | 537597.5448 | 195.6072 | 0
5723 | 8 | 0 | 0.82095 | 0.24478 | 247.1024 | 0 | 0 | 0 | 0 | 180 | 67.1024 | 101200 | 67.1024 | 537664.6472 | 351.6312 | 0
5724 | 8 | 0 | 0.93162 | 0.30562 | 281.5522 | 0 | 0 | 0 | 0 | 180 | 101.5522 | 101200 | 101.5522 | 537766.1994 | 507.6552 | 0
5725 | 8 | 0 | 0.97006 | 0.28186 | 291.6827 | 0 | 0 | 0 | 0 | 3.6396 | 200 | 101200 | 200 | 537966.1994 | 510.81 | 88.043
5726 | 8 | 0 | 0.93162 | 0.19452 | 277.0079 | 0 | 0 | 0 | 0 | 0 | 200 | 101200 | 200 | 538166.1994 | 510.81 | 77.0079
5727 | 8 | 0 | 0.82095 | 0.31091 | 249.8071 | 0 | 0 | 0 | 0 | 0 | 200 | 101200 | 200 | 538366.1994 | 510.81 | 49.8071
5728 | 8 | 0 | 0.65168 | 0.30221 | 200.5644 | 0 | 0 | 0 | 0 | 0 | 200 | 101200 | 200 | 538566.1994 | 510.81 | 0.56438
5729 | 8 | 0 | 0.44547 | 0.35797 | 143.2936 | 0 | 0 | 0 | 0 | 0 | 143.2936 | 101200 | 143.2936 | 538709.4931 | 510.81 | 0
5730 | 8 | 0 | 0.23135 | 0.35706 | 81.4172 | 0 | 0 | 0 | 0 | 0 | 81.4172 | 101200 | 81.4172 | 538790.9103 | 510.81 | 0
5731 | 8 | 0 | 0.048901 | 0.24997 | 24.3465 | 0 | 0 | 0 | 0 | 0 | 24.3465 | 101200 | 24.3465 | 538815.2568 | 510.81 | 0
5732 | 8 | 1 | 0 | 0.17511 | 7.1622 | 200 | 7.1622 | 180 | 187.1622 | 0 | 0 | 101000 | 187.1622 | 539002.419 | 330.81 | 0
5733 | 8 | 1 | 0 | 0.10905 | 4.4602 | 200 | 4.4602 | 180 | 184.4602 | 0 | 0 | 100800 | 184.4602 | 539186.8792 | 150.81 | 0
5734 | 8 | 0 | 0 | 0.13534 | 5.5355 | 0 | 0 | 0 | 0 | 5.5355 | 0 | 100800 | 0 | 539186.8792 | 155.6082 | 0
5735 | 8 | 0 | 0 | 0.092664 | 3.79 | 0 | 0 | 0 | 0 | 3.79 | 0 | 100800 | 0 | 539186.8792 | 158.8933 | 0
5736 | 8 | 0 | 0 | 0.1001 | 4.0941 | 0 | 0 | 0 | 0 | 4.0941 | 0 | 100800 | 0 | 539186.8792 | 162.4421 | 0
5737 | 8 | 0 | 0 | 0.12167 | 4.9763 | 0 | 0 | 0 | 0 | 4.9763 | 0 | 100800 | 0 | 539186.8792 | 166.7556 | 0
5738 | 8 | 0 | 0 | 0.1407 | 5.7547 | 0 | 0 | 0 | 0 | 5.7547 | 0 | 100800 | 0 | 539186.8792 | 171.7438 | 0
5739 | 8 | 0 | 0 | 0.18628 | 7.619 | 0 | 0 | 0 | 0 | 7.619 | 0 | 100800 | 0 | 539186.8792 | 178.3479 | 0
5740 | 8 | 0 | 0 | 0.22205 | 9.0818 | 0 | 0 | 0 | 0 | 9.0818 | 0 | 100800 | 0 | 539186.8792 | 186.22 | 0
5741 | 8 | 0 | 0 | 0.21958 | 8.9807 | 0 | 0 | 0 | 0 | 8.9807 | 0 | 100800 | 0 | 539186.8792 | 194.0045 | 0
5742 | 8 | 0 | 0 | 0.2332 | 9.5378 | 0 | 0 | 0 | 0 | 9.5378 | 0 | 100800 | 0 | 539186.8792 | 202.2719 | 0
5743 | 8 | 0 | 0.054837 | 0.35179 | 30.2253 | 0 | 0 | 0 | 0 | 30.2253 | 0 | 100800 | 0 | 539186.8792 | 228.4711 | 0
5744 | 8 | 1 | 0.25943 | 0.53567 | 96.8319 | 200 | 96.8319 | 103.1681 | 200 | 0 | 0 | 100600 | 200 | 539386.8792 | 125.303 | 0
5745 | 8 | 1 | 0.49954 | 0.52066 | 165.5631 | 200 | 165.5631 | 34.4369 | 200 | 0 | 0 | 100400 | 200 | 539586.8792 | 90.8661 | 0
5746 | 8 | 0 | 0.73077 | 0.5255 | 232.5409 | 0 | 0 | 0 | 0 | 180 | 52.5409 | 100400 | 52.5409 | 539639.4201 | 246.8901 | 0
5747 | 8 | 0 | 0.9206 | 0.69871 | 294.4456 | 0 | 0 | 0 | 0 | 180 | 114.4456 | 100400 | 114.4456 | 539753.8656 | 402.9141 | 0
5748 | 8 | 0 | 1 | 0.87591 | 324.6246 | 0 | 0 | 0 | 0 | 124.4761 | 200 | 100400 | 200 | 539953.8656 | 510.81 | 0.14847
5749 | 8 | 0 | 1 | 0.7105 | 317.8594 | 0 | 0 | 0 | 0 | 0 | 200 | 100400 | 200 | 540153.8656 | 510.81 | 117.8594
5750 | 8 | 0 | 1 | 0.88323 | 324.9241 | 0 | 0 | 0 | 0 | 0 | 200 | 100400 | 200 | 540353.8656 | 510.81 | 124.9241
5751 | 8 | 0 | 0.9206 | 0.85595 | 300.8764 | 0 | 0 | 0 | 0 | 0 | 200 | 100400 | 200 | 540553.8656 | 510.81 | 100.8764
5752 | 8 | 0 | 0.73077 | 0.76014 | 242.1377 | 0 | 0 | 0 | 0 | 0 | 200 | 100400 | 200 | 540753.8656 | 510.81 | 42.1377
5753 | 8 | 0 | 0.49954 | 0.91132 | 181.5409 | 0 | 0 | 0 | 0 | 0 | 181.5409 | 100400 | 181.5409 | 540935.4066 | 510.81 | 0
5754 | 8 | 0 | 0.25943 | 0.90262 | 111.8404 | 0 | 0 | 0 | 0 | 0 | 111.8404 | 100400 | 111.8404 | 541047.247 | 510.81 | 0
5755 | 8 | 0 | 0.054837 | 0.70426 | 44.641 | 0 | 0 | 0 | 0 | 0 | 44.641 | 100400 | 44.641 | 541091.888 | 510.81 | 0
5756 | 8 | 1 | 0 | 0.76996 | 31.4914 | 200 | 31.4914 | 168.5086 | 200 | 0 | 0 | 100200 | 200 | 541291.888 | 342.3014 | 0
5757 | 8 | 1 | 0 | 0.95279 | 38.9692 | 200 | 38.9692 | 161.0308 | 200 | 0 | 0 | 100000 | 200 | 541491.888 | 181.2706 | 0
5758 | 8 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 100000 | 0 | 541491.888 | 216.7227 | 0
5759 | 8 | 0 | 0 | 0.85062 | 34.7903 | 0 | 0 | 0 | 0 | 34.7903 | 0 | 100000 | 0 | 541491.888 | 246.8789 | 0
5760 | 8 | 0 | 0 | 0.60703 | 24.8274 | 0 | 0 | 0 | 0 | 24.8274 | 0 | 100000 | 0 | 541491.888 | 268.3994 | 0
5761 | 8 | 0 | 0 | 0.61672 | 25.224 | 0 | 0 | 0 | 0 | 25.224 | 0 | 100000 | 0 | 541491.888 | 290.2635 | 0
5762 | 8 | 0 | 0 | 0.65723 | 26.8807 | 0 | 0 | 0 | 0 | 26.8807 | 0 | 100000 | 0 | 541491.888 | 313.5637 | 0
5763 | 8 | 0 | 0 | 0.58336 | 23.8594 | 0 | 0 | 0 | 0 | 23.8594 | 0 | 100000 | 0 | 541491.888 | 334.245 | 0
5764 | 8 | 0 | 0 | 0.59252 | 24.234 | 0 | 0 | 0 | 0 | 24.234 | 0 | 100000 | 0 | 541491.888 | 355.2511 | 0
5765 | 8 | 0 | 0 | 0.5816 | 23.7874 | 0 | 0 | 0 | 0 | 23.7874 | 0 | 100000 | 0 | 541491.888 | 375.87 | 0
5766 | 8 | 0 | 0 | 0.64628 | 26.4326 | 0 | 0 | 0 | 0 | 26.4326 | 0 | 100000 | 0 | 541491.888 | 398.7818 | 0
5767 | 8 | 0 | 0.038134 | 0.8354 | 45.1809 | 0 | 0 | 0 | 0 | 45.1809 | 0 | 100000 | 0 | 541491.888 | 437.9446 | 0
5768 | 8 | 1 | 0.18041 | 0.70927 | 81.1112 | 200 | 81.1112 | 118.8888 | 200 | 0 | 0 | 99800 | 200 | 541691.888 | 319.0558 | 0
5769 | 8 | 1 | 0.34738 | 0.48649 | 120.2221 | 200 | 120.2221 | 79.7779 | 200 | 0 | 0 | 99600 | 200 | 541891.888 | 239.2779 | 0
5770 | 8 | 0 | 0.50818 | 0.51085 | 167.6575 | 0 | 0 | 0 | 0 | 167.6575 | 0 | 99600 | 0 | 541891.888 | 384.6034 | 0
5771 | 8 | 0 | 0.64019 | 0.71881 | 214.2855 | 0 | 0 | 0 | 0 | 145.6006 | 68.6849 | 99600 | 68.6849 | 541960.5728 | 510.81 | 0
5772 | 8 | 0 | 0.72649 | 0.56128 | 232.7662 | 0 | 0 | 0 | 0 | 0 | 200 | 99600 | 200 | 542160.5728 | 510.81 | 32.7662
5773 | 8 | 0 | 0.75647 | 0.50919 | 239.2936 | 0 | 0 | 0 | 0 | 0 | 200 | 99600 | 200 | 542360.5728 | 510.81 | 39.2936
5774 | 8 | 0 | 0.72649 | 0.65881 | 236.7555 | 0 | 0 | 0 | 0 | 0 | 200 | 99600 | 200 | 542560.5728 | 510.81 | 36.7555
5775 | 8 | 0 | 0.64019 | 0.72744 | 214.6385 | 0 | 0 | 0 | 0 | 0 | 200 | 99600 | 200 | 542760.5728 | 510.81 | 14.6385
5776 | 8 | 0 | 0.50818 | 0.54309 | 168.9762 | 0 | 0 | 0 | 0 | 0 | 168.9762 | 99600 | 168.9762 | 542929.549 | 510.81 | 0
5777 | 8 | 0 | 0.34738 | 0.48289 | 120.0748 | 0 | 0 | 0 | 0 | 0 | 120.0748 | 99600 | 120.0748 | 543049.6238 | 510.81 | 0
5778 | 8 | 0 | 0.18041 | 0.42667 | 69.5529 | 0 | 0 | 0 | 0 | 0 | 69.5529 | 99600 | 69.5529 | 543119.1767 | 510.81 | 0
5779 | 8 | 0 | 0.038134 | 0.5148 | 32.0683 | 0 | 0 | 0 | 0 | 0 | 32.0683 | 99600 | 32.0683 | 543151.245 | 510.81 | 0
5780 | 8 | 1 | 0 | 0.47464 | 19.4128 | 200 | 19.4128 | 180 | 199.4128 | 0 | 0 | 99400 | 199.4128 | 543350.6578 | 330.81 | 0
5781 | 8 | 1 | 0 | 0.52455 | 21.4539 | 200 | 21.4539 | 178.5461 | 200 | 0 | 0 | 99200 | 200 | 543550.6578 | 152.2639 | 0
5782 | 8 | 0 | 0 | 0.53992 | 22.0826 | 0 | 0 | 0 | 0 | 22.0826 | 0 | 99200 | 0 | 543550.6578 | 171.4051 | 0
5783 | 8 | 0 | 0 | 0.42763 | 17.4901 | 0 | 0 | 0 | 0 | 17.4901 | 0 | 99200 | 0 | 543550.6578 | 186.5656 | 0
5784 | 8 | 0 | 0 | 0.44875 | 18.3539 | 0 | 0 | 0 | 0 | 18.3539 | 0 | 99200 | 0 | 543550.6578 | 202.4747 | 0
5785 | 8 | 0 | 0 | 0.56708 | 23.1937 | 0 | 0 | 0 | 0 | 23.1937 | 0 | 99200 | 0 | 543550.6578 | 222.579 | 0
5786 | 8 | 0 | 0 | 0.42508 | 17.3857 | 0 | 0 | 0 | 0 | 17.3857 | 0 | 99200 | 0 | 543550.6578 | 237.649 | 0
5787 | 8 | 0 | 0 | 0.45632 | 18.6633 | 0 | 0 | 0 | 0 | 18.6633 | 0 | 99200 | 0 | 543550.6578 | 253.8263 | 0
5788 | 8 | 0 | 0 | 0.3863 | 15.7995 | 0 | 0 | 0 | 0 | 15.7995 | 0 | 99200 | 0 | 543550.6578 | 267.5214 | 0
5789 | 8 | 0 | 0 | 0.30862 | 12.6224 | 0 | 0 | 0 | 0 | 12.6224 | 0 | 99200 | 0 | 543550.6578 | 278.4625 | 0
5790 | 8 | 0 | 0 | 0.26212 | 10.7207 | 0 | 0 | 0 | 0 | 10.7207 | 0 | 99200 | 0 | 543550.6578 | 287.7552 | 0
5791 | 8 | 0 | 0.044063 | 0.2256 | 21.9526 | 0 | 0 | 0 | 0 | 21.9526 | 0 | 99200 | 0 | 543550.6578 | 306.7837 | 0
5792 | 8 | 1 | 0.20846 | 0.18834 | 67.906 | 200 | 67.906 | 132.094 | 200 | 0 | 0 | 99000 | 200 | 543750.6578 | 174.6897 | 0
5793 | 8 | 1 | 0.4014 | 0.36297 | 130.7688 | 200 | 130.7688 | 69.2312 | 200 | 0 | 0 | 98800 | 200 | 543950.6578 | 105.4585 | 0
5794 | 8 | 0 | 0.5872 | 0.38644 | 185.3883 | 0 | 0 | 0 | 0 | 180 | 5.3883 | 98800 | 5.3883 | 543956.0461 | 261.4825 | 0
5795 | 8 | 0 | 0.73973 | 0.31837 | 226.6542 | 0 | 0 | 0 | 0 | 180 | 46.6542 | 98800 | 46.6542 | 544002.7003 | 417.5065 | 0
5796 | 8 | 0 | 0.83945 | 0.30811 | 255.0336 | 0 | 0 | 0 | 0 | 107.6413 | 147.3923 | 98800 | 147.3923 | 544150.0926 | 510.81 | 0
5797 | 8 | 0 | 0.87409 | 0.44079 | 270.4641 | 0 | 0 | 0 | 0 | 0 | 200 | 98800 | 200 | 544350.0926 | 510.81 | 70.4641
5798 | 8 | 0 | 0.83945 | 0.48539 | 262.2845 | 0 | 0 | 0 | 0 | 0 | 200 | 98800 | 200 | 544550.0926 | 510.81 | 62.2845
5799 | 8 | 0 | 0.73973 | 0.64519 | 240.0213 | 0 | 0 | 0 | 0 | 0 | 200 | 98800 | 200 | 544750.0926 | 510.81 | 40.0213
5800 | 8 | 0 | 0.5872 | 0.42198 | 186.842 | 0 | 0 | 0 | 0 | 0 | 186.842 | 98800 | 186.842 | 544936.9346 | 510.81 | 0
5801 | 8 | 0 | 0.4014 | 0.41025 | 132.7028 | 0 | 0 | 0 | 0 | 0 | 132.7028 | 98800 | 132.7028 | 545069.6374 | 510.81 | 0
5802 | 8 | 0 | 0.20846 | 0.32973 | 73.6889 | 0 | 0 | 0 | 0 | 0 | 73.6889 | 98800 | 73.6889 | 545143.3264 | 510.81 | 0
5803 | 8 | 0 | 0.044063 | 0.25401 | 23.1145 | 0 | 0 | 0 | 0 | 0 | 23.1145 | 98800 | 23.1145 | 545166.4408 | 510.81 | 0
5804 | 8 | 1 | 0 | 0.22379 | 9.153 | 200 | 9.153 | 180 | 189.153 | 0 | 0 | 98600 | 189.153 | 545355.5939 | 330.81 | 0
5805 | 8 | 1 | 0 | 0.15011 | 6.1393 | 200 | 6.1393 | 180 | 186.1393 | 0 | 0 | 98400 | 186.1393 | 545541.7332 | 150.81 | 0
5806 | 8 | 0 | 0 | 0.13884 | 5.6785 | 0 | 0 | 0 | 0 | 5.6785 | 0 | 98400 | 0 | 545541.7332 | 155.7321 | 0
5807 | 8 | 0 | 0 | 0.17059 | 6.9772 | 0 | 0 | 0 | 0 | 6.9772 | 0 | 98400 | 0 | 545541.7332 | 161.78 | 0
5808 | 8 | 0 | 0 | 0.11969 | 4.8955 | 0 | 0 | 0 | 0 | 4.8955 | 0 | 98400 | 0 | 545541.7332 | 166.0234 | 0
5809 | 8 | 0 | 0 | 0.15352 | 6.2792 | 0 | 0 | 0 | 0 | 6.2792 | 0 | 98400 | 0 | 545541.7332 | 171.4662 | 0
5810 | 8 | 0 | 0 | 0.11355 | 4.6444 | 0 | 0 | 0 | 0 | 4.6444 | 0 | 98400 | 0 | 545541.7332 | 175.4919 | 0
5811 | 8 | 0 | 0 | 0.15744 | 6.4395 | 0 | 0 | 0 | 0 | 6.4395 | 0 | 98400 | 0 | 545541.7332 | 181.0737 | 0
5812 | 8 | 0 | 0 | 0.17409 | 7.1202 | 0 | 0 | 0 | 0 | 7.1202 | 0 | 98400 | 0 | 545541.7332 | 187.2455 | 0
5813 | 8 | 0 | 0 | 0.15419 | 6.3065 | 0 | 0 | 0 | 0 | 6.3065 | 0 | 98400 | 0 | 545541.7332 | 192.712 | 0
5814 | 8 | 0 | 0 | 0.18696 | 7.6467 | 0 | 0 | 0 | 0 | 7.6467 | 0 | 98400 | 0 | 545541.7332 | 199.3401 | 0
5815 | 8 | 0 | 0.045075 | 0.33627 | 26.771 | 0 | 0 | 0 | 0 | 26.771 | 0 | 98400 | 0 | 545541.7332 | 222.5452 | 0
5816 | 8 | 1 | 0.21325 | 0.29492 | 73.6484 | 200 | 73.6484 | 126.3516 | 200 | 0 | 0 | 98200 | 200 | 545741.7332 | 96.1936 | 0
5817 | 8 | 1 | 0.41062 | 0.39141 | 134.5954 | 200 | 134.5954 | 65.4046 | 200 | 0 | 0 | 98000 | 200 | 545941.7332 | 30.7891 | 0
5818 | 8 | 0 | 0.60069 | 0.47863 | 193.0547 | 0 | 0 | 0 | 0 | 180 | 13.0547 | 98000 | 13.0547 | 545954.7879 | 186.8131 | 0
5819 | 8 | 0 | 0.75672 | 0.42901 | 236.087 | 0 | 0 | 0 | 0 | 180 | 56.087 | 98000 | 56.087 | 546010.875 | 342.8371 | 0
5820 | 8 | 0 | 0.85873 | 0.56562 | 271.1355 | 0 | 0 | 0 | 0 | 180 | 91.1355 | 98000 | 91.1355 | 546102.0105 | 498.8611 | 0
5821 | 8 | 0 | 0.89417 | 0.59731 | 282.6652 | 0 | 0 | 0 | 0 | 13.7851 | 200 | 98000 | 200 | 546302.0105 | 510.81 | 68.8801
5822 | 8 | 0 | 0.85873 | 0.54572 | 270.3214 | 0 | 0 | 0 | 0 | 0 | 200 | 98000 | 200 | 546502.0105 | 510.81 | 70.3214
5823 | 8 | 0 | 0.75672 | 1 | 259.4407 | 0 | 0 | 0 | 0 | 0 | 200 | 98000 | 200 | 546702.0105 | 510.81 | 59.4407
5824 | 8 | 0 | 0.60069 | 1 | 214.379 | 0 | 0 | 0 | 0 | 0 | 200 | 98000 | 200 | 546902.0105 | 510.81 | 14.379
5825 | 8 | 0 | 0.41062 | 1 | 159.4868 | 0 | 0 | 0 | 0 | 0 | 159.4868 | 98000 | 159.4868 | 547061.4972 | 510.81 | 0
5826 | 8 | 0 | 0.21325 | 1 | 102.486 | 0 | 0 | 0 | 0 | 0 | 102.486 | 98000 | 102.486 | 547163.9833 | 510.81 | 0
5827 | 8 | 0 | 0.045075 | 1 | 53.9177 | 0 | 0 | 0 | 0 | 0 | 53.9177 | 98000 | 53.9177 | 547217.9009 | 510.81 | 0
5828 | 8 | 1 | 0 | 1 | 40.9 | 200 | 40.9 | 159.1 | 200 | 0 | 0 | 97800 | 200 | 547417.9009 | 351.71 | 0
5829 | 8 | 1 | 0 | 1 | 40.9 | 200 | 40.9 | 159.1 | 200 | 0 | 0 | 97600 | 200 | 547617.9009 | 192.61 | 0
5830 | 8 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 97600 | 0 | 547617.9009 | 228.0621 | 0
5831 | 8 | 0 | 0 | 0.88784 | 36.3127 | 0 | 0 | 0 | 0 | 36.3127 | 0 | 97600 | 0 | 547617.9009 | 259.5379 | 0
5832 | 8 | 0 | 0 | 0.62758 | 25.6681 | 0 | 0 | 0 | 0 | 25.6681 | 0 | 97600 | 0 | 547617.9009 | 281.787 | 0
5833 | 9 | 0 | 0 | 0.41525 | 16.9836 | 0 | 0 | 0 | 0 | 16.9836 | 0 | 97600 | 0 | 547617.9009 | 296.5084 | 0
5834 | 9 | 0 | 0 | 0.31439 | 12.8585 | 0 | 0 | 0 | 0 | 12.8585 | 0 | 97600 | 0 | 547617.9009 | 307.6541 | 0
5835 | 9 | 0 | 0 | 0.3052 | 12.4828 | 0 | 0 | 0 | 0 | 12.4828 | 0 | 97600 | 0 | 547617.9009 | 318.4742 | 0
5836 | 9 | 0 | 0 | 0.2966 | 12.1311 | 0 | 0 | 0 | 0 | 12.1311 | 0 | 97600 | 0 | 547617.9009 | 328.9894 | 0
5837 | 9 | 0 | 0 | 0.40077 | 16.3917 | 0 | 0 | 0 | 0 | 16.3917 | 0 | 97600 | 0 | 547617.9009 | 343.1978 | 0
5838 | 9 | 0 | 0 | 0.40036 | 16.3745 | 0 | 0 | 0 | 0 | 16.3745 | 0 | 97600 | 0 | 547617.9009 | 357.3912 | 0
5839 | 9 | 0 | 0.0084 | 0.41301 | 19.318 | 0 | 0 | 0 | 0 | 19.318 | 0 | 97600 | 0 | 547617.9009 | 374.136 | 0
5840 | 9 | 1 | 0.21008 | 0.5119 | 81.6083 | 200 | 81.6083 | 118.3917 | 200 | 0 | 0 | 97400 | 200 | 547817.9009 | 255.7443 | 0
5841 | 9 | 1 | 0.47919 | 0.44634 | 156.6451 | 200 | 156.6451 | 43.3549 | 200 | 0 | 0 | 97200 | 200 | 548017.9009 | 212.3894 | 0
5842 | 9 | 0 | 0.74827 | 0.45877 | 234.8649 | 0 | 0 | 0 | 0 | 180 | 54.8649 | 97200 | 54.8649 | 548072.7658 | 368.4134 | 0
5843 | 9 | 0 | 0.97352 | 0.57112 | 304.5123 | 0 | 0 | 0 | 0 | 164.2785 | 140.2338 | 97200 | 140.2338 | 548212.9996 | 510.81 | 0
5844 | 9 | 0 | 1 | 0.56151 | 311.7658 | 0 | 0 | 0 | 0 | 0 | 200 | 97200 | 200 | 548412.9996 | 510.81 | 111.7658
5845 | 9 | 0 | 1 | 0.4313 | 306.44 | 0 | 0 | 0 | 0 | 0 | 200 | 97200 | 200 | 548612.9996 | 510.81 | 106.44
5846 | 9 | 0 | 1 | 0.3621 | 303.6097 | 0 | 0 | 0 | 0 | 0 | 200 | 97200 | 200 | 548812.9996 | 510.81 | 103.6097
5847 | 9 | 0 | 0.97352 | 0.3316 | 294.7159 | 0 | 0 | 0 | 0 | 0 | 200 | 97200 | 200 | 549012.9996 | 510.81 | 94.7159
5848 | 9 | 0 | 0.74827 | 0.28761 | 227.8645 | 0 | 0 | 0 | 0 | 0 | 200 | 97200 | 200 | 549212.9996 | 510.81 | 27.8645
5849 | 9 | 0 | 0.47919 | 0.45348 | 156.9371 | 0 | 0 | 0 | 0 | 0 | 156.9371 | 97200 | 156.9371 | 549369.9367 | 510.81 | 0
5850 | 9 | 0 | 0.21008 | 0.52755 | 82.2486 | 0 | 0 | 0 | 0 | 0 | 82.2486 | 97200 | 82.2486 | 549452.1852 | 510.81 | 0
5851 | 9 | 0 | 0.0084 | 0.47729 | 21.947 | 0 | 0 | 0 | 0 | 0 | 21.947 | 97200 | 21.947 | 549474.1322 | 510.81 | 0
5852 | 9 | 1 | 0 | 0.35966 | 14.7102 | 200 | 14.7102 | 180 | 194.7102 | 0 | 0 | 97000 | 194.7102 | 549668.8424 | 330.81 | 0
5853 | 9 | 1 | 0 | 0.346 | 14.1513 | 200 | 14.1513 | 180 | 194.1513 | 0 | 0 | 96800 | 194.1513 | 549862.9937 | 150.81 | 0
5854 | 9 | 0 | 0 | 0.36129 | 14.7767 | 0 | 0 | 0 | 0 | 14.7767 | 0 | 96800 | 0 | 549862.9937 | 163.6184 | 0
5855 | 9 | 0 | 0 | 0.24762 | 10.1275 | 0 | 0 | 0 | 0 | 10.1275 | 0 | 96800 | 0 | 549862.9937 | 172.397 | 0
5856 | 9 | 0 | 0 | 0.2406 | 9.8407 | 0 | 0 | 0 | 0 | 9.8407 | 0 | 96800 | 0 | 549862.9937 | 180.9269 | 0
5857 | 9 | 0 | 0 | 0.38123 | 15.5923 | 0 | 0 | 0 | 0 | 15.5923 | 0 | 96800 | 0 | 549862.9937 | 194.4423 | 0
5858 | 9 | 0 | 0 | 0.44531 | 18.2133 | 0 | 0 | 0 | 0 | 18.2133 | 0 | 96800 | 0 | 549862.9937 | 210.2296 | 0
5859 | 9 | 0 | 0 | 0.4073 | 16.6588 | 0 | 0 | 0 | 0 | 16.6588 | 0 | 96800 | 0 | 549862.9937 | 224.6695 | 0
5860 | 9 | 0 | 0 | 0.39571 | 16.1845 | 0 | 0 | 0 | 0 | 16.1845 | 0 | 96800 | 0 | 549862.9937 | 238.6982 | 0
5861 | 9 | 0 | 0 | 0.43791 | 17.9104 | 0 | 0 | 0 | 0 | 17.9104 | 0 | 96800 | 0 | 549862.9937 | 254.2229 | 0
5862 | 9 | 0 | 0 | 0.36116 | 14.7716 | 0 | 0 | 0 | 0 | 14.7716 | 0 | 96800 | 0 | 549862.9937 | 267.0269 | 0
5863 | 9 | 0 | 0.007081 | 0.32829 | 15.4719 | 0 | 0 | 0 | 0 | 15.4719 | 0 | 96800 | 0 | 549862.9937 | 280.438 | 0
5864 | 9 | 1 | 0.17708 | 0.37417 | 66.4449 | 200 | 66.4449 | 133.5551 | 200 | 0 | 0 | 96600 | 200 | 550062.9937 | 146.8829 | 0
5865 | 9 | 1 | 0.40392 | 0.33473 | 130.3419 | 200 | 130.3419 | 69.6581 | 200 | 0 | 0 | 96400 | 200 | 550262.9937 | 77.2248 | 0
5866 | 9 | 0 | 0.63073 | 0.33449 | 195.8365 | 0 | 0 | 0 | 0 | 180 | 15.8365 | 96400 | 15.8365 | 550278.8302 | 233.2488 | 0
5867 | 9 | 0 | 0.8206 | 0.45857 | 255.7453 | 0 | 0 | 0 | 0 | 180 | 75.7453 | 96400 | 75.7453 | 550354.5755 | 389.2728 | 0
5868 | 9 | 0 | 0.94609 | 0.31692 | 286.1926 | 0 | 0 | 0 | 0 | 140.2136 | 145.9789 | 96400 | 145.9789 | 550500.5545 | 510.81 | 0
5869 | 9 | 0 | 0.98989 | 0.36077 | 300.6373 | 0 | 0 | 0 | 0 | 0 | 200 | 96400 | 200 | 550700.5545 | 510.81 | 100.6373
5870 | 9 | 0 | 0.94609 | 0.26599 | 284.1096 | 0 | 0 | 0 | 0 | 0 | 200 | 96400 | 200 | 550900.5545 | 510.81 | 84.1096
5871 | 9 | 0 | 0.8206 | 0.34196 | 250.9759 | 0 | 0 | 0 | 0 | 0 | 200 | 96400 | 200 | 551100.5545 | 510.81 | 50.9759
5872 | 9 | 0 | 0.63073 | 0.3711 | 197.334 | 0 | 0 | 0 | 0 | 0 | 197.334 | 96400 | 197.334 | 551297.8885 | 510.81 | 0
5873 | 9 | 0 | 0.40392 | 0.42141 | 133.8874 | 0 | 0 | 0 | 0 | 0 | 133.8874 | 96400 | 133.8874 | 551431.7758 | 510.81 | 0
5874 | 9 | 0 | 0.17708 | 0.52365 | 72.5587 | 0 | 0 | 0 | 0 | 0 | 72.5587 | 96400 | 72.5587 | 551504.3346 | 510.81 | 0
5875 | 9 | 0 | 0.007081 | 0.64475 | 28.4154 | 0 | 0 | 0 | 0 | 0 | 28.4154 | 96400 | 28.4154 | 551532.75 | 510.81 | 0
5876 | 9 | 1 | 0 | 0.51135 | 20.9143 | 200 | 20.9143 | 179.0857 | 200 | 0 | 0 | 96200 | 200 | 551732.75 | 331.7243 | 0
5877 | 9 | 1 | 0 | 0.61545 | 25.1718 | 200 | 25.1718 | 174.8282 | 200 | 0 | 0 | 96000 | 200 | 551932.75 | 156.8961 | 0
5878 | 9 | 0 | 0 | 0.75375 | 30.8285 | 0 | 0 | 0 | 0 | 30.8285 | 0 | 96000 | 0 | 551932.75 | 183.6182 | 0
5879 | 9 | 0 | 0 | 0.64698 | 26.4616 | 0 | 0 | 0 | 0 | 26.4616 | 0 | 96000 | 0 | 551932.75 | 206.5551 | 0
5880 | 9 | 0 | 0 | 0.38911 | 15.9146 | 0 | 0 | 0 | 0 | 15.9146 | 0 | 96000 | 0 | 551932.75 | 220.3498 | 0
5881 | 9 | 0 | 0 | 0.25988 | 10.629 | 0 | 0 | 0 | 0 | 10.629 | 0 | 96000 | 0 | 551932.75 | 229.5631 | 0
5882 | 9 | 0 | 0 | 0.28173 | 11.5229 | 0 | 0 | 0 | 0 | 11.5229 | 0 | 96000 | 0 | 551932.75 | 239.5511 | 0
5883 | 9 | 0 | 0 | 0.26187 | 10.7103 | 0 | 0 | 0 | 0 | 10.7103 | 0 | 96000 | 0 | 551932.75 | 248.8348 | 0
5884 | 9 | 0 | 0 | 0.40224 | 16.4516 | 0 | 0 | 0 | 0 | 16.4516 | 0 | 96000 | 0 | 551932.75 | 263.095 | 0
5885 | 9 | 0 | 0 | 0.49573 | 20.2752 | 0 | 0 | 0 | 0 | 20.2752 | 0 | 96000 | 0 | 551932.75 | 280.6696 | 0
5886 | 9 | 0 | 0 | 0.38076 | 15.5732 | 0 | 0 | 0 | 0 | 15.5732 | 0 | 96000 | 0 | 551932.75 | 294.1684 | 0
5887 | 9 | 0 | 0.007394 | 0.50895 | 22.9514 | 0 | 0 | 0 | 0 | 22.9514 | 0 | 96000 | 0 | 551932.75 | 314.0627 | 0
5888 | 9 | 1 | 0.1849 | 0.65236 | 80.0809 | 200 | 80.0809 | 119.9191 | 200 | 0 | 0 | 95800 | 200 | 552132.75 | 194.1436 | 0
5889 | 9 | 1 | 0.42175 | 0.72739 | 151.5522 | 200 | 151.5522 | 48.4478 | 200 | 0 | 0 | 95600 | 200 | 552332.75 | 145.6958 | 0
5890 | 9 | 0 | 0.65858 | 0.84214 | 224.6424 | 0 | 0 | 0 | 0 | 180 | 44.6424 | 95600 | 44.6424 | 552377.3924 | 301.7198 | 0
5891 | 9 | 0 | 0.85683 | 1 | 288.3537 | 0 | 0 | 0 | 0 | 180 | 108.3537 | 95600 | 108.3537 | 552485.746 | 457.7438 | 0
5892 | 9 | 0 | 0.98786 | 1 | 326.1943 | 0 | 0 | 0 | 0 | 61.2208 | 200 | 95600 | 200 | 552685.746 | 510.81 | 64.9735
5893 | 9 | 0 | 1 | 0.72423 | 318.4208 | 0 | 0 | 0 | 0 | 0 | 200 | 95600 | 200 | 552885.746 | 510.81 | 118.4208
5894 | 9 | 0 | 0.98786 | 0.68036 | 313.1208 | 0 | 0 | 0 | 0 | 0 | 200 | 95600 | 200 | 553085.746 | 510.81 | 113.1208
5895 | 9 | 0 | 0.85683 | 0.66577 | 274.6835 | 0 | 0 | 0 | 0 | 0 | 200 | 95600 | 200 | 553285.746 | 510.81 | 74.6835
5896 | 9 | 0 | 0.65858 | 0.57956 | 213.9028 | 0 | 0 | 0 | 0 | 0 | 200 | 95600 | 200 | 553485.746 | 510.81 | 13.9028
5897 | 9 | 0 | 0.42175 | 0.38938 | 137.7277 | 0 | 0 | 0 | 0 | 0 | 137.7277 | 95600 | 137.7277 | 553623.4737 | 510.81 | 0
5898 | 9 | 0 | 0.1849 | 0.34622 | 67.5598 | 0 | 0 | 0 | 0 | 0 | 67.5598 | 95600 | 67.5598 | 553691.0335 | 510.81 | 0
5899 | 9 | 0 | 0.007394 | 0.30672 | 14.6803 | 0 | 0 | 0 | 0 | 0 | 14.6803 | 95600 | 14.6803 | 553705.7138 | 510.81 | 0
5900 | 9 | 1 | 0 | 0.24433 | 9.9933 | 200 | 9.9933 | 180 | 189.9933 | 0 | 0 | 95400 | 189.9933 | 553895.7071 | 330.81 | 0
5901 | 9 | 1 | 0 | 0.13561 | 5.5464 | 200 | 5.5464 | 180 | 185.5464 | 0 | 0 | 95200 | 185.5464 | 554081.2534 | 150.81 | 0
5902 | 9 | 0 | 0 | 0.17897 | 7.3199 | 0 | 0 | 0 | 0 | 7.3199 | 0 | 95200 | 0 | 554081.2534 | 157.1549 | 0
5903 | 9 | 0 | 0 | 0.14481 | 5.9229 | 0 | 0 | 0 | 0 | 5.9229 | 0 | 95200 | 0 | 554081.2534 | 162.2889 | 0
5904 | 9 | 0 | 0 | 0.1652 | 6.7569 | 0 | 0 | 0 | 0 | 6.7569 | 0 | 95200 | 0 | 554081.2534 | 168.1458 | 0
5905 | 9 | 0 | 0 | 0.16704 | 6.8318 | 0 | 0 | 0 | 0 | 6.8318 | 0 | 95200 | 0 | 554081.2534 | 174.0676 | 0
5906 | 9 | 0 | 0 | 0.3451 | 14.1147 | 0 | 0 | 0 | 0 | 14.1147 | 0 | 95200 | 0 | 554081.2534 | 186.3022 | 0
5907 | 9 | 0 | 0 | 0.51475 | 21.0533 | 0 | 0 | 0 | 0 | 21.0533 | 0 | 95200 | 0 | 554081.2534 | 204.5512 | 0
5908 | 9 | 0 | 0 | 0.56779 | 23.2226 | 0 | 0 | 0 | 0 | 23.2226 | 0 | 95200 | 0 | 554081.2534 | 224.6805 | 0
5909 | 9 | 0 | 0 | 0.60829 | 24.8791 | 0 | 0 | 0 | 0 | 24.8791 | 0 | 95200 | 0 | 554081.2534 | 246.2458 | 0
5910 | 9 | 0 | 0 | 0.65881 | 26.9454 | 0 | 0 | 0 | 0 | 26.9454 | 0 | 95200 | 0 | 554081.2534 | 269.602 | 0
5911 | 9 | 0 | 0.008917 | 0.56738 | 25.7812 | 0 | 0 | 0 | 0 | 25.7812 | 0 | 95200 | 0 | 554081.2534 | 291.9491 | 0
5912 | 9 | 1 | 0.22299 | 0.66049 | 91.4137 | 200 | 91.4137 | 108.5863 | 200 | 0 | 0 | 95000 | 200 | 554281.2534 | 183.3628 | 0
5913 | 9 | 1 | 0.50863 | 0.67392 | 174.4569 | 200 | 174.4569 | 25.5431 | 200 | 0 | 0 | 94800 | 200 | 554481.2534 | 157.8197 | 0
5914 | 9 | 0 | 0.79426 | 0.75299 | 260.1779 | 0 | 0 | 0 | 0 | 180 | 80.1779 | 94800 | 80.1779 | 554561.4314 | 313.8437 | 0
5915 | 9 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 180 | 149.7 | 94800 | 149.7 | 554711.1314 | 469.8677 | 0
5916 | 9 | 0 | 1 | 0.76019 | 319.8919 | 0 | 0 | 0 | 0 | 47.2338 | 200 | 94800 | 200 | 554911.1314 | 510.81 | 72.658
5917 | 9 | 0 | 1 | 0.54679 | 311.1635 | 0 | 0 | 0 | 0 | 0 | 200 | 94800 | 200 | 555111.1314 | 510.81 | 111.1635
5918 | 9 | 0 | 1 | 0.4555 | 307.43 | 0 | 0 | 0 | 0 | 0 | 200 | 94800 | 200 | 555311.1314 | 510.81 | 107.43
5919 | 9 | 0 | 1 | 0.63148 | 314.6274 | 0 | 0 | 0 | 0 | 0 | 200 | 94800 | 200 | 555511.1314 | 510.81 | 114.6274
5920 | 9 | 0 | 0.79426 | 0.70806 | 258.3404 | 0 | 0 | 0 | 0 | 0 | 200 | 94800 | 200 | 555711.1314 | 510.81 | 58.3404
5921 | 9 | 0 | 0.50863 | 0.97593 | 186.8093 | 0 | 0 | 0 | 0 | 0 | 186.8093 | 94800 | 186.8093 | 555897.9407 | 510.81 | 0
5922 | 9 | 0 | 0.22299 | 1 | 105.2998 | 0 | 0 | 0 | 0 | 0 | 105.2998 | 94800 | 105.2998 | 556003.2405 | 510.81 | 0
5923 | 9 | 0 | 0.008917 | 0.95181 | 41.5043 | 0 | 0 | 0 | 0 | 0 | 41.5043 | 94800 | 41.5043 | 556044.7448 | 510.81 | 0
5924 | 9 | 1 | 0 | 1 | 40.9 | 200 | 40.9 | 159.1 | 200 | 0 | 0 | 94600 | 200 | 556244.7448 | 351.71 | 0
5925 | 9 | 1 | 0 | 1 | 40.9 | 200 | 40.9 | 159.1 | 200 | 0 | 0 | 94400 | 200 | 556444.7448 | 192.61 | 0
5926 | 9 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 94400 | 0 | 556444.7448 | 228.0621 | 0
5927 | 9 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 94400 | 0 | 556444.7448 | 263.5142 | 0
5928 | 9 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 94400 | 0 | 556444.7448 | 298.9664 | 0
5929 | 9 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 94400 | 0 | 556444.7448 | 334.4185 | 0
5930 | 9 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 94400 | 0 | 556444.7448 | 369.8706 | 0
5931 | 9 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 94400 | 0 | 556444.7448 | 405.3227 | 0
5932 | 9 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 94400 | 0 | 556444.7448 | 440.7748 | 0
5933 | 9 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 94400 | 0 | 556444.7448 | 476.227 | 0
5934 | 9 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 39.8974 | 1.0026 | 94400 | 1.0026 | 556445.7475 | 510.81 | 0
5935 | 9 | 0 | 0.007949 | 0.73582 | 32.3906 | 0 | 0 | 0 | 0 | 0 | 32.3906 | 94400 | 32.3906 | 556478.1381 | 510.81 | 0
5936 | 9 | 1 | 0.1988 | 0.58692 | 81.4192 | 200 | 81.4192 | 118.5808 | 200 | 0 | 0 | 94200 | 200 | 556678.1381 | 392.2292 | 0
5937 | 9 | 1 | 0.45346 | 0.9683 | 170.5623 | 200 | 170.5623 | 29.4377 | 200 | 0 | 0 | 94000 | 200 | 556878.1381 | 362.7915 | 0
5938 | 9 | 0 | 0.7081 | 0.59478 | 228.8243 | 0 | 0 | 0 | 0 | 170.7643 | 58.0599 | 94000 | 58.0599 | 556936.198 | 510.81 | 0
5939 | 9 | 0 | 0.92125 | 0.64458 | 292.4201 | 0 | 0 | 0 | 0 | 0 | 200 | 94000 | 200 | 557136.198 | 510.81 | 92.4201
5940 | 9 | 0 | 1 | 0.59025 | 312.9412 | 0 | 0 | 0 | 0 | 0 | 200 | 94000 | 200 | 557336.198 | 510.81 | 112.9412
5941 | 9 | 0 | 1 | 0.29899 | 301.0287 | 0 | 0 | 0 | 0 | 0 | 200 | 94000 | 200 | 557536.198 | 510.81 | 101.0287
5942 | 9 | 0 | 1 | 0.30023 | 301.0796 | 0 | 0 | 0 | 0 | 0 | 200 | 94000 | 200 | 557736.198 | 510.81 | 101.0796
5943 | 9 | 0 | 0.92125 | 0.20177 | 274.3096 | 0 | 0 | 0 | 0 | 0 | 200 | 94000 | 200 | 557936.198 | 510.81 | 74.3096
5944 | 9 | 0 | 0.7081 | 0.29155 | 216.4223 | 0 | 0 | 0 | 0 | 0 | 200 | 94000 | 200 | 558136.198 | 510.81 | 16.4223
5945 | 9 | 0 | 0.45346 | 0.28164 | 142.4781 | 0 | 0 | 0 | 0 | 0 | 142.4781 | 94000 | 142.4781 | 558278.6761 | 510.81 | 0
5946 | 9 | 0 | 0.1988 | 0.40373 | 73.9266 | 0 | 0 | 0 | 0 | 0 | 73.9266 | 94000 | 73.9266 | 558352.6027 | 510.81 | 0
5947 | 9 | 0 | 0.007949 | 0.31996 | 15.382 | 0 | 0 | 0 | 0 | 0 | 15.382 | 94000 | 15.382 | 558367.9847 | 510.81 | 0
5948 | 9 | 1 | 0 | 0.29278 | 11.9748 | 200 | 11.9748 | 180 | 191.9748 | 0 | 0 | 93800 | 191.9748 | 558559.9595 | 330.81 | 0
5949 | 9 | 1 | 0 | 0.3334 | 13.6361 | 200 | 13.6361 | 180 | 193.6361 | 0 | 0 | 93600 | 193.6361 | 558753.5955 | 150.81 | 0
5950 | 9 | 0 | 0 | 0.3559 | 14.5564 | 0 | 0 | 0 | 0 | 14.5564 | 0 | 93600 | 0 | 558753.5955 | 163.4275 | 0
5951 | 9 | 0 | 0 | 0.37066 | 15.1599 | 0 | 0 | 0 | 0 | 15.1599 | 0 | 93600 | 0 | 558753.5955 | 176.5681 | 0
5952 | 9 | 0 | 0 | 0.42237 | 17.2751 | 0 | 0 | 0 | 0 | 17.2751 | 0 | 93600 | 0 | 558753.5955 | 191.5421 | 0
5953 | 9 | 0 | 0 | 0.22691 | 9.2807 | 0 | 0 | 0 | 0 | 9.2807 | 0 | 93600 | 0 | 558753.5955 | 199.5866 | 0
5954 | 9 | 0 | 0 | 0.23657 | 9.6758 | 0 | 0 | 0 | 0 | 9.6758 | 0 | 93600 | 0 | 558753.5955 | 207.9736 | 0
5955 | 9 | 0 | 0 | 0.25677 | 10.5017 | 0 | 0 | 0 | 0 | 10.5017 | 0 | 93600 | 0 | 558753.5955 | 217.0765 | 0
5956 | 9 | 0 | 0 | 0.3113 | 12.732 | 0 | 0 | 0 | 0 | 12.732 | 0 | 93600 | 0 | 558753.5955 | 228.1126 | 0
5957 | 9 | 0 | 0 | 0.26676 | 10.9107 | 0 | 0 | 0 | 0 | 10.9107 | 0 | 93600 | 0 | 558753.5955 | 237.57 | 0
5958 | 9 | 0 | 0 | 0.32101 | 13.1293 | 0 | 0 | 0 | 0 | 13.1293 | 0 | 93600 | 0 | 558753.5955 | 248.9505 | 0
5959 | 9 | 0 | 0.007565 | 0.27512 | 13.4373 | 0 | 0 | 0 | 0 | 13.4373 | 0 | 93600 | 0 | 558753.5955 | 260.5979 | 0
5960 | 9 | 1 | 0.18918 | 0.29931 | 66.8758 | 200 | 66.8758 | 133.1242 | 200 | 0 | 0 | 93400 | 200 | 558953.5955 | 127.4738 | 0
5961 | 9 | 1 | 0.43151 | 0.42887 | 142.1593 | 200 | 142.1593 | 57.8407 | 200 | 0 | 0 | 93200 | 200 | 559153.5955 | 69.6331 | 0
5962 | 9 | 0 | 0.67381 | 0.55987 | 217.4955 | 0 | 0 | 0 | 0 | 180 | 37.4955 | 93200 | 37.4955 | 559191.0911 | 225.6571 | 0
5963 | 9 | 0 | 0.87665 | 0.3516 | 267.556 | 0 | 0 | 0 | 0 | 180 | 87.556 | 93200 | 87.556 | 559278.6471 | 381.6811 | 0
5964 | 9 | 0 | 1 | 0.36415 | 303.6937 | 0 | 0 | 0 | 0 | 148.9719 | 154.7218 | 93200 | 154.7218 | 559433.3689 | 510.81 | 0
5965 | 9 | 0 | 1 | 0.40804 | 305.4887 | 0 | 0 | 0 | 0 | 0 | 200 | 93200 | 200 | 559633.3689 | 510.81 | 105.4887
5966 | 9 | 0 | 1 | 0.46177 | 307.6865 | 0 | 0 | 0 | 0 | 0 | 200 | 93200 | 200 | 559833.3689 | 510.81 | 107.6865
5967 | 9 | 0 | 0.87665 | 0.46697 | 272.2748 | 0 | 0 | 0 | 0 | 0 | 200 | 93200 | 200 | 560033.3689 | 510.81 | 72.2748
5968 | 9 | 0 | 0.67381 | 0.42917 | 212.1498 | 0 | 0 | 0 | 0 | 0 | 200 | 93200 | 200 | 560233.3689 | 510.81 | 12.1498
5969 | 9 | 0 | 0.43151 | 0.36615 | 139.5941 | 0 | 0 | 0 | 0 | 0 | 139.5941 | 93200 | 139.5941 | 560372.963 | 510.81 | 0
5970 | 9 | 0 | 0.18918 | 0.34357 | 68.6862 | 0 | 0 | 0 | 0 | 0 | 68.6862 | 93200 | 68.6862 | 560441.6492 | 510.81 | 0
5971 | 9 | 0 | 0.007565 | 0.35221 | 16.59 | 0 | 0 | 0 | 0 | 0 | 16.59 | 93200 | 16.59 | 560458.2392 | 510.81 | 0
5972 | 9 | 1 | 0 | 0.37752 | 15.4408 | 200 | 15.4408 | 180 | 195.4408 | 0 | 0 | 93000 | 195.4408 | 560653.68 | 330.81 | 0
5973 | 9 | 1 | 0 | 0.26182 | 10.7086 | 200 | 10.7086 | 180 | 190.7086 | 0 | 0 | 92800 | 190.7086 | 560844.3885 | 150.81 | 0
5974 | 9 | 0 | 0 | 0.17696 | 7.2378 | 0 | 0 | 0 | 0 | 7.2378 | 0 | 92800 | 0 | 560844.3885 | 157.0837 | 0
5975 | 9 | 0 | 0 | 0.13464 | 5.5066 | 0 | 0 | 0 | 0 | 5.5066 | 0 | 92800 | 0 | 560844.3885 | 161.8568 | 0
5976 | 9 | 0 | 0 | 0.15749 | 6.4415 | 0 | 0 | 0 | 0 | 6.4415 | 0 | 92800 | 0 | 560844.3885 | 167.4403 | 0
5977 | 9 | 0 | 0 | 0.20447 | 8.3628 | 0 | 0 | 0 | 0 | 8.3628 | 0 | 92800 | 0 | 560844.3885 | 174.6892 | 0
5978 | 9 | 0 | 0 | 0.31199 | 12.7604 | 0 | 0 | 0 | 0 | 12.7604 | 0 | 92800 | 0 | 560844.3885 | 185.7499 | 0
5979 | 9 | 0 | 0 | 0.26774 | 10.9506 | 0 | 0 | 0 | 0 | 10.9506 | 0 | 92800 | 0 | 560844.3885 | 195.2419 | 0
5980 | 9 | 0 | 0 | 0.35382 | 14.4714 | 0 | 0 | 0 | 0 | 14.4714 | 0 | 92800 | 0 | 560844.3885 | 207.7857 | 0
5981 | 9 | 0 | 0 | 0.331 | 13.5379 | 0 | 0 | 0 | 0 | 13.5379 | 0 | 92800 | 0 | 560844.3885 | 219.5203 | 0
5982 | 9 | 0 | 0 | 0.57251 | 23.4157 | 0 | 0 | 0 | 0 | 23.4157 | 0 | 92800 | 0 | 560844.3885 | 239.817 | 0
5983 | 9 | 0 | 0.007729 | 0.46348 | 21.1884 | 0 | 0 | 0 | 0 | 21.1884 | 0 | 92800 | 0 | 560844.3885 | 258.1831 | 0
5984 | 9 | 1 | 0.19328 | 0.45458 | 74.4107 | 200 | 74.4107 | 125.5893 | 200 | 0 | 0 | 92600 | 200 | 561044.3885 | 132.5938 | 0
5985 | 9 | 1 | 0.44086 | 0.40671 | 143.9544 | 200 | 143.9544 | 56.0456 | 200 | 0 | 0 | 92400 | 200 | 561244.3885 | 76.5482 | 0
5986 | 9 | 0 | 0.68842 | 0.52004 | 220.0845 | 0 | 0 | 0 | 0 | 180 | 40.0845 | 92400 | 40.0845 | 561284.4731 | 232.5722 | 0
5987 | 9 | 0 | 0.89565 | 0.88241 | 294.7542 | 0 | 0 | 0 | 0 | 180 | 114.7542 | 92400 | 114.7542 | 561399.2272 | 388.5962 | 0
5988 | 9 | 0 | 1 | 0.62037 | 314.1731 | 0 | 0 | 0 | 0 | 140.9942 | 173.1789 | 92400 | 173.1789 | 561572.4062 | 510.81 | 0
5989 | 9 | 0 | 1 | 0.51119 | 309.7079 | 0 | 0 | 0 | 0 | 0 | 200 | 92400 | 200 | 561772.4062 | 510.81 | 109.7079
5990 | 9 | 0 | 1 | 0.41515 | 305.7795 | 0 | 0 | 0 | 0 | 0 | 200 | 92400 | 200 | 561972.4062 | 510.81 | 105.7795
5991 | 9 | 0 | 0.89565 | 0.35188 | 273.0552 | 0 | 0 | 0 | 0 | 0 | 200 | 92400 | 200 | 562172.4062 | 510.81 | 73.0552
5992 | 9 | 0 | 0.68842 | 0.34236 | 212.8176 | 0 | 0 | 0 | 0 | 0 | 200 | 92400 | 200 | 562372.4062 | 510.81 | 12.8176
5993 | 9 | 0 | 0.44086 | 0.46768 | 146.4479 | 0 | 0 | 0 | 0 | 0 | 146.4479 | 92400 | 146.4479 | 562518.8541 | 510.81 | 0
5994 | 9 | 0 | 0.19328 | 0.31808 | 68.828 | 0 | 0 | 0 | 0 | 0 | 68.828 | 92400 | 68.828 | 562587.6821 | 510.81 | 0
5995 | 9 | 0 | 0.007729 | 0.17652 | 9.4519 | 0 | 0 | 0 | 0 | 0 | 9.4519 | 92400 | 9.4519 | 562597.134 | 510.81 | 0
5996 | 9 | 1 | 0 | 0.1755 | 7.1779 | 200 | 7.1779 | 180 | 187.1779 | 0 | 0 | 92200 | 187.1779 | 562784.3119 | 330.81 | 0
5997 | 9 | 1 | 0 | 0.31535 | 12.8977 | 200 | 12.8977 | 180 | 192.8977 | 0 | 0 | 92000 | 192.8977 | 562977.2095 | 150.81 | 0
5998 | 9 | 0 | 0 | 0.33155 | 13.5604 | 0 | 0 | 0 | 0 | 13.5604 | 0 | 92000 | 0 | 562977.2095 | 162.5642 | 0
5999 | 9 | 0 | 0 | 0.52325 | 21.4008 | 0 | 0 | 0 | 0 | 21.4008 | 0 | 92000 | 0 | 562977.2095 | 181.1143 | 0
6000 | 9 | 0 | 0 | 0.47473 | 19.4163 | 0 | 0 | 0 | 0 | 19.4163 | 0 | 92000 | 0 | 562977.2095 | 197.9444 | 0
6001 | 9 | 0 | 0 | 0.60012 | 24.5451 | 0 | 0 | 0 | 0 | 24.5451 | 0 | 92000 | 0 | 562977.2095 | 219.2201 | 0
6002 | 9 | 0 | 0 | 0.52299 | 21.3903 | 0 | 0 | 0 | 0 | 21.3903 | 0 | 92000 | 0 | 562977.2095 | 237.7612 | 0
6003 | 9 | 0 | 0 | 0.3713 | 15.186 | 0 | 0 | 0 | 0 | 15.186 | 0 | 92000 | 0 | 562977.2095 | 250.9244 | 0
6004 | 9 | 0 | 0 | 0.53137 | 21.7329 | 0 | 0 | 0 | 0 | 21.7329 | 0 | 92000 | 0 | 562977.2095 | 269.7625 | 0
6005 | 9 | 0 | 0 | 0.80982 | 33.1215 | 0 | 0 | 0 | 0 | 33.1215 | 0 | 92000 | 0 | 562977.2095 | 298.4722 | 0
6006 | 9 | 0 | 0 | 0.91156 | 37.283 | 0 | 0 | 0 | 0 | 37.283 | 0 | 92000 | 0 | 562977.2095 | 330.7891 | 0
6007 | 9 | 0 | 0.007665 | 0.55713 | 25.0002 | 0 | 0 | 0 | 0 | 25.0002 | 0 | 92000 | 0 | 562977.2095 | 352.4592 | 0
6008 | 9 | 1 | 0.19169 | 0.38893 | 71.2661 | 200 | 71.2661 | 128.7339 | 200 | 0 | 0 | 91800 | 200 | 563177.2095 | 223.7253 | 0
6009 | 9 | 1 | 0.43723 | 0.37563 | 141.6347 | 200 | 141.6347 | 58.3653 | 200 | 0 | 0 | 91600 | 200 | 563377.2095 | 165.3601 | 0
6010 | 9 | 0 | 0.68275 | 0.41389 | 214.1063 | 0 | 0 | 0 | 0 | 180 | 34.1063 | 91600 | 34.1063 | 563411.3158 | 321.3841 | 0
6011 | 9 | 0 | 0.88828 | 0.32464 | 269.8117 | 0 | 0 | 0 | 0 | 180 | 89.8117 | 91600 | 89.8117 | 563501.1276 | 477.4081 | 0
6012 | 9 | 0 | 1 | 0.27345 | 299.9842 | 0 | 0 | 0 | 0 | 38.5348 | 200 | 91600 | 200 | 563701.1276 | 510.81 | 61.4495
6013 | 9 | 0 | 1 | 0.30287 | 301.1874 | 0 | 0 | 0 | 0 | 0 | 200 | 91600 | 200 | 563901.1276 | 510.81 | 101.1874
6014 | 9 | 0 | 1 | 0.36269 | 303.6339 | 0 | 0 | 0 | 0 | 0 | 200 | 91600 | 200 | 564101.1276 | 510.81 | 103.6339
6015 | 9 | 0 | 0.88828 | 0.46362 | 275.496 | 0 | 0 | 0 | 0 | 0 | 200 | 91600 | 200 | 564301.1276 | 510.81 | 75.496
6016 | 9 | 0 | 0.68275 | 0.48746 | 217.1154 | 0 | 0 | 0 | 0 | 0 | 200 | 91600 | 200 | 564501.1276 | 510.81 | 17.1154
6017 | 9 | 0 | 0.43723 | 0.50154 | 146.7844 | 0 | 0 | 0 | 0 | 0 | 146.7844 | 91600 | 146.7844 | 564647.9119 | 510.81 | 0
6018 | 9 | 0 | 0.19169 | 0.49704 | 75.6878 | 0 | 0 | 0 | 0 | 0 | 75.6878 | 91600 | 75.6878 | 564723.5997 | 510.81 | 0
6019 | 9 | 0 | 0.007665 | 0.50129 | 22.7163 | 0 | 0 | 0 | 0 | 0 | 22.7163 | 91600 | 22.7163 | 564746.316 | 510.81 | 0
6020 | 9 | 1 | 0 | 0.45709 | 18.6949 | 200 | 18.6949 | 180 | 198.6949 | 0 | 0 | 91400 | 198.6949 | 564945.0109 | 330.81 | 0
6021 | 9 | 1 | 0 | 0.3995 | 16.3395 | 200 | 16.3395 | 180 | 196.3395 | 0 | 0 | 91200 | 196.3395 | 565141.3505 | 150.81 | 0
6022 | 9 | 0 | 0 | 0.43372 | 17.7393 | 0 | 0 | 0 | 0 | 17.7393 | 0 | 91200 | 0 | 565141.3505 | 166.1864 | 0
6023 | 9 | 0 | 0 | 0.3935 | 16.0943 | 0 | 0 | 0 | 0 | 16.0943 | 0 | 91200 | 0 | 565141.3505 | 180.137 | 0
6024 | 9 | 0 | 0 | 0.52405 | 21.4338 | 0 | 0 | 0 | 0 | 21.4338 | 0 | 91200 | 0 | 565141.3505 | 198.7158 | 0
6025 | 9 | 0 | 0 | 0.30756 | 12.5794 | 0 | 0 | 0 | 0 | 12.5794 | 0 | 91200 | 0 | 565141.3505 | 209.6196 | 0
6026 | 9 | 0 | 0 | 0.21737 | 8.8904 | 0 | 0 | 0 | 0 | 8.8904 | 0 | 91200 | 0 | 565141.3505 | 217.3258 | 0
6027 | 9 | 0 | 0 | 0.15993 | 6.5411 | 0 | 0 | 0 | 0 | 6.5411 | 0 | 91200 | 0 | 565141.3505 | 222.9956 | 0
6028 | 9 | 0 | 0 | 0.19131 | 7.8247 | 0 | 0 | 0 | 0 | 7.8247 | 0 | 91200 | 0 | 565141.3505 | 229.778 | 0
6029 | 9 | 0 | 0 | 0.16684 | 6.8238 | 0 | 0 | 0 | 0 | 6.8238 | 0 | 91200 | 0 | 565141.3505 | 235.6929 | 0
6030 | 9 | 0 | 0 | 0.15591 | 6.3768 | 0 | 0 | 0 | 0 | 6.3768 | 0 | 91200 | 0 | 565141.3505 | 241.2204 | 0
6031 | 9 | 0 | 0.007054 | 0.15303 | 8.2962 | 0 | 0 | 0 | 0 | 8.2962 | 0 | 91200 | 0 | 565141.3505 | 248.4116 | 0
6032 | 9 | 1 | 0.17641 | 0.19346 | 58.8602 | 200 | 58.8602 | 141.1398 | 200 | 0 | 0 | 91000 | 200 | 565341.3505 | 107.2717 | 0
6033 | 9 | 1 | 0.40239 | 0.25648 | 126.6999 | 200 | 126.6999 | 73.3001 | 200 | 0 | 0 | 90800 | 200 | 565541.3505 | 33.9716 | 0
6034 | 9 | 0 | 0.62835 | 0.18267 | 188.9382 | 0 | 0 | 0 | 0 | 180 | 8.9382 | 90800 | 8.9382 | 565550.2887 | 189.9956 | 0
6035 | 9 | 0 | 0.8175 | 0.21084 | 244.7167 | 0 | 0 | 0 | 0 | 180 | 64.7167 | 90800 | 64.7167 | 565615.0053 | 346.0196 | 0
6036 | 9 | 0 | 0.94251 | 0.24205 | 282.0964 | 0 | 0 | 0 | 0 | 180 | 102.0964 | 90800 | 102.0964 | 565717.1018 | 502.0436 | 0
6037 | 9 | 0 | 0.98615 | 0.2228 | 293.9122 | 0 | 0 | 0 | 0 | 10.1135 | 200 | 90800 | 200 | 565917.1018 | 510.81 | 83.7987
6038 | 9 | 0 | 0.94251 | 0.24729 | 282.3109 | 0 | 0 | 0 | 0 | 0 | 200 | 90800 | 200 | 566117.1018 | 510.81 | 82.3109
6039 | 9 | 0 | 0.8175 | 0.29525 | 248.1689 | 0 | 0 | 0 | 0 | 0 | 200 | 90800 | 200 | 566317.1018 | 510.81 | 48.1689
6040 | 9 | 0 | 0.62835 | 0.31489 | 194.3461 | 0 | 0 | 0 | 0 | 0 | 194.3461 | 90800 | 194.3461 | 566511.4479 | 510.81 | 0
6041 | 9 | 0 | 0.40239 | 0.34687 | 130.3971 | 0 | 0 | 0 | 0 | 0 | 130.3971 | 90800 | 130.3971 | 566641.8449 | 510.81 | 0
6042 | 9 | 0 | 0.17641 | 0.26348 | 61.724 | 0 | 0 | 0 | 0 | 0 | 61.724 | 90800 | 61.724 | 566703.569 | 510.81 | 0
6043 | 9 | 0 | 0.007054 | 0.34474 | 16.137 | 0 | 0 | 0 | 0 | 0 | 16.137 | 90800 | 16.137 | 566719.706 | 510.81 | 0
6044 | 9 | 1 | 0 | 0.30349 | 12.4125 | 200 | 12.4125 | 180 | 192.4125 | 0 | 0 | 90600 | 192.4125 | 566912.1185 | 330.81 | 0
6045 | 9 | 1 | 0 | 0.24883 | 10.1771 | 200 | 10.1771 | 180 | 190.1771 | 0 | 0 | 90400 | 190.1771 | 567102.2956 | 150.81 | 0
6046 | 9 | 0 | 0 | 0.24643 | 10.0791 | 0 | 0 | 0 | 0 | 10.0791 | 0 | 90400 | 0 | 567102.2956 | 159.5466 | 0
6047 | 9 | 0 | 0 | 0.23263 | 9.5144 | 0 | 0 | 0 | 0 | 9.5144 | 0 | 90400 | 0 | 567102.2956 | 167.7937 | 0
6048 | 9 | 0 | 0 | 0.16134 | 6.5989 | 0 | 0 | 0 | 0 | 6.5989 | 0 | 90400 | 0 | 567102.2956 | 173.5136 | 0
6049 | 9 | 0 | 0 | 0.12162 | 4.9744 | 0 | 0 | 0 | 0 | 4.9744 | 0 | 90400 | 0 | 567102.2956 | 177.8254 | 0
6050 | 9 | 0 | 0 | 0.11686 | 4.7795 | 0 | 0 | 0 | 0 | 4.7795 | 0 | 90400 | 0 | 567102.2956 | 181.9683 | 0
6051 | 9 | 0 | 0 | 0.12979 | 5.3085 | 0 | 0 | 0 | 0 | 5.3085 | 0 | 90400 | 0 | 567102.2956 | 186.5697 | 0
6052 | 9 | 0 | 0 | 0.17852 | 7.3014 | 0 | 0 | 0 | 0 | 7.3014 | 0 | 90400 | 0 | 567102.2956 | 192.8986 | 0
6053 | 9 | 0 | 0 | 0.25491 | 10.4259 | 0 | 0 | 0 | 0 | 10.4259 | 0 | 90400 | 0 | 567102.2956 | 201.9358 | 0
6054 | 9 | 0 | 0 | 0.15714 | 6.4271 | 0 | 0 | 0 | 0 | 6.4271 | 0 | 90400 | 0 | 567102.2956 | 207.5068 | 0
6055 | 9 | 0 | 0.008173 | 0.20828 | 10.8789 | 0 | 0 | 0 | 0 | 10.8789 | 0 | 90400 | 0 | 567102.2956 | 216.9366 | 0
6056 | 9 | 1 | 0.20439 | 0.23061 | 68.4588 | 200 | 68.4588 | 131.5412 | 200 | 0 | 0 | 90200 | 200 | 567302.2956 | 85.3954 | 0
6057 | 9 | 1 | 0.4662 | 0.28179 | 146.1627 | 200 | 146.1627 | 53.8373 | 200 | 0 | 0 | 90000 | 200 | 567502.2956 | 31.5582 | 0
6058 | 9 | 0 | 0.72799 | 0.24309 | 220.1847 | 0 | 0 | 0 | 0 | 180 | 40.1847 | 90000 | 40.1847 | 567542.4803 | 187.5822 | 0
6059 | 9 | 0 | 0.94713 | 0.31894 | 286.5757 | 0 | 0 | 0 | 0 | 180 | 106.5757 | 90000 | 106.5757 | 567649.056 | 343.6062 | 0
6060 | 9 | 0 | 1 | 0.29648 | 300.926 | 0 | 0 | 0 | 0 | 180 | 120.926 | 90000 | 120.926 | 567769.982 | 499.6302 | 0
6061 | 9 | 0 | 1 | 0.30572 | 301.3038 | 0 | 0 | 0 | 0 | 12.8978 | 200 | 90000 | 200 | 567969.982 | 510.81 | 88.4059
6062 | 9 | 0 | 1 | 0.26779 | 299.7528 | 0 | 0 | 0 | 0 | 0 | 200 | 90000 | 200 | 568169.982 | 510.81 | 99.7528
6063 | 9 | 0 | 0.94713 | 0.45341 | 292.0753 | 0 | 0 | 0 | 0 | 0 | 200 | 90000 | 200 | 568369.982 | 510.81 | 92.0753
6064 | 9 | 0 | 0.72799 | 0.37301 | 225.4985 | 0 | 0 | 0 | 0 | 0 | 200 | 90000 | 200 | 568569.982 | 510.81 | 25.4985
6065 | 9 | 0 | 0.4662 | 0.33489 | 148.3348 | 0 | 0 | 0 | 0 | 0 | 148.3348 | 90000 | 148.3348 | 568718.3168 | 510.81 | 0
6066 | 9 | 0 | 0.20439 | 0.35386 | 73.4996 | 0 | 0 | 0 | 0 | 0 | 73.4996 | 90000 | 73.4996 | 568791.8164 | 510.81 | 0
6067 | 9 | 0 | 0.008173 | 0.26231 | 13.0888 | 0 | 0 | 0 | 0 | 0 | 13.0888 | 90000 | 13.0888 | 568804.9052 | 510.81 | 0
6068 | 9 | 1 | 0 | 0.33332 | 13.633 | 200 | 13.633 | 180 | 193.633 | 0 | 0 | 89800 | 193.633 | 568998.5382 | 330.81 | 0
6069 | 9 | 1 | 0 | 0.21422 | 8.7618 | 200 | 8.7618 | 180 | 188.7618 | 0 | 0 | 89600 | 188.7618 | 569187.3 | 150.81 | 0
6070 | 9 | 0 | 0 | 0.18014 | 7.3678 | 0 | 0 | 0 | 0 | 7.3678 | 0 | 89600 | 0 | 569187.3 | 157.1964 | 0
6071 | 9 | 0 | 0 | 0.20901 | 8.5487 | 0 | 0 | 0 | 0 | 8.5487 | 0 | 89600 | 0 | 569187.3 | 164.6064 | 0
6072 | 9 | 0 | 0 | 0.14905 | 6.0961 | 0 | 0 | 0 | 0 | 6.0961 | 0 | 89600 | 0 | 569187.3 | 169.8905 | 0
6073 | 9 | 0 | 0 | 0.19501 | 7.9761 | 0 | 0 | 0 | 0 | 7.9761 | 0 | 89600 | 0 | 569187.3 | 176.8042 | 0
6074 | 9 | 0 | 0 | 0.20596 | 8.4237 | 0 | 0 | 0 | 0 | 8.4237 | 0 | 89600 | 0 | 569187.3 | 184.1059 | 0
6075 | 9 | 0 | 0 | 0.19065 | 7.7975 | 0 | 0 | 0 | 0 | 7.7975 | 0 | 89600 | 0 | 569187.3 | 190.8648 | 0
6076 | 9 | 0 | 0 | 0.22863 | 9.3508 | 0 | 0 | 0 | 0 | 9.3508 | 0 | 89600 | 0 | 569187.3 | 198.9701 | 0
6077 | 9 | 0 | 0 | 0.28784 | 11.7726 | 0 | 0 | 0 | 0 | 11.7726 | 0 | 89600 | 0 | 569187.3 | 209.1745 | 0
6078 | 9 | 0 | 0 | 0.14329 | 5.8606 | 0 | 0 | 0 | 0 | 5.8606 | 0 | 89600 | 0 | 569187.3 | 214.2545 | 0
6079 | 9 | 0 | 0.007864 | 0.22568 | 11.5015 | 0 | 0 | 0 | 0 | 11.5015 | 0 | 89600 | 0 | 569187.3 | 224.224 | 0
6080 | 9 | 1 | 0.19665 | 0.17538 | 63.9665 | 200 | 63.9665 | 136.0335 | 200 | 0 | 0 | 89400 | 200 | 569387.3 | 88.1905 | 0
6081 | 9 | 1 | 0.44856 | 0.12906 | 134.8222 | 200 | 134.8222 | 65.1778 | 200 | 0 | 0 | 89200 | 200 | 569587.3 | 23.0128 | 0
6082 | 9 | 0 | 0.70044 | 0.16214 | 208.9199 | 0 | 0 | 0 | 0 | 180 | 28.9199 | 89200 | 28.9199 | 569616.22 | 179.0368 | 0
6083 | 9 | 0 | 0.9113 | 0.28301 | 274.7576 | 0 | 0 | 0 | 0 | 180 | 94.7576 | 89200 | 94.7576 | 569710.9775 | 335.0608 | 0
6084 | 9 | 0 | 1 | 0.51727 | 309.9565 | 0 | 0 | 0 | 0 | 180 | 129.9565 | 89200 | 129.9565 | 569840.934 | 491.0848 | 0
6085 | 9 | 0 | 1 | 0.39644 | 305.0146 | 0 | 0 | 0 | 0 | 22.7564 | 200 | 89200 | 200 | 570040.934 | 510.81 | 82.2582
6086 | 9 | 0 | 1 | 0.49809 | 309.1719 | 0 | 0 | 0 | 0 | 0 | 200 | 89200 | 200 | 570240.934 | 510.81 | 109.1719
6087 | 9 | 0 | 0.9113 | 0.7203 | 292.6425 | 0 | 0 | 0 | 0 | 0 | 200 | 89200 | 200 | 570440.934 | 510.81 | 92.6425
6088 | 9 | 0 | 0.70044 | 1 | 243.1882 | 0 | 0 | 0 | 0 | 0 | 200 | 89200 | 200 | 570640.934 | 510.81 | 43.1882
6089 | 9 | 0 | 0.44856 | 1 | 170.4438 | 0 | 0 | 0 | 0 | 0 | 170.4438 | 89200 | 170.4438 | 570811.3778 | 510.81 | 0
6090 | 9 | 0 | 0.19665 | 0.72473 | 86.4348 | 0 | 0 | 0 | 0 | 0 | 86.4348 | 89200 | 86.4348 | 570897.8127 | 510.81 | 0
6091 | 9 | 0 | 0.007864 | 0.67142 | 29.7322 | 0 | 0 | 0 | 0 | 0 | 29.7322 | 89200 | 29.7322 | 570927.5448 | 510.81 | 0
6092 | 9 | 1 | 0 | 0.77337 | 31.6308 | 200 | 31.6308 | 168.3692 | 200 | 0 | 0 | 89000 | 200 | 571127.5448 | 342.4408 | 0
6093 | 9 | 1 | 0 | 0.81637 | 33.3893 | 200 | 33.3893 | 166.6107 | 200 | 0 | 0 | 88800 | 200 | 571327.5448 | 175.8301 | 0
6094 | 9 | 0 | 0 | 0.85714 | 35.0569 | 0 | 0 | 0 | 0 | 35.0569 | 0 | 88800 | 0 | 571327.5448 | 206.2175 | 0
6095 | 9 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 88800 | 0 | 571327.5448 | 241.6696 | 0
6096 | 9 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 88800 | 0 | 571327.5448 | 277.1217 | 0
6097 | 9 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 88800 | 0 | 571327.5448 | 312.5738 | 0
6098 | 9 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 88800 | 0 | 571327.5448 | 348.026 | 0
6099 | 9 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 88800 | 0 | 571327.5448 | 383.4781 | 0
6100 | 9 | 0 | 0 | 0.91775 | 37.5359 | 0 | 0 | 0 | 0 | 37.5359 | 0 | 88800 | 0 | 571327.5448 | 416.0142 | 0
6101 | 9 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 88800 | 0 | 571327.5448 | 451.4663 | 0
6102 | 9 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 88800 | 0 | 571327.5448 | 486.9185 | 0
6103 | 9 | 0 | 0.007756 | 1 | 43.1399 | 0 | 0 | 0 | 0 | 27.5629 | 15.577 | 88800 | 15.577 | 571343.1218 | 510.81 | 0
6104 | 9 | 1 | 0.19396 | 1 | 96.9159 | 200 | 96.9159 | 103.0841 | 200 | 0 | 0 | 88600 | 200 | 571543.1218 | 407.7259 | 0
6105 | 9 | 1 | 0.44242 | 1 | 168.67 | 200 | 168.67 | 31.33 | 200 | 0 | 0 | 88400 | 200 | 571743.1218 | 376.396 | 0
6106 | 9 | 0 | 0.69085 | 1 | 240.4183 | 0 | 0 | 0 | 0 | 155.0693 | 85.3491 | 88400 | 85.3491 | 571828.4709 | 510.81 | 0
6107 | 9 | 0 | 0.89882 | 1 | 300.4783 | 0 | 0 | 0 | 0 | 0 | 200 | 88400 | 200 | 572028.4709 | 510.81 | 100.4783
6108 | 9 | 0 | 1 | 0.94099 | 327.2863 | 0 | 0 | 0 | 0 | 0 | 200 | 88400 | 200 | 572228.4709 | 510.81 | 127.2863
6109 | 9 | 0 | 1 | 0.8634 | 324.1131 | 0 | 0 | 0 | 0 | 0 | 200 | 88400 | 200 | 572428.4709 | 510.81 | 124.1131
6110 | 9 | 0 | 1 | 0.81114 | 321.9756 | 0 | 0 | 0 | 0 | 0 | 200 | 88400 | 200 | 572628.4709 | 510.81 | 121.9756
6111 | 9 | 0 | 0.89882 | 0.87516 | 295.3723 | 0 | 0 | 0 | 0 | 0 | 200 | 88400 | 200 | 572828.4709 | 510.81 | 95.3723
6112 | 9 | 0 | 0.69085 | 0.62016 | 224.883 | 0 | 0 | 0 | 0 | 0 | 200 | 88400 | 200 | 573028.4709 | 510.81 | 24.883
6113 | 9 | 0 | 0.44242 | 0.45122 | 146.225 | 0 | 0 | 0 | 0 | 0 | 146.225 | 88400 | 146.225 | 573174.6959 | 510.81 | 0
6114 | 9 | 0 | 0.19396 | 0.51055 | 76.8976 | 0 | 0 | 0 | 0 | 0 | 76.8976 | 88400 | 76.8976 | 573251.5936 | 510.81 | 0
6115 | 9 | 0 | 0.007756 | 0.42733 | 19.7176 | 0 | 0 | 0 | 0 | 0 | 19.7176 | 88400 | 19.7176 | 573271.3112 | 510.81 | 0
6116 | 9 | 1 | 0 | 0.48794 | 19.9568 | 200 | 19.9568 | 180 | 199.9568 | 0 | 0 | 88200 | 199.9568 | 573471.268 | 330.81 | 0
6117 | 9 | 1 | 0 | 0.56616 | 23.1559 | 200 | 23.1559 | 176.8441 | 200 | 0 | 0 | 88000 | 200 | 573671.268 | 153.9659 | 0
6118 | 9 | 0 | 0 | 0.47715 | 19.5153 | 0 | 0 | 0 | 0 | 19.5153 | 0 | 88000 | 0 | 573671.268 | 170.8818 | 0
6119 | 9 | 0 | 0 | 0.41448 | 16.9521 | 0 | 0 | 0 | 0 | 16.9521 | 0 | 88000 | 0 | 573671.268 | 185.5759 | 0
6120 | 9 | 0 | 0 | 0.3348 | 13.6933 | 0 | 0 | 0 | 0 | 13.6933 | 0 | 88000 | 0 | 573671.268 | 197.4452 | 0
6121 | 9 | 0 | 0 | 0.21155 | 8.6526 | 0 | 0 | 0 | 0 | 8.6526 | 0 | 88000 | 0 | 573671.268 | 204.9452 | 0
6122 | 9 | 0 | 0 | 0.26062 | 10.6595 | 0 | 0 | 0 | 0 | 10.6595 | 0 | 88000 | 0 | 573671.268 | 214.1849 | 0
6123 | 9 | 0 | 0 | 0.29373 | 12.0134 | 0 | 0 | 0 | 0 | 12.0134 | 0 | 88000 | 0 | 573671.268 | 224.598 | 0
6124 | 9 | 0 | 0 | 0.39342 | 16.091 | 0 | 0 | 0 | 0 | 16.091 | 0 | 88000 | 0 | 573671.268 | 238.5458 | 0
6125 | 9 | 0 | 0 | 0.41019 | 16.7766 | 0 | 0 | 0 | 0 | 16.7766 | 0 | 88000 | 0 | 573671.268 | 253.0877 | 0
6126 | 9 | 0 | 0 | 0.37369 | 15.2838 | 0 | 0 | 0 | 0 | 15.2838 | 0 | 88000 | 0 | 573671.268 | 266.3357 | 0
6127 | 9 | 0 | 0.008324 | 0.29254 | 14.3689 | 0 | 0 | 0 | 0 | 14.3689 | 0 | 88000 | 0 | 573671.268 | 278.7906 | 0
6128 | 9 | 1 | 0.20817 | 0.32423 | 73.3798 | 200 | 73.3798 | 126.6202 | 200 | 0 | 0 | 87800 | 200 | 573871.268 | 152.1704 | 0
6129 | 9 | 1 | 0.47482 | 0.28191 | 148.6592 | 200 | 148.6592 | 51.3408 | 200 | 0 | 0 | 87600 | 200 | 574071.268 | 100.8296 | 0
6130 | 9 | 0 | 0.74146 | 0.39935 | 230.4662 | 0 | 0 | 0 | 0 | 180 | 50.4662 | 87600 | 50.4662 | 574121.7342 | 256.8536 | 0
6131 | 9 | 0 | 0.96466 | 0.32402 | 291.8449 | 0 | 0 | 0 | 0 | 180 | 111.8449 | 87600 | 111.8449 | 574233.5792 | 412.8776 | 0
6132 | 9 | 0 | 1 | 0.44301 | 306.919 | 0 | 0 | 0 | 0 | 112.9816 | 193.9375 | 87600 | 193.9375 | 574427.5166 | 510.81 | 0
6133 | 9 | 0 | 1 | 0.60301 | 313.463 | 0 | 0 | 0 | 0 | 0 | 200 | 87600 | 200 | 574627.5166 | 510.81 | 113.463
6134 | 9 | 0 | 1 | 0.74453 | 319.2512 | 0 | 0 | 0 | 0 | 0 | 200 | 87600 | 200 | 574827.5166 | 510.81 | 119.2512
6135 | 9 | 0 | 0.96466 | 0.58057 | 302.3378 | 0 | 0 | 0 | 0 | 0 | 200 | 87600 | 200 | 575027.5166 | 510.81 | 102.3378
6136 | 9 | 0 | 0.74146 | 0.58277 | 237.9679 | 0 | 0 | 0 | 0 | 0 | 200 | 87600 | 200 | 575227.5166 | 510.81 | 37.9679
6137 | 9 | 0 | 0.47482 | 0.7937 | 169.5913 | 0 | 0 | 0 | 0 | 0 | 169.5913 | 87600 | 169.5913 | 575397.1079 | 510.81 | 0
6138 | 9 | 0 | 0.20817 | 0.67072 | 87.5513 | 0 | 0 | 0 | 0 | 0 | 87.5513 | 87600 | 87.5513 | 575484.6592 | 510.81 | 0
6139 | 9 | 0 | 0.008324 | 0.64936 | 28.9626 | 0 | 0 | 0 | 0 | 0 | 28.9626 | 87600 | 28.9626 | 575513.6218 | 510.81 | 0
6140 | 9 | 1 | 0 | 0.77544 | 31.7154 | 200 | 31.7154 | 168.2846 | 200 | 0 | 0 | 87400 | 200 | 575713.6218 | 342.5254 | 0
6141 | 9 | 1 | 0 | 0.92414 | 37.7975 | 200 | 37.7975 | 162.2025 | 200 | 0 | 0 | 87200 | 200 | 575913.6218 | 180.3229 | 0
6142 | 9 | 0 | 0 | 0.79413 | 32.4799 | 0 | 0 | 0 | 0 | 32.4799 | 0 | 87200 | 0 | 575913.6218 | 208.4765 | 0
6143 | 9 | 0 | 0 | 0.67411 | 27.5709 | 0 | 0 | 0 | 0 | 27.5709 | 0 | 87200 | 0 | 575913.6218 | 232.375 | 0
6144 | 9 | 0 | 0 | 0.35585 | 14.5544 | 0 | 0 | 0 | 0 | 14.5544 | 0 | 87200 | 0 | 575913.6218 | 244.9907 | 0
6145 | 9 | 0 | 0 | 0.38596 | 15.7859 | 0 | 0 | 0 | 0 | 15.7859 | 0 | 87200 | 0 | 575913.6218 | 258.674 | 0
6146 | 9 | 0 | 0 | 0.34838 | 14.2486 | 0 | 0 | 0 | 0 | 14.2486 | 0 | 87200 | 0 | 575913.6218 | 271.0247 | 0
6147 | 9 | 0 | 0 | 0.17463 | 7.1424 | 0 | 0 | 0 | 0 | 7.1424 | 0 | 87200 | 0 | 575913.6218 | 277.2157 | 0
6148 | 9 | 0 | 0 | 0.16613 | 6.7948 | 0 | 0 | 0 | 0 | 6.7948 | 0 | 87200 | 0 | 575913.6218 | 283.1054 | 0
6149 | 9 | 0 | 0 | 0.17657 | 7.2218 | 0 | 0 | 0 | 0 | 7.2218 | 0 | 87200 | 0 | 575913.6218 | 289.3653 | 0
6150 | 9 | 0 | 0 | 0.17746 | 7.2582 | 0 | 0 | 0 | 0 | 7.2582 | 0 | 87200 | 0 | 575913.6218 | 295.6567 | 0
6151 | 9 | 0 | 0.008313 | 0.11404 | 7.0649 | 0 | 0 | 0 | 0 | 7.0649 | 0 | 87200 | 0 | 575913.6218 | 301.7806 | 0
6152 | 9 | 1 | 0.2079 | 0.17139 | 67.0519 | 200 | 67.0519 | 132.9481 | 200 | 0 | 0 | 87000 | 200 | 576113.6218 | 168.8325 | 0
6153 | 9 | 1 | 0.47421 | 0.24789 | 147.0917 | 200 | 147.0917 | 52.9083 | 200 | 0 | 0 | 86800 | 200 | 576313.6218 | 115.9242 | 0
6154 | 9 | 0 | 0.7405 | 0.19704 | 221.9169 | 0 | 0 | 0 | 0 | 180 | 41.9169 | 86800 | 41.9169 | 576355.5387 | 271.9482 | 0
6155 | 9 | 0 | 0.96342 | 0.1292 | 283.5189 | 0 | 0 | 0 | 0 | 180 | 103.5189 | 86800 | 103.5189 | 576459.0576 | 427.9722 | 0
6156 | 9 | 0 | 1 | 0.14409 | 294.6934 | 0 | 0 | 0 | 0 | 95.5673 | 199.126 | 86800 | 199.126 | 576658.1836 | 510.81 | 0
6157 | 9 | 0 | 1 | 0.13004 | 294.1186 | 0 | 0 | 0 | 0 | 0 | 200 | 86800 | 200 | 576858.1836 | 510.81 | 94.1186
6158 | 9 | 0 | 1 | 0.12166 | 293.7759 | 0 | 0 | 0 | 0 | 0 | 200 | 86800 | 200 | 577058.1836 | 510.81 | 93.7759
6159 | 9 | 0 | 0.96342 | 0.12306 | 283.2676 | 0 | 0 | 0 | 0 | 0 | 200 | 86800 | 200 | 577258.1836 | 510.81 | 83.2676
6160 | 9 | 0 | 0.7405 | 0.090859 | 217.574 | 0 | 0 | 0 | 0 | 0 | 200 | 86800 | 200 | 577458.1836 | 510.81 | 17.574
6161 | 9 | 0 | 0.47421 | 0.09445 | 140.816 | 0 | 0 | 0 | 0 | 0 | 140.816 | 86800 | 140.816 | 577598.9996 | 510.81 | 0
6162 | 9 | 0 | 0.2079 | 0.18438 | 67.583 | 0 | 0 | 0 | 0 | 0 | 67.583 | 86800 | 67.583 | 577666.5826 | 510.81 | 0
6163 | 9 | 0 | 0.008313 | 0.253 | 12.7485 | 0 | 0 | 0 | 0 | 0 | 12.7485 | 86800 | 12.7485 | 577679.3311 | 510.81 | 0
6164 | 9 | 1 | 0 | 0.2638 | 10.7892 | 200 | 10.7892 | 180 | 190.7892 | 0 | 0 | 86600 | 190.7892 | 577870.1203 | 330.81 | 0
6165 | 9 | 1 | 0 | 0.2212 | 9.047 | 200 | 9.047 | 180 | 189.047 | 0 | 0 | 86400 | 189.047 | 578059.1673 | 150.81 | 0
6166 | 9 | 0 | 0 | 0.23919 | 9.7829 | 0 | 0 | 0 | 0 | 9.7829 | 0 | 86400 | 0 | 578059.1673 | 159.2898 | 0
6167 | 9 | 0 | 0 | 0.19044 | 7.7892 | 0 | 0 | 0 | 0 | 7.7892 | 0 | 86400 | 0 | 578059.1673 | 166.0414 | 0
6168 | 9 | 0 | 0 | 0.1629 | 6.6625 | 0 | 0 | 0 | 0 | 6.6625 | 0 | 86400 | 0 | 578059.1673 | 171.8165 | 0
6169 | 9 | 0 | 0 | 0.13538 | 5.537 | 0 | 0 | 0 | 0 | 5.537 | 0 | 86400 | 0 | 578059.1673 | 176.616 | 0
6170 | 9 | 0 | 0 | 0.13929 | 5.697 | 0 | 0 | 0 | 0 | 5.697 | 0 | 86400 | 0 | 578059.1673 | 181.5542 | 0
6171 | 9 | 0 | 0 | 0.16497 | 6.7472 | 0 | 0 | 0 | 0 | 6.7472 | 0 | 86400 | 0 | 578059.1673 | 187.4027 | 0
6172 | 9 | 0 | 0 | 0.26706 | 10.9228 | 0 | 0 | 0 | 0 | 10.9228 | 0 | 86400 | 0 | 578059.1673 | 196.8705 | 0
6173 | 9 | 0 | 0 | 0.33232 | 13.5921 | 0 | 0 | 0 | 0 | 13.5921 | 0 | 86400 | 0 | 578059.1673 | 208.6521 | 0
6174 | 9 | 0 | 0 | 0.33829 | 13.8361 | 0 | 0 | 0 | 0 | 13.8361 | 0 | 86400 | 0 | 578059.1673 | 220.6452 | 0
6175 | 9 | 0 | 0.00715 | 0.38917 | 17.9819 | 0 | 0 | 0 | 0 | 17.9819 | 0 | 86400 | 0 | 578059.1673 | 236.2319 | 0
6176 | 9 | 1 | 0.17881 | 0.3345 | 65.3223 | 200 | 65.3223 | 134.6777 | 200 | 0 | 0 | 86200 | 200 | 578259.1673 | 101.5542 | 0
6177 | 9 | 1 | 0.40786 | 0.45594 | 136.4394 | 200 | 136.4394 | 63.5606 | 200 | 0 | 0 | 86000 | 200 | 578459.1673 | 37.9937 | 0
6178 | 9 | 0 | 0.6369 | 0.49321 | 204.1083 | 0 | 0 | 0 | 0 | 180 | 24.1083 | 86000 | 24.1083 | 578483.2757 | 194.0177 | 0
6179 | 9 | 0 | 0.82862 | 0.51388 | 260.3234 | 0 | 0 | 0 | 0 | 180 | 80.3234 | 86000 | 80.3234 | 578563.5991 | 350.0417 | 0
6180 | 9 | 0 | 0.95533 | 0.32277 | 289.1016 | 0 | 0 | 0 | 0 | 180 | 109.1016 | 86000 | 109.1016 | 578672.7007 | 506.0657 | 0
6181 | 9 | 0 | 0.99957 | 0.42866 | 306.2078 | 0 | 0 | 0 | 0 | 5.4734 | 200 | 86000 | 200 | 578872.7007 | 510.81 | 100.7344
6182 | 9 | 0 | 0.95533 | 0.53057 | 297.6009 | 0 | 0 | 0 | 0 | 0 | 200 | 86000 | 200 | 579072.7007 | 510.81 | 97.6009
6183 | 9 | 0 | 0.82862 | 0.58394 | 263.1889 | 0 | 0 | 0 | 0 | 0 | 200 | 86000 | 200 | 579272.7007 | 510.81 | 63.1889
6184 | 9 | 0 | 0.6369 | 0.56222 | 206.931 | 0 | 0 | 0 | 0 | 0 | 200 | 86000 | 200 | 579472.7007 | 510.81 | 6.931
6185 | 9 | 0 | 0.40786 | 0.39279 | 133.8566 | 0 | 0 | 0 | 0 | 0 | 133.8566 | 86000 | 133.8566 | 579606.5573 | 510.81 | 0
6186 | 9 | 0 | 0.17881 | 0.26747 | 62.5805 | 0 | 0 | 0 | 0 | 0 | 62.5805 | 86000 | 62.5805 | 579669.1378 | 510.81 | 0
6187 | 9 | 0 | 0.00715 | 0.30868 | 14.69 | 0 | 0 | 0 | 0 | 0 | 14.69 | 86000 | 14.69 | 579683.8278 | 510.81 | 0
6188 | 9 | 1 | 0 | 0.22474 | 9.1917 | 200 | 9.1917 | 180 | 189.1917 | 0 | 0 | 85800 | 189.1917 | 579873.0195 | 330.81 | 0
6189 | 9 | 1 | 0 | 0.31767 | 12.9927 | 200 | 12.9927 | 180 | 192.9927 | 0 | 0 | 85600 | 192.9927 | 580066.0122 | 150.81 | 0
6190 | 9 | 0 | 0 | 0.40255 | 16.4644 | 0 | 0 | 0 | 0 | 16.4644 | 0 | 85600 | 0 | 580066.0122 | 165.0814 | 0
6191 | 9 | 0 | 0 | 0.37932 | 15.5142 | 0 | 0 | 0 | 0 | 15.5142 | 0 | 85600 | 0 | 580066.0122 | 178.5291 | 0
6192 | 9 | 0 | 0 | 0.46801 | 19.1414 | 0 | 0 | 0 | 0 | 19.1414 | 0 | 85600 | 0 | 580066.0122 | 195.1209 | 0
6193 | 9 | 0 | 0 | 0.4565 | 18.671 | 0 | 0 | 0 | 0 | 18.671 | 0 | 85600 | 0 | 580066.0122 | 211.3049 | 0
6194 | 9 | 0 | 0 | 0.50703 | 20.7376 | 0 | 0 | 0 | 0 | 20.7376 | 0 | 85600 | 0 | 580066.0122 | 229.2803 | 0
6195 | 9 | 0 | 0 | 0.41524 | 16.9834 | 0 | 0 | 0 | 0 | 16.9834 | 0 | 85600 | 0 | 580066.0122 | 244.0015 | 0
6196 | 9 | 0 | 0 | 0.40472 | 16.553 | 0 | 0 | 0 | 0 | 16.553 | 0 | 85600 | 0 | 580066.0122 | 258.3496 | 0
6197 | 9 | 0 | 0 | 0.41294 | 16.8892 | 0 | 0 | 0 | 0 | 16.8892 | 0 | 85600 | 0 | 580066.0122 | 272.9892 | 0
6198 | 9 | 0 | 0 | 0.45999 | 18.8138 | 0 | 0 | 0 | 0 | 18.8138 | 0 | 85600 | 0 | 580066.0122 | 289.297 | 0
6199 | 9 | 0 | 0.010091 | 0.55251 | 25.5121 | 0 | 0 | 0 | 0 | 25.5121 | 0 | 85600 | 0 | 580066.0122 | 311.4109 | 0
6200 | 9 | 1 | 0.25235 | 0.55458 | 95.5617 | 200 | 95.5617 | 104.4383 | 200 | 0 | 0 | 85400 | 200 | 580266.0122 | 206.9727 | 0
6201 | 9 | 1 | 0.57561 | 0.38642 | 182.0404 | 200 | 182.0404 | 17.9596 | 200 | 0 | 0 | 85200 | 200 | 580466.0122 | 189.0131 | 0
6202 | 9 | 0 | 0.89884 | 0.47331 | 278.9426 | 0 | 0 | 0 | 0 | 180 | 98.9426 | 85200 | 98.9426 | 580564.9548 | 345.0371 | 0
6203 | 9 | 0 | 1 | 0.36656 | 303.7925 | 0 | 0 | 0 | 0 | 180 | 123.7925 | 85200 | 123.7925 | 580688.7473 | 501.0611 | 0
6204 | 9 | 0 | 1 | 0.46248 | 307.7156 | 0 | 0 | 0 | 0 | 11.2471 | 200 | 85200 | 200 | 580888.7473 | 510.81 | 96.4685
6205 | 9 | 0 | 1 | 0.61432 | 313.9256 | 0 | 0 | 0 | 0 | 0 | 200 | 85200 | 200 | 581088.7473 | 510.81 | 113.9256
6206 | 9 | 0 | 1 | 0.46851 | 307.962 | 0 | 0 | 0 | 0 | 0 | 200 | 85200 | 200 | 581288.7473 | 510.81 | 107.962
6207 | 9 | 0 | 1 | 0.74323 | 319.198 | 0 | 0 | 0 | 0 | 0 | 200 | 85200 | 200 | 581488.7473 | 510.81 | 119.198
6208 | 9 | 0 | 0.89884 | 0.6827 | 287.5067 | 0 | 0 | 0 | 0 | 0 | 200 | 85200 | 200 | 581688.7473 | 510.81 | 87.5067
6209 | 9 | 0 | 0.57561 | 0.51549 | 187.3193 | 0 | 0 | 0 | 0 | 0 | 187.3193 | 85200 | 187.3193 | 581876.0666 | 510.81 | 0
6210 | 9 | 0 | 0.25235 | 0.53183 | 94.6316 | 0 | 0 | 0 | 0 | 0 | 94.6316 | 85200 | 94.6316 | 581970.6982 | 510.81 | 0
6211 | 9 | 0 | 0.010091 | 0.67242 | 30.4164 | 0 | 0 | 0 | 0 | 0 | 30.4164 | 85200 | 30.4164 | 582001.1146 | 510.81 | 0
6212 | 9 | 1 | 0 | 0.53805 | 22.0061 | 200 | 22.0061 | 177.9939 | 200 | 0 | 0 | 85000 | 200 | 582201.1146 | 332.8161 | 0
6213 | 9 | 1 | 0 | 0.35128 | 14.3674 | 200 | 14.3674 | 180 | 194.3674 | 0 | 0 | 84800 | 194.3674 | 582395.4821 | 152.8161 | 0
6214 | 9 | 0 | 0 | 0.33639 | 13.7585 | 0 | 0 | 0 | 0 | 13.7585 | 0 | 84800 | 0 | 582395.4821 | 164.742 | 0
6215 | 9 | 0 | 0 | 0.23606 | 9.6548 | 0 | 0 | 0 | 0 | 9.6548 | 0 | 84800 | 0 | 582395.4821 | 173.1107 | 0
6216 | 9 | 0 | 0 | 0.21075 | 8.6196 | 0 | 0 | 0 | 0 | 8.6196 | 0 | 84800 | 0 | 582395.4821 | 180.5821 | 0
6217 | 9 | 0 | 0 | 0.2176 | 8.9 | 0 | 0 | 0 | 0 | 8.9 | 0 | 84800 | 0 | 582395.4821 | 188.2967 | 0
6218 | 9 | 0 | 0 | 0.20748 | 8.4859 | 0 | 0 | 0 | 0 | 8.4859 | 0 | 84800 | 0 | 582395.4821 | 195.6523 | 0
6219 | 9 | 0 | 0 | 0.31573 | 12.9134 | 0 | 0 | 0 | 0 | 12.9134 | 0 | 84800 | 0 | 582395.4821 | 206.8456 | 0
6220 | 9 | 0 | 0 | 0.29569 | 12.0937 | 0 | 0 | 0 | 0 | 12.0937 | 0 | 84800 | 0 | 582395.4821 | 217.3285 | 0
6221 | 9 | 0 | 0 | 0.45016 | 18.4113 | 0 | 0 | 0 | 0 | 18.4113 | 0 | 84800 | 0 | 582395.4821 | 233.2874 | 0
6222 | 9 | 0 | 0 | 0.45576 | 18.6406 | 0 | 0 | 0 | 0 | 18.6406 | 0 | 84800 | 0 | 582395.4821 | 249.4451 | 0
6223 | 9 | 0 | 0.008227 | 0.54035 | 24.4763 | 0 | 0 | 0 | 0 | 24.4763 | 0 | 84800 | 0 | 582395.4821 | 270.6611 | 0
6224 | 9 | 1 | 0.20574 | 0.51683 | 80.5555 | 200 | 80.5555 | 119.4445 | 200 | 0 | 0 | 84600 | 200 | 582595.4821 | 151.2166 | 0
6225 | 9 | 1 | 0.46928 | 0.64622 | 161.959 | 200 | 161.959 | 38.041 | 200 | 0 | 0 | 84400 | 200 | 582795.4821 | 113.1756 | 0
6226 | 9 | 0 | 0.7328 | 0.62457 | 237.1781 | 0 | 0 | 0 | 0 | 180 | 57.1781 | 84400 | 57.1781 | 582852.6602 | 269.1996 | 0
6227 | 9 | 0 | 0.95339 | 0.9138 | 312.7148 | 0 | 0 | 0 | 0 | 180 | 132.7148 | 84400 | 132.7148 | 582985.375 | 425.2236 | 0
6228 | 9 | 0 | 1 | 0.8493 | 323.5365 | 0 | 0 | 0 | 0 | 98.7383 | 200 | 84400 | 200 | 583185.375 | 510.81 | 24.7982
6229 | 9 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 0 | 200 | 84400 | 200 | 583385.375 | 510.81 | 129.7
6230 | 9 | 0 | 1 | 0.81554 | 322.1554 | 0 | 0 | 0 | 0 | 0 | 200 | 84400 | 200 | 583585.375 | 510.81 | 122.1554
6231 | 9 | 0 | 0.95339 | 0.60313 | 300.0087 | 0 | 0 | 0 | 0 | 0 | 200 | 84400 | 200 | 583785.375 | 510.81 | 100.0087
6232 | 9 | 0 | 0.7328 | 0.70935 | 240.6457 | 0 | 0 | 0 | 0 | 0 | 200 | 84400 | 200 | 583985.375 | 510.81 | 40.6457
6233 | 9 | 0 | 0.46928 | 0.89381 | 172.0856 | 0 | 0 | 0 | 0 | 0 | 172.0856 | 84400 | 172.0856 | 584157.4606 | 510.81 | 0
6234 | 9 | 0 | 0.20574 | 0.81801 | 92.8738 | 0 | 0 | 0 | 0 | 0 | 92.8738 | 84400 | 92.8738 | 584250.3344 | 510.81 | 0
6235 | 9 | 0 | 0.008227 | 0.68009 | 30.1917 | 0 | 0 | 0 | 0 | 0 | 30.1917 | 84400 | 30.1917 | 584280.5261 | 510.81 | 0
6236 | 9 | 1 | 0 | 0.69334 | 28.3575 | 200 | 28.3575 | 171.6425 | 200 | 0 | 0 | 84200 | 200 | 584480.5261 | 339.1675 | 0
6237 | 9 | 1 | 0 | 0.6464 | 26.4376 | 200 | 26.4376 | 173.5624 | 200 | 0 | 0 | 84000 | 200 | 584680.5261 | 165.6051 | 0
6238 | 9 | 0 | 0 | 0.39794 | 16.2756 | 0 | 0 | 0 | 0 | 16.2756 | 0 | 84000 | 0 | 584680.5261 | 179.7128 | 0
6239 | 9 | 0 | 0 | 0.29766 | 12.1741 | 0 | 0 | 0 | 0 | 12.1741 | 0 | 84000 | 0 | 584680.5261 | 190.2653 | 0
6240 | 9 | 0 | 0 | 0.23207 | 9.4917 | 0 | 0 | 0 | 0 | 9.4917 | 0 | 84000 | 0 | 584680.5261 | 198.4927 | 0
6241 | 9 | 0 | 0 | 0.22394 | 9.1591 | 0 | 0 | 0 | 0 | 9.1591 | 0 | 84000 | 0 | 584680.5261 | 206.4318 | 0
6242 | 9 | 0 | 0 | 0.30682 | 12.5488 | 0 | 0 | 0 | 0 | 12.5488 | 0 | 84000 | 0 | 584680.5261 | 217.3091 | 0
6243 | 9 | 0 | 0 | 0.29625 | 12.1167 | 0 | 0 | 0 | 0 | 12.1167 | 0 | 84000 | 0 | 584680.5261 | 227.8119 | 0
6244 | 9 | 0 | 0 | 0.47368 | 19.3735 | 0 | 0 | 0 | 0 | 19.3735 | 0 | 84000 | 0 | 584680.5261 | 244.6049 | 0
6245 | 9 | 0 | 0 | 0.28023 | 11.4612 | 0 | 0 | 0 | 0 | 11.4612 | 0 | 84000 | 0 | 584680.5261 | 254.5395 | 0
6246 | 9 | 0 | 0 | 0.22537 | 9.2178 | 0 | 0 | 0 | 0 | 9.2178 | 0 | 84000 | 0 | 584680.5261 | 262.5294 | 0
6247 | 9 | 0 | 0.008137 | 0.22773 | 11.664 | 0 | 0 | 0 | 0 | 11.664 | 0 | 84000 | 0 | 584680.5261 | 272.6397 | 0
6248 | 9 | 1 | 0.20348 | 0.15314 | 65.0301 | 200 | 65.0301 | 134.9699 | 200 | 0 | 0 | 83800 | 200 | 584880.5261 | 137.6698 | 0
6249 | 9 | 1 | 0.46414 | 0.16098 | 140.6285 | 200 | 140.6285 | 59.3715 | 200 | 0 | 0 | 83600 | 200 | 585080.5261 | 78.2983 | 0
6250 | 9 | 0 | 0.72478 | 0.14406 | 215.208 | 0 | 0 | 0 | 0 | 180 | 35.208 | 83600 | 35.208 | 585115.7341 | 234.3223 | 0
6251 | 9 | 0 | 0.94295 | 0.12466 | 277.424 | 0 | 0 | 0 | 0 | 180 | 97.424 | 83600 | 97.424 | 585213.1581 | 390.3463 | 0
6252 | 9 | 0 | 1 | 0.13376 | 294.2709 | 0 | 0 | 0 | 0 | 138.9752 | 155.2957 | 83600 | 155.2957 | 585368.4539 | 510.81 | 0
6253 | 9 | 0 | 1 | 0.1304 | 294.1335 | 0 | 0 | 0 | 0 | 0 | 200 | 83600 | 200 | 585568.4539 | 510.81 | 94.1335
6254 | 9 | 0 | 1 | 0.19739 | 296.873 | 0 | 0 | 0 | 0 | 0 | 200 | 83600 | 200 | 585768.4539 | 510.81 | 96.873
6255 | 9 | 0 | 0.94295 | 0.13853 | 277.9913 | 0 | 0 | 0 | 0 | 0 | 200 | 83600 | 200 | 585968.4539 | 510.81 | 77.9913
6256 | 9 | 0 | 0.72478 | 0.11794 | 214.1397 | 0 | 0 | 0 | 0 | 0 | 200 | 83600 | 200 | 586168.4539 | 510.81 | 14.1397
6257 | 9 | 0 | 0.46414 | 0.14202 | 139.853 | 0 | 0 | 0 | 0 | 0 | 139.853 | 83600 | 139.853 | 586308.3068 | 510.81 | 0
6258 | 9 | 0 | 0.20348 | 0.10632 | 63.1151 | 0 | 0 | 0 | 0 | 0 | 63.1151 | 83600 | 63.1151 | 586371.4219 | 510.81 | 0
6259 | 9 | 0 | 0.008137 | 0.08824 | 5.959 | 0 | 0 | 0 | 0 | 0 | 5.959 | 83600 | 5.959 | 586377.3809 | 510.81 | 0
6260 | 9 | 1 | 0 | 0.13243 | 5.4165 | 200 | 5.4165 | 180 | 185.4165 | 0 | 0 | 83400 | 185.4165 | 586562.7973 | 330.81 | 0
6261 | 9 | 1 | 0 | 0.21592 | 8.8311 | 200 | 8.8311 | 180 | 188.8311 | 0 | 0 | 83200 | 188.8311 | 586751.6285 | 150.81 | 0
6262 | 9 | 0 | 0 | 0.23065 | 9.4338 | 0 | 0 | 0 | 0 | 9.4338 | 0 | 83200 | 0 | 586751.6285 | 158.9872 | 0
6263 | 9 | 0 | 0 | 0.14087 | 5.7617 | 0 | 0 | 0 | 0 | 5.7617 | 0 | 83200 | 0 | 586751.6285 | 163.9815 | 0
6264 | 9 | 0 | 0 | 0.18454 | 7.5478 | 0 | 0 | 0 | 0 | 7.5478 | 0 | 83200 | 0 | 586751.6285 | 170.524 | 0
6265 | 9 | 0 | 0 | 0.14766 | 6.0393 | 0 | 0 | 0 | 0 | 6.0393 | 0 | 83200 | 0 | 586751.6285 | 175.7589 | 0
6266 | 9 | 0 | 0 | 0.15172 | 6.2053 | 0 | 0 | 0 | 0 | 6.2053 | 0 | 83200 | 0 | 586751.6285 | 181.1376 | 0
6267 | 9 | 0 | 0 | 0.12034 | 4.9221 | 0 | 0 | 0 | 0 | 4.9221 | 0 | 83200 | 0 | 586751.6285 | 185.404 | 0
6268 | 9 | 0 | 0 | 0.15346 | 6.2765 | 0 | 0 | 0 | 0 | 6.2765 | 0 | 83200 | 0 | 586751.6285 | 190.8445 | 0
6269 | 9 | 0 | 0 | 0.12396 | 5.0699 | 0 | 0 | 0 | 0 | 5.0699 | 0 | 83200 | 0 | 586751.6285 | 195.2391 | 0
6270 | 9 | 0 | 0 | 0.10196 | 4.1702 | 0 | 0 | 0 | 0 | 4.1702 | 0 | 83200 | 0 | 586751.6285 | 198.8538 | 0
6271 | 9 | 0 | 0.008336 | 0.1541 | 8.71 | 0 | 0 | 0 | 0 | 8.71 | 0 | 83200 | 0 | 586751.6285 | 206.4037 | 0
6272 | 9 | 1 | 0.20847 | 0.21587 | 69.0364 | 200 | 69.0364 | 130.9636 | 200 | 0 | 0 | 83000 | 200 | 586951.6285 | 75.4401 | 0
6273 | 9 | 1 | 0.47552 | 0.32177 | 150.4914 | 200 | 150.4914 | 49.5086 | 200 | 0 | 0 | 82800 | 200 | 587151.6285 | 25.9314 | 0
6274 | 9 | 0 | 0.74255 | 0.49617 | 234.7409 | 0 | 0 | 0 | 0 | 180 | 54.7409 | 82800 | 54.7409 | 587206.3694 | 181.9554 | 0
6275 | 9 | 0 | 0.96607 | 0.63671 | 305.0433 | 0 | 0 | 0 | 0 | 180 | 125.0433 | 82800 | 125.0433 | 587331.4127 | 337.9794 | 0
6276 | 9 | 0 | 1 | 0.56768 | 312.0182 | 0 | 0 | 0 | 0 | 180 | 132.0182 | 82800 | 132.0182 | 587463.4309 | 494.0034 | 0
6277 | 9 | 0 | 1 | 0.51192 | 309.7373 | 0 | 0 | 0 | 0 | 19.3892 | 200 | 82800 | 200 | 587663.4309 | 510.81 | 90.3481
6278 | 9 | 0 | 1 | 0.55619 | 311.5482 | 0 | 0 | 0 | 0 | 0 | 200 | 82800 | 200 | 587863.4309 | 510.81 | 111.5482
6279 | 9 | 0 | 0.96607 | 0.55213 | 301.584 | 0 | 0 | 0 | 0 | 0 | 200 | 82800 | 200 | 588063.4309 | 510.81 | 101.584
6280 | 9 | 0 | 0.74255 | 0.47199 | 233.7522 | 0 | 0 | 0 | 0 | 0 | 200 | 82800 | 200 | 588263.4309 | 510.81 | 33.7522
6281 | 9 | 0 | 0.47552 | 0.35317 | 151.7752 | 0 | 0 | 0 | 0 | 0 | 151.7752 | 82800 | 151.7752 | 588415.2062 | 510.81 | 0
6282 | 9 | 0 | 0.20847 | 0.22961 | 69.5985 | 0 | 0 | 0 | 0 | 0 | 69.5985 | 82800 | 69.5985 | 588484.8046 | 510.81 | 0
6283 | 9 | 0 | 0.008336 | 0.21115 | 11.0434 | 0 | 0 | 0 | 0 | 0 | 11.0434 | 82800 | 11.0434 | 588495.848 | 510.81 | 0
6284 | 9 | 1 | 0 | 0.38493 | 15.7438 | 200 | 15.7438 | 180 | 195.7438 | 0 | 0 | 82600 | 195.7438 | 588691.5918 | 330.81 | 0
6285 | 9 | 1 | 0 | 0.47378 | 19.3777 | 200 | 19.3777 | 180 | 199.3777 | 0 | 0 | 82400 | 199.3777 | 588890.9695 | 150.81 | 0
6286 | 9 | 0 | 0 | 0.48125 | 19.6831 | 0 | 0 | 0 | 0 | 19.6831 | 0 | 82400 | 0 | 588890.9695 | 167.8713 | 0
6287 | 9 | 0 | 0 | 0.64405 | 26.3417 | 0 | 0 | 0 | 0 | 26.3417 | 0 | 82400 | 0 | 588890.9695 | 190.7043 | 0
6288 | 9 | 0 | 0 | 0.51801 | 21.1865 | 0 | 0 | 0 | 0 | 21.1865 | 0 | 82400 | 0 | 588890.9695 | 209.0688 | 0
6289 | 9 | 0 | 0 | 0.605 | 24.7443 | 0 | 0 | 0 | 0 | 24.7443 | 0 | 82400 | 0 | 588890.9695 | 230.5171 | 0
6290 | 9 | 0 | 0 | 0.4998 | 20.4417 | 0 | 0 | 0 | 0 | 20.4417 | 0 | 82400 | 0 | 588890.9695 | 248.236 | 0
6291 | 9 | 0 | 0 | 0.32584 | 13.3269 | 0 | 0 | 0 | 0 | 13.3269 | 0 | 82400 | 0 | 588890.9695 | 259.7877 | 0
6292 | 9 | 0 | 0 | 0.65189 | 26.6621 | 0 | 0 | 0 | 0 | 26.6621 | 0 | 82400 | 0 | 588890.9695 | 282.8985 | 0
6293 | 9 | 0 | 0 | 0.49248 | 20.1423 | 0 | 0 | 0 | 0 | 20.1423 | 0 | 82400 | 0 | 588890.9695 | 300.3578 | 0
6294 | 9 | 0 | 0 | 0.88982 | 36.3936 | 0 | 0 | 0 | 0 | 36.3936 | 0 | 82400 | 0 | 588890.9695 | 331.9038 | 0
6295 | 9 | 0 | 0.007694 | 0.69893 | 30.8084 | 0 | 0 | 0 | 0 | 30.8084 | 0 | 82400 | 0 | 588890.9695 | 358.6085 | 0
6296 | 9 | 1 | 0.19242 | 0.65598 | 82.3998 | 200 | 82.3998 | 117.6002 | 200 | 0 | 0 | 82200 | 200 | 589090.9695 | 241.0082 | 0
6297 | 9 | 1 | 0.4389 | 0.36083 | 141.5122 | 200 | 141.5122 | 58.4878 | 200 | 0 | 0 | 82000 | 200 | 589290.9695 | 182.5205 | 0
6298 | 9 | 0 | 0.68536 | 0.39291 | 214.0018 | 0 | 0 | 0 | 0 | 180 | 34.0018 | 82000 | 34.0018 | 589324.9713 | 338.5445 | 0
6299 | 9 | 0 | 0.89167 | 0.23533 | 267.1394 | 0 | 0 | 0 | 0 | 180 | 87.1394 | 82000 | 87.1394 | 589412.1108 | 494.5685 | 0
6300 | 9 | 0 | 1 | 0.22251 | 297.9007 | 0 | 0 | 0 | 0 | 18.7373 | 200 | 82000 | 200 | 589612.1108 | 510.81 | 79.1633
6301 | 9 | 0 | 1 | 0.30483 | 301.2676 | 0 | 0 | 0 | 0 | 0 | 200 | 82000 | 200 | 589812.1108 | 510.81 | 101.2676
6302 | 9 | 0 | 1 | 0.43465 | 306.5773 | 0 | 0 | 0 | 0 | 0 | 200 | 82000 | 200 | 590012.1108 | 510.81 | 106.5773
6303 | 9 | 0 | 0.89167 | 0.66894 | 284.8743 | 0 | 0 | 0 | 0 | 0 | 200 | 82000 | 200 | 590212.1108 | 510.81 | 84.8743
6304 | 9 | 0 | 0.68536 | 0.52772 | 219.5159 | 0 | 0 | 0 | 0 | 0 | 200 | 82000 | 200 | 590412.1108 | 510.81 | 19.5159
6305 | 9 | 0 | 0.4389 | 0.21946 | 135.7302 | 0 | 0 | 0 | 0 | 0 | 135.7302 | 82000 | 135.7302 | 590547.8409 | 510.81 | 0
6306 | 9 | 0 | 0.19242 | 0.17347 | 62.6651 | 0 | 0 | 0 | 0 | 0 | 62.6651 | 82000 | 62.6651 | 590610.506 | 510.81 | 0
6307 | 9 | 0 | 0.007694 | 0.18489 | 9.7839 | 0 | 0 | 0 | 0 | 0 | 9.7839 | 82000 | 9.7839 | 590620.2899 | 510.81 | 0
6308 | 9 | 1 | 0 | 0.24515 | 10.0268 | 200 | 10.0268 | 180 | 190.0268 | 0 | 0 | 81800 | 190.0268 | 590810.3167 | 330.81 | 0
6309 | 9 | 1 | 0 | 0.17518 | 7.1648 | 200 | 7.1648 | 180 | 187.1648 | 0 | 0 | 81600 | 187.1648 | 590997.4814 | 150.81 | 0
6310 | 9 | 0 | 0 | 0.154 | 6.2986 | 0 | 0 | 0 | 0 | 6.2986 | 0 | 81600 | 0 | 590997.4814 | 156.2696 | 0
6311 | 9 | 0 | 0 | 0.17442 | 7.1338 | 0 | 0 | 0 | 0 | 7.1338 | 0 | 81600 | 0 | 590997.4814 | 162.4532 | 0
6312 | 9 | 0 | 0 | 0.18006 | 7.3643 | 0 | 0 | 0 | 0 | 7.3643 | 0 | 81600 | 0 | 590997.4814 | 168.8366 | 0
6313 | 9 | 0 | 0 | 0.14261 | 5.8328 | 0 | 0 | 0 | 0 | 5.8328 | 0 | 81600 | 0 | 590997.4814 | 173.8925 | 0
6314 | 9 | 0 | 0 | 0.13264 | 5.4249 | 0 | 0 | 0 | 0 | 5.4249 | 0 | 81600 | 0 | 590997.4814 | 178.5948 | 0
6315 | 9 | 0 | 0 | 0.10588 | 4.3305 | 0 | 0 | 0 | 0 | 4.3305 | 0 | 81600 | 0 | 590997.4814 | 182.3485 | 0
6316 | 9 | 0 | 0 | 0.091177 | 3.7291 | 0 | 0 | 0 | 0 | 3.7291 | 0 | 81600 | 0 | 590997.4814 | 185.5809 | 0
6317 | 9 | 0 | 0 | 0.10814 | 4.4229 | 0 | 0 | 0 | 0 | 4.4229 | 0 | 81600 | 0 | 590997.4814 | 189.4146 | 0
6318 | 9 | 0 | 0 | 0.089702 | 3.6688 | 0 | 0 | 0 | 0 | 3.6688 | 0 | 81600 | 0 | 590997.4814 | 192.5948 | 0
6319 | 9 | 0 | 0.007833 | 0.13398 | 7.742 | 0 | 0 | 0 | 0 | 7.742 | 0 | 81600 | 0 | 590997.4814 | 199.3056 | 0
6320 | 9 | 1 | 0.1959 | 0.14696 | 62.587 | 200 | 62.587 | 137.413 | 200 | 0 | 0 | 81400 | 200 | 591197.4814 | 61.8925 | 0
6321 | 9 | 1 | 0.44684 | 0.17832 | 136.3415 | 200 | 136.3415 | 61.8925 | 198.234 | 0 | 0 | 81200 | 198.234 | 591395.7154 | 0 | 0
6322 | 9 | 0 | 0.69776 | 0.21016 | 210.1095 | 0 | 0 | 0 | 0 | 180 | 30.1095 | 81200 | 30.1095 | 591425.8249 | 156.024 | 0
6323 | 9 | 0 | 0.90781 | 0.16739 | 269.0212 | 0 | 0 | 0 | 0 | 180 | 89.0212 | 81200 | 89.0212 | 591514.8461 | 312.048 | 0
6324 | 9 | 0 | 1 | 0.2491 | 298.9883 | 0 | 0 | 0 | 0 | 180 | 118.9883 | 81200 | 118.9883 | 591633.8345 | 468.072 | 0
6325 | 9 | 0 | 1 | 0.31252 | 301.5821 | 0 | 0 | 0 | 0 | 49.3055 | 200 | 81200 | 200 | 591833.8345 | 510.81 | 52.2767
6326 | 9 | 0 | 1 | 0.53521 | 310.6903 | 0 | 0 | 0 | 0 | 0 | 200 | 81200 | 200 | 592033.8345 | 510.81 | 110.6903
6327 | 9 | 0 | 0.90781 | 0.75727 | 293.1475 | 0 | 0 | 0 | 0 | 0 | 200 | 81200 | 200 | 592233.8345 | 510.81 | 93.1475
6328 | 9 | 0 | 0.69776 | 0.69668 | 230.0082 | 0 | 0 | 0 | 0 | 0 | 200 | 81200 | 200 | 592433.8345 | 510.81 | 30.0082
6329 | 9 | 0 | 0.44684 | 0.72671 | 158.7707 | 0 | 0 | 0 | 0 | 0 | 158.7707 | 81200 | 158.7707 | 592592.6051 | 510.81 | 0
6330 | 9 | 0 | 0.1959 | 0.75655 | 87.5191 | 0 | 0 | 0 | 0 | 0 | 87.5191 | 81200 | 87.5191 | 592680.1242 | 510.81 | 0
6331 | 9 | 0 | 0.007833 | 0.77585 | 33.9944 | 0 | 0 | 0 | 0 | 0 | 33.9944 | 81200 | 33.9944 | 592714.1187 | 510.81 | 0
6332 | 9 | 1 | 0 | 0.70508 | 28.838 | 200 | 28.838 | 171.162 | 200 | 0 | 0 | 81000 | 200 | 592914.1187 | 339.648 | 0
6333 | 9 | 1 | 0 | 0.56079 | 22.9364 | 200 | 22.9364 | 177.0636 | 200 | 0 | 0 | 80800 | 200 | 593114.1187 | 162.5844 | 0
6334 | 9 | 0 | 0 | 0.5801 | 23.7261 | 0 | 0 | 0 | 0 | 23.7261 | 0 | 80800 | 0 | 593114.1187 | 183.1502 | 0
6335 | 9 | 0 | 0 | 0.45353 | 18.5495 | 0 | 0 | 0 | 0 | 18.5495 | 0 | 80800 | 0 | 593114.1187 | 199.2289 | 0
6336 | 9 | 0 | 0 | 0.4452 | 18.2086 | 0 | 0 | 0 | 0 | 18.2086 | 0 | 80800 | 0 | 593114.1187 | 215.0121 | 0
6337 | 9 | 0 | 0 | 0.37172 | 15.2033 | 0 | 0 | 0 | 0 | 15.2033 | 0 | 80800 | 0 | 593114.1187 | 228.1903 | 0
6338 | 9 | 0 | 0 | 0.26422 | 10.8068 | 0 | 0 | 0 | 0 | 10.8068 | 0 | 80800 | 0 | 593114.1187 | 237.5576 | 0
6339 | 9 | 0 | 0 | 0.23762 | 9.7186 | 0 | 0 | 0 | 0 | 9.7186 | 0 | 80800 | 0 | 593114.1187 | 245.9817 | 0
6340 | 9 | 0 | 0 | 0.22114 | 9.0446 | 0 | 0 | 0 | 0 | 9.0446 | 0 | 80800 | 0 | 593114.1187 | 253.8216 | 0
6341 | 9 | 0 | 0 | 0.30149 | 12.331 | 0 | 0 | 0 | 0 | 12.331 | 0 | 80800 | 0 | 593114.1187 | 264.5101 | 0
6342 | 9 | 0 | 0 | 0.35761 | 14.626 | 0 | 0 | 0 | 0 | 14.626 | 0 | 80800 | 0 | 593114.1187 | 277.188 | 0
6343 | 9 | 0 | 0.007234 | 0.31751 | 15.0752 | 0 | 0 | 0 | 0 | 15.0752 | 0 | 80800 | 0 | 593114.1187 | 290.2552 | 0
6344 | 9 | 1 | 0.1809 | 0.24902 | 62.4283 | 200 | 62.4283 | 137.5717 | 200 | 0 | 0 | 80600 | 200 | 593314.1187 | 152.6834 | 0
6345 | 9 | 1 | 0.41262 | 0.20071 | 127.3746 | 200 | 127.3746 | 72.6254 | 200 | 0 | 0 | 80400 | 200 | 593514.1187 | 80.0581 | 0
6346 | 9 | 0 | 0.64433 | 0.20822 | 194.598 | 0 | 0 | 0 | 0 | 180 | 14.598 | 80400 | 14.598 | 593528.7167 | 236.0821 | 0
6347 | 9 | 0 | 0.83829 | 0.24227 | 252.0063 | 0 | 0 | 0 | 0 | 180 | 72.0063 | 80400 | 72.0063 | 593600.723 | 392.1061 | 0
6348 | 9 | 0 | 0.96648 | 0.2544 | 289.5239 | 0 | 0 | 0 | 0 | 136.945 | 152.5789 | 80400 | 152.5789 | 593753.3019 | 510.81 | 0
6349 | 9 | 0 | 1 | 0.23536 | 298.4263 | 0 | 0 | 0 | 0 | 0 | 200 | 80400 | 200 | 593953.3019 | 510.81 | 98.4263
6350 | 9 | 0 | 0.96648 | 0.18977 | 286.8806 | 0 | 0 | 0 | 0 | 0 | 200 | 80400 | 200 | 594153.3019 | 510.81 | 86.8806
6351 | 9 | 0 | 0.83829 | 0.21886 | 251.0488 | 0 | 0 | 0 | 0 | 0 | 200 | 80400 | 200 | 594353.3019 | 510.81 | 51.0488
6352 | 9 | 0 | 0.64433 | 0.3541 | 200.5642 | 0 | 0 | 0 | 0 | 0 | 200 | 80400 | 200 | 594553.3019 | 510.81 | 0.5642
6353 | 9 | 0 | 0.41262 | 0.51004 | 140.0263 | 0 | 0 | 0 | 0 | 0 | 140.0263 | 80400 | 140.0263 | 594693.3282 | 510.81 | 0
6354 | 9 | 0 | 0.1809 | 0.45768 | 70.9623 | 0 | 0 | 0 | 0 | 0 | 70.9623 | 80400 | 70.9623 | 594764.2906 | 510.81 | 0
6355 | 9 | 0 | 0.007234 | 0.35866 | 16.7583 | 0 | 0 | 0 | 0 | 0 | 16.7583 | 80400 | 16.7583 | 594781.0488 | 510.81 | 0
6356 | 9 | 1 | 0 | 0.32523 | 13.3017 | 200 | 13.3017 | 180 | 193.3017 | 0 | 0 | 80200 | 193.3017 | 594974.3506 | 330.81 | 0
6357 | 9 | 1 | 0 | 0.25033 | 10.2387 | 200 | 10.2387 | 180 | 190.2387 | 0 | 0 | 80000 | 190.2387 | 595164.5893 | 150.81 | 0
6358 | 9 | 0 | 0 | 0.2365 | 9.6729 | 0 | 0 | 0 | 0 | 9.6729 | 0 | 80000 | 0 | 595164.5893 | 159.1945 | 0
6359 | 9 | 0 | 0 | 0.2177 | 8.9039 | 0 | 0 | 0 | 0 | 8.9039 | 0 | 80000 | 0 | 595164.5893 | 166.9124 | 0
6360 | 9 | 0 | 0 | 0.2793 | 11.4233 | 0 | 0 | 0 | 0 | 11.4233 | 0 | 80000 | 0 | 595164.5893 | 176.8141 | 0
6361 | 9 | 0 | 0 | 0.40046 | 16.3788 | 0 | 0 | 0 | 0 | 16.3788 | 0 | 80000 | 0 | 595164.5893 | 191.0113 | 0
6362 | 9 | 0 | 0 | 0.42248 | 17.2794 | 0 | 0 | 0 | 0 | 17.2794 | 0 | 80000 | 0 | 595164.5893 | 205.989 | 0
6363 | 9 | 0 | 0 | 0.51376 | 21.0129 | 0 | 0 | 0 | 0 | 21.0129 | 0 | 80000 | 0 | 595164.5893 | 224.203 | 0
6364 | 9 | 0 | 0 | 0.73045 | 29.8756 | 0 | 0 | 0 | 0 | 29.8756 | 0 | 80000 | 0 | 595164.5893 | 250.0992 | 0
6365 | 9 | 0 | 0 | 0.91346 | 37.3605 | 0 | 0 | 0 | 0 | 37.3605 | 0 | 80000 | 0 | 595164.5893 | 282.4833 | 0
6366 | 9 | 0 | 0 | 0.69476 | 28.4158 | 0 | 0 | 0 | 0 | 28.4158 | 0 | 80000 | 0 | 595164.5893 | 307.1141 | 0
6367 | 9 | 0 | 0.009671 | 0.85303 | 37.682 | 0 | 0 | 0 | 0 | 37.682 | 0 | 80000 | 0 | 595164.5893 | 339.7769 | 0
6368 | 9 | 1 | 0.24185 | 0.74077 | 100.1429 | 200 | 100.1429 | 99.8571 | 200 | 0 | 0 | 79800 | 200 | 595364.5893 | 239.9197 | 0
6369 | 9 | 1 | 0.55164 | 0.47941 | 178.9227 | 200 | 178.9227 | 21.0773 | 200 | 0 | 0 | 79600 | 200 | 595564.5893 | 218.8424 | 0
6370 | 9 | 0 | 0.86142 | 0.46714 | 267.8829 | 0 | 0 | 0 | 0 | 180 | 87.8829 | 79600 | 87.8829 | 595652.4721 | 374.8664 | 0
6371 | 9 | 0 | 1 | 0.42589 | 306.2187 | 0 | 0 | 0 | 0 | 156.8338 | 149.3849 | 79600 | 149.3849 | 595801.857 | 510.81 | 0
6372 | 9 | 0 | 1 | 0.41293 | 305.6887 | 0 | 0 | 0 | 0 | 0 | 200 | 79600 | 200 | 596001.857 | 510.81 | 105.6887
6373 | 9 | 0 | 1 | 0.40354 | 305.3046 | 0 | 0 | 0 | 0 | 0 | 200 | 79600 | 200 | 596201.857 | 510.81 | 105.3046
6374 | 9 | 0 | 1 | 0.46392 | 307.7744 | 0 | 0 | 0 | 0 | 0 | 200 | 79600 | 200 | 596401.857 | 510.81 | 107.7744
6375 | 9 | 0 | 1 | 0.58662 | 312.7927 | 0 | 0 | 0 | 0 | 0 | 200 | 79600 | 200 | 596601.857 | 510.81 | 112.7927
6376 | 9 | 0 | 0.86142 | 0.5227 | 270.1551 | 0 | 0 | 0 | 0 | 0 | 200 | 79600 | 200 | 596801.857 | 510.81 | 70.1551
6377 | 9 | 0 | 0.55164 | 0.57157 | 182.692 | 0 | 0 | 0 | 0 | 0 | 182.692 | 79600 | 182.692 | 596984.549 | 510.81 | 0
6378 | 9 | 0 | 0.24185 | 0.65242 | 96.5295 | 0 | 0 | 0 | 0 | 0 | 96.5295 | 79600 | 96.5295 | 597081.0785 | 510.81 | 0
6379 | 9 | 0 | 0.009671 | 0.59011 | 26.9283 | 0 | 0 | 0 | 0 | 0 | 26.9283 | 79600 | 26.9283 | 597108.0068 | 510.81 | 0
6380 | 9 | 1 | 0 | 0.46893 | 19.1794 | 200 | 19.1794 | 180 | 199.1794 | 0 | 0 | 79400 | 199.1794 | 597307.1862 | 330.81 | 0
6381 | 9 | 1 | 0 | 0.40318 | 16.4902 | 200 | 16.4902 | 180 | 196.4902 | 0 | 0 | 79200 | 196.4902 | 597503.6764 | 150.81 | 0
6382 | 9 | 0 | 0 | 0.53054 | 21.6991 | 0 | 0 | 0 | 0 | 21.6991 | 0 | 79200 | 0 | 597503.6764 | 169.6188 | 0
6383 | 9 | 0 | 0 | 0.54911 | 22.4584 | 0 | 0 | 0 | 0 | 22.4584 | 0 | 79200 | 0 | 597503.6764 | 189.0857 | 0
6384 | 9 | 0 | 0 | 0.62998 | 25.766 | 0 | 0 | 0 | 0 | 25.766 | 0 | 79200 | 0 | 597503.6764 | 211.4197 | 0
6385 | 9 | 0 | 0 | 0.81439 | 33.3086 | 0 | 0 | 0 | 0 | 33.3086 | 0 | 79200 | 0 | 597503.6764 | 240.2916 | 0
6386 | 9 | 0 | 0 | 0.65444 | 26.7666 | 0 | 0 | 0 | 0 | 26.7666 | 0 | 79200 | 0 | 597503.6764 | 263.4929 | 0
6387 | 9 | 0 | 0 | 0.45394 | 18.5661 | 0 | 0 | 0 | 0 | 18.5661 | 0 | 79200 | 0 | 597503.6764 | 279.586 | 0
6388 | 9 | 0 | 0 | 0.4792 | 19.5992 | 0 | 0 | 0 | 0 | 19.5992 | 0 | 79200 | 0 | 597503.6764 | 296.5747 | 0
6389 | 9 | 0 | 0 | 0.24214 | 9.9036 | 0 | 0 | 0 | 0 | 9.9036 | 0 | 79200 | 0 | 597503.6764 | 305.1591 | 0
6390 | 9 | 0 | 0 | 0.29712 | 12.1522 | 0 | 0 | 0 | 0 | 12.1522 | 0 | 79200 | 0 | 597503.6764 | 315.6927 | 0
6391 | 9 | 0 | 0.007628 | 0.2736 | 13.3933 | 0 | 0 | 0 | 0 | 13.3933 | 0 | 79200 | 0 | 597503.6764 | 327.302 | 0
6392 | 9 | 1 | 0.19076 | 0.3657 | 70.05 | 200 | 70.05 | 129.95 | 200 | 0 | 0 | 79000 | 200 | 597703.6764 | 197.352 | 0
6393 | 9 | 1 | 0.43513 | 0.24961 | 135.8739 | 200 | 135.8739 | 64.1261 | 200 | 0 | 0 | 78800 | 200 | 597903.6764 | 133.2258 | 0
6394 | 9 | 0 | 0.67947 | 0.29546 | 208.3153 | 0 | 0 | 0 | 0 | 180 | 28.3153 | 78800 | 28.3153 | 597931.9917 | 289.2498 | 0
6395 | 9 | 0 | 0.88401 | 0.30906 | 267.9423 | 0 | 0 | 0 | 0 | 180 | 87.9423 | 78800 | 87.9423 | 598019.934 | 445.2738 | 0
6396 | 9 | 0 | 1 | 0.33038 | 302.3124 | 0 | 0 | 0 | 0 | 75.6071 | 200 | 78800 | 200 | 598219.934 | 510.81 | 26.7054
6397 | 9 | 0 | 1 | 0.40008 | 305.1634 | 0 | 0 | 0 | 0 | 0 | 200 | 78800 | 200 | 598419.934 | 510.81 | 105.1634
6398 | 9 | 0 | 1 | 0.69218 | 317.1102 | 0 | 0 | 0 | 0 | 0 | 200 | 78800 | 200 | 598619.934 | 510.81 | 117.1102
6399 | 9 | 0 | 0.88401 | 0.58853 | 279.3723 | 0 | 0 | 0 | 0 | 0 | 200 | 78800 | 200 | 598819.934 | 510.81 | 79.3723
6400 | 9 | 0 | 0.67947 | 0.47508 | 215.6617 | 0 | 0 | 0 | 0 | 0 | 200 | 78800 | 200 | 599019.934 | 510.81 | 15.6617
6401 | 9 | 0 | 0.43513 | 0.47467 | 145.0789 | 0 | 0 | 0 | 0 | 0 | 145.0789 | 78800 | 145.0789 | 599165.0129 | 510.81 | 0
6402 | 9 | 0 | 0.19076 | 0.59296 | 79.3448 | 0 | 0 | 0 | 0 | 0 | 79.3448 | 78800 | 79.3448 | 599244.3578 | 510.81 | 0
6403 | 9 | 0 | 0.007628 | 0.83889 | 36.5137 | 0 | 0 | 0 | 0 | 0 | 36.5137 | 78800 | 36.5137 | 599280.8715 | 510.81 | 0
6404 | 9 | 1 | 0 | 0.69766 | 28.5342 | 200 | 28.5342 | 171.4658 | 200 | 0 | 0 | 78600 | 200 | 599480.8715 | 339.3442 | 0
6405 | 9 | 1 | 0 | 0.84203 | 34.4391 | 200 | 34.4391 | 165.5609 | 200 | 0 | 0 | 78400 | 200 | 599680.8715 | 173.7833 | 0
6406 | 9 | 0 | 0 | 0.53368 | 21.8275 | 0 | 0 | 0 | 0 | 21.8275 | 0 | 78400 | 0 | 599680.8715 | 192.7034 | 0
6407 | 9 | 0 | 0 | 0.51283 | 20.9746 | 0 | 0 | 0 | 0 | 20.9746 | 0 | 78400 | 0 | 599680.8715 | 210.8842 | 0
6408 | 9 | 0 | 0 | 0.47941 | 19.6078 | 0 | 0 | 0 | 0 | 19.6078 | 0 | 78400 | 0 | 599680.8715 | 227.8802 | 0
6409 | 9 | 0 | 0 | 0.4067 | 16.6342 | 0 | 0 | 0 | 0 | 16.6342 | 0 | 78400 | 0 | 599680.8715 | 242.2987 | 0
6410 | 9 | 0 | 0 | 0.39495 | 16.1535 | 0 | 0 | 0 | 0 | 16.1535 | 0 | 78400 | 0 | 599680.8715 | 256.3005 | 0
6411 | 9 | 0 | 0 | 0.44517 | 18.2074 | 0 | 0 | 0 | 0 | 18.2074 | 0 | 78400 | 0 | 599680.8715 | 272.0827 | 0
6412 | 9 | 0 | 0 | 0.50569 | 20.6828 | 0 | 0 | 0 | 0 | 20.6828 | 0 | 78400 | 0 | 599680.8715 | 290.0106 | 0
6413 | 9 | 0 | 0 | 0.41608 | 17.0175 | 0 | 0 | 0 | 0 | 17.0175 | 0 | 78400 | 0 | 599680.8715 | 304.7614 | 0
6414 | 9 | 0 | 0 | 0.60166 | 24.608 | 0 | 0 | 0 | 0 | 24.608 | 0 | 78400 | 0 | 599680.8715 | 326.0916 | 0
6415 | 9 | 0 | 0.009657 | 0.46647 | 21.8677 | 0 | 0 | 0 | 0 | 21.8677 | 0 | 78400 | 0 | 599680.8715 | 345.0466 | 0
6416 | 9 | 1 | 0.2415 | 0.3727 | 84.9877 | 200 | 84.9877 | 115.0123 | 200 | 0 | 0 | 78200 | 200 | 599880.8715 | 230.0342 | 0
6417 | 9 | 1 | 0.55085 | 0.41279 | 175.9678 | 200 | 175.9678 | 24.0322 | 200 | 0 | 0 | 78000 | 200 | 600080.8715 | 206.002 | 0
6418 | 9 | 0 | 0.86017 | 0.37108 | 263.5943 | 0 | 0 | 0 | 0 | 180 | 83.5943 | 78000 | 83.5943 | 600164.4657 | 362.026 | 0
6419 | 9 | 0 | 1 | 0.28926 | 300.6308 | 0 | 0 | 0 | 0 | 171.6474 | 128.9834 | 78000 | 128.9834 | 600293.4491 | 510.81 | 0
6420 | 9 | 0 | 1 | 0.20814 | 297.3128 | 0 | 0 | 0 | 0 | 0 | 200 | 78000 | 200 | 600493.4491 | 510.81 | 97.3128
6421 | 9 | 0 | 1 | 0.20182 | 297.0543 | 0 | 0 | 0 | 0 | 0 | 200 | 78000 | 200 | 600693.4491 | 510.81 | 97.0543
6422 | 9 | 0 | 1 | 0.20893 | 297.3453 | 0 | 0 | 0 | 0 | 0 | 200 | 78000 | 200 | 600893.4491 | 510.81 | 97.3453
6423 | 9 | 0 | 1 | 0.29097 | 300.7006 | 0 | 0 | 0 | 0 | 0 | 200 | 78000 | 200 | 601093.4491 | 510.81 | 100.7006
6424 | 9 | 0 | 0.86017 | 0.34155 | 262.3867 | 0 | 0 | 0 | 0 | 0 | 200 | 78000 | 200 | 601293.4491 | 510.81 | 62.3867
6425 | 9 | 0 | 0.55085 | 0.26727 | 170.0161 | 0 | 0 | 0 | 0 | 0 | 170.0161 | 78000 | 170.0161 | 601463.4652 | 510.81 | 0
6426 | 9 | 0 | 0.2415 | 0.30179 | 82.0875 | 0 | 0 | 0 | 0 | 0 | 82.0875 | 78000 | 82.0875 | 601545.5527 | 510.81 | 0
6427 | 9 | 0 | 0.009657 | 0.2642 | 13.5948 | 0 | 0 | 0 | 0 | 0 | 13.5948 | 78000 | 13.5948 | 601559.1475 | 510.81 | 0
6428 | 9 | 1 | 0 | 0.28588 | 11.6925 | 200 | 11.6925 | 180 | 191.6925 | 0 | 0 | 77800 | 191.6925 | 601750.84 | 330.81 | 0
6429 | 9 | 1 | 0 | 0.25789 | 10.5477 | 200 | 10.5477 | 180 | 190.5477 | 0 | 0 | 77600 | 190.5477 | 601941.3877 | 150.81 | 0
6430 | 9 | 0 | 0 | 0.28504 | 11.6581 | 0 | 0 | 0 | 0 | 11.6581 | 0 | 77600 | 0 | 601941.3877 | 160.9153 | 0
6431 | 9 | 0 | 0 | 0.34736 | 14.207 | 0 | 0 | 0 | 0 | 14.207 | 0 | 77600 | 0 | 601941.3877 | 173.2299 | 0
6432 | 9 | 0 | 0 | 0.39339 | 16.0895 | 0 | 0 | 0 | 0 | 16.0895 | 0 | 77600 | 0 | 601941.3877 | 187.1763 | 0
6433 | 9 | 0 | 0 | 0.38687 | 15.8229 | 0 | 0 | 0 | 0 | 15.8229 | 0 | 77600 | 0 | 601941.3877 | 200.8916 | 0
6434 | 9 | 0 | 0 | 0.30844 | 12.6152 | 0 | 0 | 0 | 0 | 12.6152 | 0 | 77600 | 0 | 601941.3877 | 211.8264 | 0
6435 | 9 | 0 | 0 | 0.26769 | 10.9486 | 0 | 0 | 0 | 0 | 10.9486 | 0 | 77600 | 0 | 601941.3877 | 221.3167 | 0
6436 | 9 | 0 | 0 | 0.42845 | 17.5236 | 0 | 0 | 0 | 0 | 17.5236 | 0 | 77600 | 0 | 601941.3877 | 236.5061 | 0
6437 | 9 | 0 | 0 | 0.34015 | 13.9121 | 0 | 0 | 0 | 0 | 13.9121 | 0 | 77600 | 0 | 601941.3877 | 248.5651 | 0
6438 | 9 | 0 | 0 | 0.34472 | 14.099 | 0 | 0 | 0 | 0 | 14.099 | 0 | 77600 | 0 | 601941.3877 | 260.7861 | 0
6439 | 9 | 0 | 0.008466 | 0.40655 | 19.0727 | 0 | 0 | 0 | 0 | 19.0727 | 0 | 77600 | 0 | 601941.3877 | 277.3184 | 0
6440 | 9 | 1 | 0.21173 | 0.52354 | 82.561 | 200 | 82.561 | 117.439 | 200 | 0 | 0 | 77400 | 200 | 602141.3877 | 159.8793 | 0
6441 | 9 | 1 | 0.48295 | 0.6773 | 167.1783 | 200 | 167.1783 | 32.8217 | 200 | 0 | 0 | 77200 | 200 | 602341.3877 | 127.0577 | 0
6442 | 9 | 0 | 0.75415 | 0.87663 | 253.6531 | 0 | 0 | 0 | 0 | 180 | 73.6531 | 77200 | 73.6531 | 602415.0408 | 283.0817 | 0
6443 | 9 | 0 | 0.98117 | 0.80724 | 316.3781 | 0 | 0 | 0 | 0 | 180 | 136.3781 | 77200 | 136.3781 | 602551.4189 | 439.1057 | 0
6444 | 9 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 82.7231 | 200 | 77200 | 200 | 602751.4189 | 510.81 | 46.9769
6445 | 9 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 0 | 200 | 77200 | 200 | 602951.4189 | 510.81 | 129.7
6446 | 9 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 0 | 200 | 77200 | 200 | 603151.4189 | 510.81 | 129.7
6447 | 9 | 0 | 0.98117 | 1 | 324.2619 | 0 | 0 | 0 | 0 | 0 | 200 | 77200 | 200 | 603351.4189 | 510.81 | 124.2619
6448 | 9 | 0 | 0.75415 | 1 | 258.6988 | 0 | 0 | 0 | 0 | 0 | 200 | 77200 | 200 | 603551.4189 | 510.81 | 58.6988
6449 | 9 | 0 | 0.48295 | 1 | 180.3768 | 0 | 0 | 0 | 0 | 0 | 180.3768 | 77200 | 180.3768 | 603731.7958 | 510.81 | 0
6450 | 9 | 0 | 0.21173 | 0.76223 | 92.3234 | 0 | 0 | 0 | 0 | 0 | 92.3234 | 77200 | 92.3234 | 603824.1192 | 510.81 | 0
6451 | 9 | 0 | 0.008466 | 0.77818 | 34.2725 | 0 | 0 | 0 | 0 | 0 | 34.2725 | 77200 | 34.2725 | 603858.3917 | 510.81 | 0
6452 | 9 | 1 | 0 | 0.9677 | 39.579 | 200 | 39.579 | 160.421 | 200 | 0 | 0 | 77000 | 200 | 604058.3917 | 350.389 | 0
6453 | 9 | 1 | 0 | 0.91772 | 37.5349 | 200 | 37.5349 | 162.4651 | 200 | 0 | 0 | 76800 | 200 | 604258.3917 | 187.9239 | 0
6454 | 9 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 76800 | 0 | 604258.3917 | 223.376 | 0
6455 | 9 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 76800 | 0 | 604258.3917 | 258.8281 | 0
6456 | 9 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 76800 | 0 | 604258.3917 | 294.2802 | 0
6457 | 9 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 76800 | 0 | 604258.3917 | 329.7324 | 0
6458 | 9 | 0 | 0 | 0.83433 | 34.1243 | 0 | 0 | 0 | 0 | 34.1243 | 0 | 76800 | 0 | 604258.3917 | 359.3113 | 0
6459 | 9 | 0 | 0 | 0.84888 | 34.7193 | 0 | 0 | 0 | 0 | 34.7193 | 0 | 76800 | 0 | 604258.3917 | 389.406 | 0
6460 | 9 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 76800 | 0 | 604258.3917 | 424.8581 | 0
6461 | 9 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 76800 | 0 | 604258.3917 | 460.3102 | 0
6462 | 9 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 76800 | 0 | 604258.3917 | 495.7623 | 0
6463 | 9 | 0 | 0.008525 | 1 | 43.362 | 0 | 0 | 0 | 0 | 17.36 | 26.002 | 76800 | 26.002 | 604284.3937 | 510.81 | 0
6464 | 9 | 1 | 0.21319 | 1 | 102.4704 | 200 | 102.4704 | 97.5296 | 200 | 0 | 0 | 76600 | 200 | 604484.3937 | 413.2804 | 0
6465 | 9 | 1 | 0.48629 | 0.90948 | 177.6379 | 200 | 177.6379 | 22.3621 | 200 | 0 | 0 | 76400 | 200 | 604684.3937 | 390.9183 | 0
6466 | 9 | 0 | 0.75936 | 0.84214 | 253.746 | 0 | 0 | 0 | 0 | 138.3153 | 115.4308 | 76400 | 115.4308 | 604799.8245 | 510.81 | 0
6467 | 9 | 0 | 0.98794 | 0.73405 | 315.3412 | 0 | 0 | 0 | 0 | 0 | 200 | 76400 | 200 | 604999.8245 | 510.81 | 115.3412
6468 | 9 | 0 | 1 | 0.52036 | 310.0826 | 0 | 0 | 0 | 0 | 0 | 200 | 76400 | 200 | 605199.8245 | 510.81 | 110.0826
6469 | 9 | 0 | 1 | 0.60395 | 313.5016 | 0 | 0 | 0 | 0 | 0 | 200 | 76400 | 200 | 605399.8245 | 510.81 | 113.5016
6470 | 9 | 0 | 1 | 0.51111 | 309.7044 | 0 | 0 | 0 | 0 | 0 | 200 | 76400 | 200 | 605599.8245 | 510.81 | 109.7044
6471 | 9 | 0 | 0.98794 | 0.57291 | 308.7505 | 0 | 0 | 0 | 0 | 0 | 200 | 76400 | 200 | 605799.8245 | 510.81 | 108.7505
6472 | 9 | 0 | 0.75936 | 0.48993 | 239.3406 | 0 | 0 | 0 | 0 | 0 | 200 | 76400 | 200 | 605999.8245 | 510.81 | 39.3406
6473 | 9 | 0 | 0.48629 | 0.42008 | 157.6211 | 0 | 0 | 0 | 0 | 0 | 157.6211 | 76400 | 157.6211 | 606157.4456 | 510.81 | 0
6474 | 9 | 0 | 0.21319 | 0.56703 | 84.7618 | 0 | 0 | 0 | 0 | 0 | 84.7618 | 76400 | 84.7618 | 606242.2074 | 510.81 | 0
6475 | 9 | 0 | 0.008525 | 0.39951 | 18.8021 | 0 | 0 | 0 | 0 | 0 | 18.8021 | 76400 | 18.8021 | 606261.0095 | 510.81 | 0
6476 | 9 | 1 | 0 | 0.45602 | 18.651 | 200 | 18.651 | 180 | 198.651 | 0 | 0 | 76200 | 198.651 | 606459.6606 | 330.81 | 0
6477 | 9 | 1 | 0 | 0.45912 | 18.7779 | 200 | 18.7779 | 180 | 198.7779 | 0 | 0 | 76000 | 198.7779 | 606658.4384 | 150.81 | 0
6478 | 9 | 0 | 0 | 0.74097 | 30.3058 | 0 | 0 | 0 | 0 | 30.3058 | 0 | 76000 | 0 | 606658.4384 | 177.0791 | 0
6479 | 9 | 0 | 0 | 0.58101 | 23.7633 | 0 | 0 | 0 | 0 | 23.7633 | 0 | 76000 | 0 | 606658.4384 | 197.6771 | 0
6480 | 9 | 0 | 0 | 0.54592 | 22.328 | 0 | 0 | 0 | 0 | 22.328 | 0 | 76000 | 0 | 606658.4384 | 217.031 | 0
6481 | 9 | 0 | 0 | 0.44599 | 18.241 | 0 | 0 | 0 | 0 | 18.241 | 0 | 76000 | 0 | 606658.4384 | 232.8423 | 0
6482 | 9 | 0 | 0 | 0.32543 | 13.3101 | 0 | 0 | 0 | 0 | 13.3101 | 0 | 76000 | 0 | 606658.4384 | 244.3795 | 0
6483 | 9 | 0 | 0 | 0.32088 | 13.124 | 0 | 0 | 0 | 0 | 13.124 | 0 | 76000 | 0 | 606658.4384 | 255.7554 | 0
6484 | 9 | 0 | 0 | 0.47593 | 19.4656 | 0 | 0 | 0 | 0 | 19.4656 | 0 | 76000 | 0 | 606658.4384 | 272.6282 | 0
6485 | 9 | 0 | 0 | 0.46457 | 19.0009 | 0 | 0 | 0 | 0 | 19.0009 | 0 | 76000 | 0 | 606658.4384 | 289.0981 | 0
6486 | 9 | 0 | 0 | 0.8502 | 34.7734 | 0 | 0 | 0 | 0 | 34.7734 | 0 | 76000 | 0 | 606658.4384 | 319.2397 | 0
6487 | 9 | 0 | 0.007057 | 0.85609 | 37.0521 | 0 | 0 | 0 | 0 | 37.0521 | 0 | 76000 | 0 | 606658.4384 | 351.3564 | 0
6488 | 9 | 1 | 0.17648 | 0.94286 | 89.5318 | 200 | 89.5318 | 110.4682 | 200 | 0 | 0 | 75800 | 200 | 606858.4384 | 240.8882 | 0
6489 | 9 | 1 | 0.40255 | 0.50119 | 136.7564 | 200 | 136.7564 | 63.2436 | 200 | 0 | 0 | 75600 | 200 | 607058.4384 | 177.6446 | 0
6490 | 9 | 0 | 0.6286 | 0.32316 | 194.7583 | 0 | 0 | 0 | 0 | 180 | 14.7583 | 75600 | 14.7583 | 607073.1968 | 333.6686 | 0
6491 | 9 | 0 | 0.81783 | 0.27002 | 247.2335 | 0 | 0 | 0 | 0 | 180 | 67.2335 | 75600 | 67.2335 | 607140.4303 | 489.6926 | 0
6492 | 9 | 0 | 0.9429 | 0.23452 | 281.8998 | 0 | 0 | 0 | 0 | 24.3625 | 200 | 75600 | 200 | 607340.4303 | 510.81 | 57.5373
6493 | 9 | 0 | 0.98655 | 0.19214 | 292.7753 | 0 | 0 | 0 | 0 | 0 | 200 | 75600 | 200 | 607540.4303 | 510.81 | 92.7753
6494 | 9 | 0 | 0.9429 | 0.35976 | 287.0221 | 0 | 0 | 0 | 0 | 0 | 200 | 75600 | 200 | 607740.4303 | 510.81 | 87.0221
6495 | 9 | 0 | 0.81783 | 0.31927 | 249.2478 | 0 | 0 | 0 | 0 | 0 | 200 | 75600 | 200 | 607940.4303 | 510.81 | 49.2478
6496 | 9 | 0 | 0.6286 | 0.27532 | 192.8016 | 0 | 0 | 0 | 0 | 0 | 192.8016 | 75600 | 192.8016 | 608133.2319 | 510.81 | 0
6497 | 9 | 0 | 0.40255 | 0.30381 | 128.6836 | 0 | 0 | 0 | 0 | 0 | 128.6836 | 75600 | 128.6836 | 608261.9155 | 510.81 | 0
6498 | 9 | 0 | 0.17648 | 0.36031 | 65.7054 | 0 | 0 | 0 | 0 | 0 | 65.7054 | 75600 | 65.7054 | 608327.6209 | 510.81 | 0
6499 | 9 | 0 | 0.007057 | 0.42636 | 19.4762 | 0 | 0 | 0 | 0 | 0 | 19.4762 | 75600 | 19.4762 | 608347.0971 | 510.81 | 0
6500 | 9 | 1 | 0 | 0.32303 | 13.2117 | 200 | 13.2117 | 180 | 193.2117 | 0 | 0 | 75400 | 193.2117 | 608540.3088 | 330.81 | 0
6501 | 9 | 1 | 0 | 0.47341 | 19.3626 | 200 | 19.3626 | 180 | 199.3626 | 0 | 0 | 75200 | 199.3626 | 608739.6714 | 150.81 | 0
6502 | 9 | 0 | 0 | 0.44286 | 18.1131 | 0 | 0 | 0 | 0 | 18.1131 | 0 | 75200 | 0 | 608739.6714 | 166.5104 | 0
6503 | 9 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 75200 | 0 | 608739.6714 | 201.9626 | 0
6504 | 9 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 75200 | 0 | 608739.6714 | 237.4147 | 0
6505 | 9 | 0 | 0 | 0.66141 | 27.0515 | 0 | 0 | 0 | 0 | 27.0515 | 0 | 75200 | 0 | 608739.6714 | 260.863 | 0
6506 | 9 | 0 | 0 | 0.66559 | 27.2226 | 0 | 0 | 0 | 0 | 27.2226 | 0 | 75200 | 0 | 608739.6714 | 284.4595 | 0
6507 | 9 | 0 | 0 | 0.7399 | 30.2618 | 0 | 0 | 0 | 0 | 30.2618 | 0 | 75200 | 0 | 608739.6714 | 310.6904 | 0
6508 | 9 | 0 | 0 | 0.87865 | 35.9368 | 0 | 0 | 0 | 0 | 35.9368 | 0 | 75200 | 0 | 608739.6714 | 341.8405 | 0
6509 | 9 | 0 | 0 | 0.90502 | 37.0152 | 0 | 0 | 0 | 0 | 37.0152 | 0 | 75200 | 0 | 608739.6714 | 373.9252 | 0
6510 | 9 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 75200 | 0 | 608739.6714 | 409.3773 | 0
6511 | 9 | 0 | 0.008254 | 1 | 43.2838 | 0 | 0 | 0 | 0 | 43.2838 | 0 | 75200 | 0 | 608739.6714 | 446.8957 | 0
6512 | 9 | 1 | 0.20641 | 1 | 100.5115 | 200 | 100.5115 | 99.4885 | 200 | 0 | 0 | 75000 | 200 | 608939.6714 | 347.4072 | 0
6513 | 9 | 1 | 0.47082 | 1 | 176.8717 | 200 | 176.8717 | 23.1283 | 200 | 0 | 0 | 74800 | 200 | 609139.6714 | 324.2788 | 0
6514 | 9 | 0 | 0.7352 | 1 | 253.2255 | 0 | 0 | 0 | 0 | 180 | 73.2255 | 74800 | 73.2255 | 609212.8969 | 480.3028 | 0
6515 | 9 | 0 | 0.95651 | 1 | 317.141 | 0 | 0 | 0 | 0 | 35.1952 | 200 | 74800 | 200 | 609412.8969 | 510.81 | 81.9458
6516 | 9 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 0 | 200 | 74800 | 200 | 609612.8969 | 510.81 | 129.7
6517 | 9 | 0 | 1 | 0.94792 | 327.57 | 0 | 0 | 0 | 0 | 0 | 200 | 74800 | 200 | 609812.8969 | 510.81 | 127.57
6518 | 9 | 0 | 1 | 0.83216 | 322.8353 | 0 | 0 | 0 | 0 | 0 | 200 | 74800 | 200 | 610012.8969 | 510.81 | 122.8353
6519 | 9 | 0 | 0.95651 | 1 | 317.141 | 0 | 0 | 0 | 0 | 0 | 200 | 74800 | 200 | 610212.8969 | 510.81 | 117.141
6520 | 9 | 0 | 0.7352 | 0.91604 | 249.7917 | 0 | 0 | 0 | 0 | 0 | 200 | 74800 | 200 | 610412.8969 | 510.81 | 49.7917
6521 | 9 | 0 | 0.47082 | 1 | 176.8717 | 0 | 0 | 0 | 0 | 0 | 176.8717 | 74800 | 176.8717 | 610589.7685 | 510.81 | 0
6522 | 9 | 0 | 0.20641 | 1 | 100.5115 | 0 | 0 | 0 | 0 | 0 | 100.5115 | 74800 | 100.5115 | 610690.28 | 510.81 | 0
6523 | 9 | 0 | 0.008254 | 0.90599 | 39.4387 | 0 | 0 | 0 | 0 | 0 | 39.4387 | 74800 | 39.4387 | 610729.7187 | 510.81 | 0
6524 | 9 | 1 | 0 | 0.54236 | 22.1824 | 200 | 22.1824 | 177.8176 | 200 | 0 | 0 | 74600 | 200 | 610929.7187 | 332.9924 | 0
6525 | 9 | 1 | 0 | 0.51101 | 20.9003 | 200 | 20.9003 | 179.0997 | 200 | 0 | 0 | 74400 | 200 | 611129.7187 | 153.8928 | 0
6526 | 9 | 0 | 0 | 0.45228 | 18.4985 | 0 | 0 | 0 | 0 | 18.4985 | 0 | 74400 | 0 | 611129.7187 | 169.9273 | 0
6527 | 9 | 0 | 0 | 0.29354 | 12.0058 | 0 | 0 | 0 | 0 | 12.0058 | 0 | 74400 | 0 | 611129.7187 | 180.3339 | 0
6528 | 9 | 0 | 0 | 0.5379 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 74400 | 0 | 611129.7187 | 199.4035 | 0
6529 | 9 | 0 | 0 | 0.46895 | 19.1802 | 0 | 0 | 0 | 0 | 19.1802 | 0 | 74400 | 0 | 611129.7187 | 216.0289 | 0
6530 | 9 | 0 | 0 | 0.36242 | 14.823 | 0 | 0 | 0 | 0 | 14.823 | 0 | 74400 | 0 | 611129.7187 | 228.8775 | 0
6531 | 9 | 0 | 0 | 0.64888 | 26.539 | 0 | 0 | 0 | 0 | 26.539 | 0 | 74400 | 0 | 611129.7187 | 251.8815 | 0
6532 | 9 | 0 | 0 | 0.93835 | 38.3786 | 0 | 0 | 0 | 0 | 38.3786 | 0 | 74400 | 0 | 611129.7187 | 285.148 | 0
6533 | 9 | 0 | 0 | 0.99674 | 40.7666 | 0 | 0 | 0 | 0 | 40.7666 | 0 | 74400 | 0 | 611129.7187 | 320.4845 | 0
6534 | 9 | 0 | 0 | 0.85595 | 35.0084 | 0 | 0 | 0 | 0 | 35.0084 | 0 | 74400 | 0 | 611129.7187 | 350.8298 | 0
6535 | 9 | 0 | 0.008843 | 0.90396 | 39.5259 | 0 | 0 | 0 | 0 | 39.5259 | 0 | 74400 | 0 | 611129.7187 | 385.0908 | 0
6536 | 9 | 1 | 0.22114 | 0.79041 | 96.1918 | 200 | 96.1918 | 103.8082 | 200 | 0 | 0 | 74200 | 200 | 611329.7187 | 281.2827 | 0
6537 | 9 | 1 | 0.5044 | 0.34053 | 159.5996 | 200 | 159.5996 | 40.4004 | 200 | 0 | 0 | 74000 | 200 | 611529.7187 | 240.8823 | 0
6538 | 9 | 0 | 0.78765 | 0.42294 | 244.7707 | 0 | 0 | 0 | 0 | 180 | 64.7707 | 74000 | 64.7707 | 611594.4894 | 396.9063 | 0
6539 | 9 | 0 | 1 | 0.49434 | 309.0184 | 0 | 0 | 0 | 0 | 131.4072 | 177.6112 | 74000 | 177.6112 | 611772.1007 | 510.81 | 0
6540 | 9 | 0 | 1 | 0.36793 | 303.8482 | 0 | 0 | 0 | 0 | 0 | 200 | 74000 | 200 | 611972.1007 | 510.81 | 103.8482
6541 | 9 | 0 | 1 | 0.4139 | 305.7285 | 0 | 0 | 0 | 0 | 0 | 200 | 74000 | 200 | 612172.1007 | 510.81 | 105.7285
6542 | 9 | 0 | 1 | 0.32437 | 302.0669 | 0 | 0 | 0 | 0 | 0 | 200 | 74000 | 200 | 612372.1007 | 510.81 | 102.0669
6543 | 9 | 0 | 1 | 0.3422 | 302.796 | 0 | 0 | 0 | 0 | 0 | 200 | 74000 | 200 | 612572.1007 | 510.81 | 102.796
6544 | 9 | 0 | 0.78765 | 0.24339 | 237.4271 | 0 | 0 | 0 | 0 | 0 | 200 | 74000 | 200 | 612772.1007 | 510.81 | 37.4271
6545 | 9 | 0 | 0.5044 | 0.30136 | 157.9974 | 0 | 0 | 0 | 0 | 0 | 157.9974 | 74000 | 157.9974 | 612930.098 | 510.81 | 0
6546 | 9 | 0 | 0.22114 | 0.33075 | 77.3918 | 0 | 0 | 0 | 0 | 0 | 77.3918 | 74000 | 77.3918 | 613007.4899 | 510.81 | 0
6547 | 9 | 0 | 0.008843 | 0.26236 | 13.2844 | 0 | 0 | 0 | 0 | 0 | 13.2844 | 74000 | 13.2844 | 613020.7743 | 510.81 | 0
6548 | 9 | 1 | 0 | 0.15461 | 6.3235 | 200 | 6.3235 | 180 | 186.3235 | 0 | 0 | 73800 | 186.3235 | 613207.0978 | 330.81 | 0
6549 | 9 | 1 | 0 | 0.12673 | 5.1831 | 200 | 5.1831 | 180 | 185.1831 | 0 | 0 | 73600 | 185.1831 | 613392.2808 | 150.81 | 0
6550 | 9 | 0 | 0 | 0.1518 | 6.2088 | 0 | 0 | 0 | 0 | 6.2088 | 0 | 73600 | 0 | 613392.2808 | 156.1918 | 0
6551 | 9 | 0 | 0 | 0.16464 | 6.7337 | 0 | 0 | 0 | 0 | 6.7337 | 0 | 73600 | 0 | 613392.2808 | 162.0285 | 0
6552 | 9 | 0 | 0 | 0.15266 | 6.2439 | 0 | 0 | 0 | 0 | 6.2439 | 0 | 73600 | 0 | 613392.2808 | 167.4407 | 0
6553 | 10 | 0 | 0 | 0.13247 | 5.418 | 0 | 0 | 0 | 0 | 5.418 | 0 | 73600 | 0 | 613392.2808 | 172.1371 | 0
6554 | 10 | 0 | 0 | 0.20644 | 8.4432 | 0 | 0 | 0 | 0 | 8.4432 | 0 | 73600 | 0 | 613392.2808 | 179.4557 | 0
6555 | 10 | 0 | 0 | 0.23099 | 9.4475 | 0 | 0 | 0 | 0 | 9.4475 | 0 | 73600 | 0 | 613392.2808 | 187.6448 | 0
6556 | 10 | 0 | 0 | 0.12597 | 5.1522 | 0 | 0 | 0 | 0 | 5.1522 | 0 | 73600 | 0 | 613392.2808 | 192.1107 | 0
6557 | 10 | 0 | 0 | 0.18346 | 7.5036 | 0 | 0 | 0 | 0 | 7.5036 | 0 | 73600 | 0 | 613392.2808 | 198.6149 | 0
6558 | 10 | 0 | 0 | 0.16324 | 6.6766 | 0 | 0 | 0 | 0 | 6.6766 | 0 | 73600 | 0 | 613392.2808 | 204.4022 | 0
6559 | 10 | 0 | 0 | 0.15581 | 6.3725 | 0 | 0 | 0 | 0 | 6.3725 | 0 | 73600 | 0 | 613392.2808 | 209.9258 | 0
6560 | 10 | 1 | 0.15191 | 0.22319 | 52.9996 | 200 | 52.9996 | 147.0004 | 200 | 0 | 0 | 73400 | 200 | 613592.2808 | 62.9255 | 0
6561 | 10 | 1 | 0.45704 | 0.2678 | 142.9457 | 200 | 142.9457 | 57.0543 | 200 | 0 | 0 | 73200 | 200 | 613792.2808 | 5.8712 | 0
6562 | 10 | 0 | 0.77845 | 0.19641 | 232.8494 | 0 | 0 | 0 | 0 | 180 | 52.8494 | 73200 | 52.8494 | 613845.1302 | 161.8952 | 0
6563 | 10 | 0 | 1 | 0.28676 | 300.5286 | 0 | 0 | 0 | 0 | 180 | 120.5286 | 73200 | 120.5286 | 613965.6588 | 317.9192 | 0
6564 | 10 | 0 | 1 | 0.27892 | 300.208 | 0 | 0 | 0 | 0 | 180 | 120.208 | 73200 | 120.208 | 614085.8668 | 473.9432 | 0
6565 | 10 | 0 | 1 | 0.42723 | 306.2735 | 0 | 0 | 0 | 0 | 42.5321 | 200 | 73200 | 200 | 614285.8668 | 510.81 | 63.7414
6566 | 10 | 0 | 1 | 0.52042 | 310.085 | 0 | 0 | 0 | 0 | 0 | 200 | 73200 | 200 | 614485.8668 | 510.81 | 110.085
6567 | 10 | 0 | 1 | 0.43171 | 306.4571 | 0 | 0 | 0 | 0 | 0 | 200 | 73200 | 200 | 614685.8668 | 510.81 | 106.4571
6568 | 10 | 0 | 0.77845 | 0.38563 | 240.5888 | 0 | 0 | 0 | 0 | 0 | 200 | 73200 | 200 | 614885.8668 | 510.81 | 40.5888
6569 | 10 | 0 | 0.45704 | 0.29459 | 144.0415 | 0 | 0 | 0 | 0 | 0 | 144.0415 | 73200 | 144.0415 | 615029.9083 | 510.81 | 0
6570 | 10 | 0 | 0.15191 | 0.33495 | 57.5706 | 0 | 0 | 0 | 0 | 0 | 57.5706 | 73200 | 57.5706 | 615087.4789 | 510.81 | 0
6571 | 10 | 0 | 0 | 0.42642 | 17.4408 | 0 | 0 | 0 | 0 | 0 | 17.4408 | 73200 | 17.4408 | 615104.9197 | 510.81 | 0
6572 | 10 | 1 | 0 | 0.39708 | 16.2407 | 200 | 16.2407 | 180 | 196.2407 | 0 | 0 | 73000 | 196.2407 | 615301.1603 | 330.81 | 0
6573 | 10 | 1 | 0 | 0.21898 | 8.9564 | 200 | 8.9564 | 180 | 188.9564 | 0 | 0 | 72800 | 188.9564 | 615490.1168 | 150.81 | 0
6574 | 10 | 0 | 0 | 0.12127 | 4.9601 | 0 | 0 | 0 | 0 | 4.9601 | 0 | 72800 | 0 | 615490.1168 | 155.1094 | 0
6575 | 10 | 0 | 0 | 0.1188 | 4.8588 | 0 | 0 | 0 | 0 | 4.8588 | 0 | 72800 | 0 | 615490.1168 | 159.321 | 0
6576 | 10 | 0 | 0 | 0.15935 | 6.5176 | 0 | 0 | 0 | 0 | 6.5176 | 0 | 72800 | 0 | 615490.1168 | 164.9705 | 0
6577 | 10 | 0 | 0 | 0.13724 | 5.6133 | 0 | 0 | 0 | 0 | 5.6133 | 0 | 72800 | 0 | 615490.1168 | 169.8361 | 0
6578 | 10 | 0 | 0 | 0.14294 | 5.8462 | 0 | 0 | 0 | 0 | 5.8462 | 0 | 72800 | 0 | 615490.1168 | 174.9036 | 0
6579 | 10 | 0 | 0 | 0.12075 | 4.9388 | 0 | 0 | 0 | 0 | 4.9388 | 0 | 72800 | 0 | 615490.1168 | 179.1846 | 0
6580 | 10 | 0 | 0 | 0.080861 | 3.3072 | 0 | 0 | 0 | 0 | 3.3072 | 0 | 72800 | 0 | 615490.1168 | 182.0513 | 0
6581 | 10 | 0 | 0 | 0.054493 | 2.2288 | 0 | 0 | 0 | 0 | 2.2288 | 0 | 72800 | 0 | 615490.1168 | 183.9832 | 0
6582 | 10 | 0 | 0 | 0.069149 | 2.8282 | 0 | 0 | 0 | 0 | 2.8282 | 0 | 72800 | 0 | 615490.1168 | 186.4346 | 0
6583 | 10 | 0 | 0 | 0.075702 | 3.0962 | 0 | 0 | 0 | 0 | 3.0962 | 0 | 72800 | 0 | 615490.1168 | 189.1184 | 0
6584 | 10 | 1 | 0.16847 | 0.10209 | 52.8307 | 200 | 52.8307 | 147.1693 | 200 | 0 | 0 | 72600 | 200 | 615690.1168 | 41.9491 | 0
6585 | 10 | 1 | 0.50688 | 0.10058 | 150.4996 | 200 | 150.4996 | 41.9491 | 192.4488 | 0 | 0 | 72400 | 192.4488 | 615882.5655 | 0 | 0
6586 | 10 | 0 | 0.86334 | 0.17499 | 256.4891 | 0 | 0 | 0 | 0 | 180 | 76.4891 | 72400 | 76.4891 | 615959.0546 | 156.024 | 0
6587 | 10 | 0 | 1 | 0.25574 | 299.2599 | 0 | 0 | 0 | 0 | 180 | 119.2599 | 72400 | 119.2599 | 616078.3145 | 312.048 | 0
6588 | 10 | 0 | 1 | 0.46269 | 307.7241 | 0 | 0 | 0 | 0 | 180 | 127.7241 | 72400 | 127.7241 | 616206.0386 | 468.072 | 0
6589 | 10 | 0 | 1 | 0.65757 | 315.6947 | 0 | 0 | 0 | 0 | 49.3055 | 200 | 72400 | 200 | 616406.0386 | 510.81 | 66.3892
6590 | 10 | 0 | 1 | 0.45064 | 307.2311 | 0 | 0 | 0 | 0 | 0 | 200 | 72400 | 200 | 616606.0386 | 510.81 | 107.2311
6591 | 10 | 0 | 1 | 0.82784 | 322.6588 | 0 | 0 | 0 | 0 | 0 | 200 | 72400 | 200 | 616806.0386 | 510.81 | 122.6588
6592 | 10 | 0 | 0.86334 | 0.64687 | 275.789 | 0 | 0 | 0 | 0 | 0 | 200 | 72400 | 200 | 617006.0386 | 510.81 | 75.789
6593 | 10 | 0 | 0.50688 | 0.48328 | 166.1521 | 0 | 0 | 0 | 0 | 0 | 166.1521 | 72400 | 166.1521 | 617172.1907 | 510.81 | 0
6594 | 10 | 0 | 0.16847 | 0.6416 | 74.8966 | 0 | 0 | 0 | 0 | 0 | 74.8966 | 72400 | 74.8966 | 617247.0873 | 510.81 | 0
6595 | 10 | 0 | 0 | 0.55063 | 22.5206 | 0 | 0 | 0 | 0 | 0 | 22.5206 | 72400 | 22.5206 | 617269.6078 | 510.81 | 0
6596 | 10 | 1 | 0 | 0.57767 | 23.6268 | 200 | 23.6268 | 176.3732 | 200 | 0 | 0 | 72200 | 200 | 617469.6078 | 334.4368 | 0
6597 | 10 | 1 | 0 | 0.52144 | 21.3269 | 200 | 21.3269 | 178.6731 | 200 | 0 | 0 | 72000 | 200 | 617669.6078 | 155.7637 | 0
6598 | 10 | 0 | 0 | 0.63226 | 25.8593 | 0 | 0 | 0 | 0 | 25.8593 | 0 | 72000 | 0 | 617669.6078 | 178.1785 | 0
6599 | 10 | 0 | 0 | 0.59116 | 24.1783 | 0 | 0 | 0 | 0 | 24.1783 | 0 | 72000 | 0 | 617669.6078 | 199.1363 | 0
6600 | 10 | 0 | 0 | 0.3908 | 15.9836 | 0 | 0 | 0 | 0 | 15.9836 | 0 | 72000 | 0 | 617669.6078 | 212.9909 | 0
6601 | 10 | 0 | 0 | 0.22381 | 9.154 | 0 | 0 | 0 | 0 | 9.154 | 0 | 72000 | 0 | 617669.6078 | 220.9255 | 0
6602 | 10 | 0 | 0 | 0.18754 | 7.6703 | 0 | 0 | 0 | 0 | 7.6703 | 0 | 72000 | 0 | 617669.6078 | 227.5741 | 0
6603 | 10 | 0 | 0 | 0.16302 | 6.6675 | 0 | 0 | 0 | 0 | 6.6675 | 0 | 72000 | 0 | 617669.6078 | 233.3535 | 0
6604 | 10 | 0 | 0 | 0.25849 | 10.5723 | 0 | 0 | 0 | 0 | 10.5723 | 0 | 72000 | 0 | 617669.6078 | 242.5176 | 0
6605 | 10 | 0 | 0 | 0.27689 | 11.325 | 0 | 0 | 0 | 0 | 11.325 | 0 | 72000 | 0 | 617669.6078 | 252.3341 | 0
6606 | 10 | 0 | 0 | 0.27048 | 11.0626 | 0 | 0 | 0 | 0 | 11.0626 | 0 | 72000 | 0 | 617669.6078 | 261.9231 | 0
6607 | 10 | 0 | 0 | 0.39728 | 16.2486 | 0 | 0 | 0 | 0 | 16.2486 | 0 | 72000 | 0 | 617669.6078 | 276.0074 | 0
6608 | 10 | 1 | 0.15775 | 0.37431 | 60.8674 | 200 | 60.8674 | 139.1326 | 200 | 0 | 0 | 71800 | 200 | 617869.6078 | 136.8749 | 0
6609 | 10 | 1 | 0.47461 | 0.2583 | 147.6325 | 200 | 147.6325 | 52.3675 | 200 | 0 | 0 | 71600 | 200 | 618069.6078 | 84.5074 | 0
6610 | 10 | 0 | 0.80838 | 0.28536 | 245.1322 | 0 | 0 | 0 | 0 | 180 | 65.1322 | 71600 | 65.1322 | 618134.74 | 240.5314 | 0
6611 | 10 | 0 | 1 | 0.21413 | 297.5578 | 0 | 0 | 0 | 0 | 180 | 117.5578 | 71600 | 117.5578 | 618252.2978 | 396.5554 | 0
6612 | 10 | 0 | 1 | 0.34146 | 302.7657 | 0 | 0 | 0 | 0 | 131.812 | 170.9538 | 71600 | 170.9538 | 618423.2515 | 510.81 | 0
6613 | 10 | 0 | 1 | 0.43397 | 306.5494 | 0 | 0 | 0 | 0 | 0 | 200 | 71600 | 200 | 618623.2515 | 510.81 | 106.5494
6614 | 10 | 0 | 1 | 0.36883 | 303.885 | 0 | 0 | 0 | 0 | 0 | 200 | 71600 | 200 | 618823.2515 | 510.81 | 103.885
6615 | 10 | 0 | 1 | 0.28742 | 300.5556 | 0 | 0 | 0 | 0 | 0 | 200 | 71600 | 200 | 619023.2515 | 510.81 | 100.5556
6616 | 10 | 0 | 0.80838 | 0.31099 | 246.1803 | 0 | 0 | 0 | 0 | 0 | 200 | 71600 | 200 | 619223.2515 | 510.81 | 46.1803
6617 | 10 | 0 | 0.47461 | 0.35482 | 151.5799 | 0 | 0 | 0 | 0 | 0 | 151.5799 | 71600 | 151.5799 | 619374.8314 | 510.81 | 0
6618 | 10 | 0 | 0.15775 | 0.27695 | 56.8856 | 0 | 0 | 0 | 0 | 0 | 56.8856 | 71600 | 56.8856 | 619431.7171 | 510.81 | 0
6619 | 10 | 0 | 0 | 0.19347 | 7.9129 | 0 | 0 | 0 | 0 | 0 | 7.9129 | 71600 | 7.9129 | 619439.63 | 510.81 | 0
6620 | 10 | 1 | 0 | 0.14127 | 5.7779 | 200 | 5.7779 | 180 | 185.7779 | 0 | 0 | 71400 | 185.7779 | 619625.4079 | 330.81 | 0
6621 | 10 | 1 | 0 | 0.22447 | 9.1807 | 200 | 9.1807 | 180 | 189.1807 | 0 | 0 | 71200 | 189.1807 | 619814.5887 | 150.81 | 0
6622 | 10 | 0 | 0 | 0.3045 | 12.4542 | 0 | 0 | 0 | 0 | 12.4542 | 0 | 71200 | 0 | 619814.5887 | 161.6053 | 0
6623 | 10 | 0 | 0 | 0.32293 | 13.2078 | 0 | 0 | 0 | 0 | 13.2078 | 0 | 71200 | 0 | 619814.5887 | 173.0538 | 0
6624 | 10 | 0 | 0 | 0.38927 | 15.9213 | 0 | 0 | 0 | 0 | 15.9213 | 0 | 71200 | 0 | 619814.5887 | 186.8543 | 0
6625 | 10 | 0 | 0 | 0.39318 | 16.0811 | 0 | 0 | 0 | 0 | 16.0811 | 0 | 71200 | 0 | 619814.5887 | 200.7935 | 0
6626 | 10 | 0 | 0 | 0.27339 | 11.1815 | 0 | 0 | 0 | 0 | 11.1815 | 0 | 71200 | 0 | 619814.5887 | 210.4856 | 0
6627 | 10 | 0 | 0 | 0.33514 | 13.7074 | 0 | 0 | 0 | 0 | 13.7074 | 0 | 71200 | 0 | 619814.5887 | 222.3672 | 0
6628 | 10 | 0 | 0 | 0.28216 | 11.5405 | 0 | 0 | 0 | 0 | 11.5405 | 0 | 71200 | 0 | 619814.5887 | 232.3705 | 0
6629 | 10 | 0 | 0 | 0.20743 | 8.484 | 0 | 0 | 0 | 0 | 8.484 | 0 | 71200 | 0 | 619814.5887 | 239.7244 | 0
6630 | 10 | 0 | 0 | 0.17439 | 7.1325 | 0 | 0 | 0 | 0 | 7.1325 | 0 | 71200 | 0 | 619814.5887 | 245.9069 | 0
6631 | 10 | 0 | 0 | 0.18056 | 7.3848 | 0 | 0 | 0 | 0 | 7.3848 | 0 | 71200 | 0 | 619814.5887 | 252.308 | 0
6632 | 10 | 1 | 0.1608 | 0.16956 | 53.3728 | 200 | 53.3728 | 146.6272 | 200 | 0 | 0 | 71000 | 200 | 620014.5887 | 105.6808 | 0
6633 | 10 | 1 | 0.48378 | 0.17958 | 147.0602 | 200 | 147.0602 | 52.9398 | 200 | 0 | 0 | 70800 | 200 | 620214.5887 | 52.741 | 0
6634 | 10 | 0 | 0.824 | 0.2011 | 246.1952 | 0 | 0 | 0 | 0 | 180 | 66.1952 | 70800 | 66.1952 | 620280.7839 | 208.765 | 0
6635 | 10 | 0 | 1 | 0.12405 | 293.8735 | 0 | 0 | 0 | 0 | 180 | 113.8735 | 70800 | 113.8735 | 620394.6574 | 364.789 | 0
6636 | 10 | 0 | 1 | 0.10172 | 292.9605 | 0 | 0 | 0 | 0 | 168.4598 | 124.5007 | 70800 | 124.5007 | 620519.1581 | 510.81 | 0
6637 | 10 | 0 | 1 | 0.13977 | 294.5166 | 0 | 0 | 0 | 0 | 0 | 200 | 70800 | 200 | 620719.1581 | 510.81 | 94.5166
6638 | 10 | 0 | 1 | 0.22336 | 297.9353 | 0 | 0 | 0 | 0 | 0 | 200 | 70800 | 200 | 620919.1581 | 510.81 | 97.9353
6639 | 10 | 0 | 1 | 0.19548 | 296.7951 | 0 | 0 | 0 | 0 | 0 | 200 | 70800 | 200 | 621119.1581 | 510.81 | 96.7951
6640 | 10 | 0 | 0.824 | 0.31652 | 250.916 | 0 | 0 | 0 | 0 | 0 | 200 | 70800 | 200 | 621319.1581 | 510.81 | 50.916
6641 | 10 | 0 | 0.48378 | 0.29814 | 151.9094 | 0 | 0 | 0 | 0 | 0 | 151.9094 | 70800 | 151.9094 | 621471.0675 | 510.81 | 0
6642 | 10 | 0 | 0.1608 | 0.30345 | 58.8488 | 0 | 0 | 0 | 0 | 0 | 58.8488 | 70800 | 58.8488 | 621529.9163 | 510.81 | 0
6643 | 10 | 0 | 0 | 0.34571 | 14.1397 | 0 | 0 | 0 | 0 | 0 | 14.1397 | 70800 | 14.1397 | 621544.056 | 510.81 | 0
6644 | 10 | 1 | 0 | 0.33445 | 13.6791 | 200 | 13.6791 | 180 | 193.6791 | 0 | 0 | 70600 | 193.6791 | 621737.7351 | 330.81 | 0
6645 | 10 | 1 | 0 | 0.43259 | 17.6928 | 200 | 17.6928 | 180 | 197.6928 | 0 | 0 | 70400 | 197.6928 | 621935.4279 | 150.81 | 0
6646 | 10 | 0 | 0 | 0.3807 | 15.5708 | 0 | 0 | 0 | 0 | 15.5708 | 0 | 70400 | 0 | 621935.4279 | 164.3067 | 0
6647 | 10 | 0 | 0 | 0.4956 | 20.2698 | 0 | 0 | 0 | 0 | 20.2698 | 0 | 70400 | 0 | 621935.4279 | 181.8766 | 0
6648 | 10 | 0 | 0 | 0.59461 | 24.3193 | 0 | 0 | 0 | 0 | 24.3193 | 0 | 70400 | 0 | 621935.4279 | 202.9566 | 0
6649 | 10 | 0 | 0 | 0.81175 | 33.2007 | 0 | 0 | 0 | 0 | 33.2007 | 0 | 70400 | 0 | 621935.4279 | 231.735 | 0
6650 | 10 | 0 | 0 | 0.73641 | 30.119 | 0 | 0 | 0 | 0 | 30.119 | 0 | 70400 | 0 | 621935.4279 | 257.8422 | 0
6651 | 10 | 0 | 0 | 0.84066 | 34.3832 | 0 | 0 | 0 | 0 | 34.3832 | 0 | 70400 | 0 | 621935.4279 | 287.6455 | 0
6652 | 10 | 0 | 0 | 0.78885 | 32.264 | 0 | 0 | 0 | 0 | 32.264 | 0 | 70400 | 0 | 621935.4279 | 315.612 | 0
6653 | 10 | 0 | 0 | 0.39011 | 15.9555 | 0 | 0 | 0 | 0 | 15.9555 | 0 | 70400 | 0 | 621935.4279 | 329.4422 | 0
6654 | 10 | 0 | 0 | 0.32981 | 13.4891 | 0 | 0 | 0 | 0 | 13.4891 | 0 | 70400 | 0 | 621935.4279 | 341.1346 | 0
6655 | 10 | 0 | 0 | 0.30688 | 12.5514 | 0 | 0 | 0 | 0 | 12.5514 | 0 | 70400 | 0 | 621935.4279 | 352.0141 | 0
6656 | 10 | 1 | 0.13567 | 0.45062 | 57.6123 | 200 | 57.6123 | 142.3877 | 200 | 0 | 0 | 70200 | 200 | 622135.4279 | 209.6263 | 0
6657 | 10 | 1 | 0.40819 | 0.5184 | 139.0871 | 200 | 139.0871 | 60.9129 | 200 | 0 | 0 | 70000 | 200 | 622335.4279 | 148.7134 | 0
6658 | 10 | 0 | 0.69524 | 0.43287 | 218.491 | 0 | 0 | 0 | 0 | 180 | 38.491 | 70000 | 38.491 | 622373.9189 | 304.7374 | 0
6659 | 10 | 0 | 0.94147 | 0.41426 | 288.8411 | 0 | 0 | 0 | 0 | 180 | 108.8411 | 70000 | 108.8411 | 622482.76 | 460.7614 | 0
6660 | 10 | 0 | 1 | 0.54789 | 311.2086 | 0 | 0 | 0 | 0 | 57.7395 | 200 | 70000 | 200 | 622682.76 | 510.81 | 53.4692
6661 | 10 | 0 | 1 | 0.63522 | 314.7804 | 0 | 0 | 0 | 0 | 0 | 200 | 70000 | 200 | 622882.76 | 510.81 | 114.7804
6662 | 10 | 0 | 1 | 0.37311 | 304.0603 | 0 | 0 | 0 | 0 | 0 | 200 | 70000 | 200 | 623082.76 | 510.81 | 104.0603
6663 | 10 | 0 | 0.94147 | 0.46808 | 291.0425 | 0 | 0 | 0 | 0 | 0 | 200 | 70000 | 200 | 623282.76 | 510.81 | 91.0425
6664 | 10 | 0 | 0.69524 | 0.48601 | 220.6645 | 0 | 0 | 0 | 0 | 0 | 200 | 70000 | 200 | 623482.76 | 510.81 | 20.6645
6665 | 10 | 0 | 0.40819 | 0.33057 | 131.4048 | 0 | 0 | 0 | 0 | 0 | 131.4048 | 70000 | 131.4048 | 623614.1648 | 510.81 | 0
6666 | 10 | 0 | 0.13567 | 0.38968 | 55.1195 | 0 | 0 | 0 | 0 | 0 | 55.1195 | 70000 | 55.1195 | 623669.2844 | 510.81 | 0
6667 | 10 | 0 | 0 | 0.44589 | 18.2367 | 0 | 0 | 0 | 0 | 0 | 18.2367 | 70000 | 18.2367 | 623687.5211 | 510.81 | 0
6668 | 10 | 1 | 0 | 0.34328 | 14.0403 | 200 | 14.0403 | 180 | 194.0403 | 0 | 0 | 69800 | 194.0403 | 623881.5614 | 330.81 | 0
6669 | 10 | 1 | 0 | 0.48287 | 19.7495 | 200 | 19.7495 | 180 | 199.7495 | 0 | 0 | 69600 | 199.7495 | 624081.3109 | 150.81 | 0
6670 | 10 | 0 | 0 | 0.39802 | 16.2791 | 0 | 0 | 0 | 0 | 16.2791 | 0 | 69600 | 0 | 624081.3109 | 164.9207 | 0
6671 | 10 | 0 | 0 | 0.24757 | 10.1257 | 0 | 0 | 0 | 0 | 10.1257 | 0 | 69600 | 0 | 624081.3109 | 173.6976 | 0
6672 | 10 | 0 | 0 | 0.24145 | 9.8752 | 0 | 0 | 0 | 0 | 9.8752 | 0 | 69600 | 0 | 624081.3109 | 182.2574 | 0
6673 | 10 | 0 | 0 | 0.28078 | 11.4841 | 0 | 0 | 0 | 0 | 11.4841 | 0 | 69600 | 0 | 624081.3109 | 192.2118 | 0
6674 | 10 | 0 | 0 | 0.37899 | 15.5007 | 0 | 0 | 0 | 0 | 15.5007 | 0 | 69600 | 0 | 624081.3109 | 205.6478 | 0
6675 | 10 | 0 | 0 | 0.38888 | 15.9054 | 0 | 0 | 0 | 0 | 15.9054 | 0 | 69600 | 0 | 624081.3109 | 219.4346 | 0
6676 | 10 | 0 | 0 | 0.40204 | 16.4436 | 0 | 0 | 0 | 0 | 16.4436 | 0 | 69600 | 0 | 624081.3109 | 233.6879 | 0
6677 | 10 | 0 | 0 | 0.34128 | 13.9585 | 0 | 0 | 0 | 0 | 13.9585 | 0 | 69600 | 0 | 624081.3109 | 245.7871 | 0
6678 | 10 | 0 | 0 | 0.25562 | 10.4549 | 0 | 0 | 0 | 0 | 10.4549 | 0 | 69600 | 0 | 624081.3109 | 254.8494 | 0
6679 | 10 | 0 | 0 | 0.23829 | 9.7462 | 0 | 0 | 0 | 0 | 9.7462 | 0 | 69600 | 0 | 624081.3109 | 263.2974 | 0
6680 | 10 | 1 | 0.14788 | 0.23635 | 52.3739 | 200 | 52.3739 | 147.6261 | 200 | 0 | 0 | 69400 | 200 | 624281.3109 | 115.6713 | 0
6681 | 10 | 1 | 0.44491 | 0.4895 | 148.5107 | 200 | 148.5107 | 51.4893 | 200 | 0 | 0 | 69200 | 200 | 624481.3109 | 64.1821 | 0
6682 | 10 | 0 | 0.75779 | 0.6192 | 244.1765 | 0 | 0 | 0 | 0 | 180 | 64.1765 | 69200 | 64.1765 | 624545.4873 | 220.2061 | 0
6683 | 10 | 0 | 1 | 0.7379 | 318.9799 | 0 | 0 | 0 | 0 | 180 | 138.9799 | 69200 | 138.9799 | 624684.4673 | 376.2301 | 0
6684 | 10 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 155.2607 | 174.4393 | 69200 | 174.4393 | 624858.9066 | 510.81 | 0
6685 | 10 | 0 | 1 | 0.61268 | 313.8588 | 0 | 0 | 0 | 0 | 0 | 200 | 69200 | 200 | 625058.9066 | 510.81 | 113.8588
6686 | 10 | 0 | 1 | 0.79485 | 321.3095 | 0 | 0 | 0 | 0 | 0 | 200 | 69200 | 200 | 625258.9066 | 510.81 | 121.3095
6687 | 10 | 0 | 1 | 0.47081 | 308.0563 | 0 | 0 | 0 | 0 | 0 | 200 | 69200 | 200 | 625458.9066 | 510.81 | 108.0563
6688 | 10 | 0 | 0.75779 | 0.60126 | 243.4428 | 0 | 0 | 0 | 0 | 0 | 200 | 69200 | 200 | 625658.9066 | 510.81 | 43.4428
6689 | 10 | 0 | 0.44491 | 0.62964 | 154.2424 | 0 | 0 | 0 | 0 | 0 | 154.2424 | 69200 | 154.2424 | 625813.149 | 510.81 | 0
6690 | 10 | 0 | 0.14788 | 0.52952 | 64.3645 | 0 | 0 | 0 | 0 | 0 | 64.3645 | 69200 | 64.3645 | 625877.5136 | 510.81 | 0
6691 | 10 | 0 | 0 | 0.43977 | 17.9867 | 0 | 0 | 0 | 0 | 0 | 17.9867 | 69200 | 17.9867 | 625895.5003 | 510.81 | 0
6692 | 10 | 1 | 0 | 0.47308 | 19.3488 | 200 | 19.3488 | 180 | 199.3488 | 0 | 0 | 69000 | 199.3488 | 626094.8491 | 330.81 | 0
6693 | 10 | 1 | 0 | 0.42393 | 17.3388 | 200 | 17.3388 | 180 | 197.3388 | 0 | 0 | 68800 | 197.3388 | 626292.1879 | 150.81 | 0
6694 | 10 | 0 | 0 | 0.35617 | 14.5673 | 0 | 0 | 0 | 0 | 14.5673 | 0 | 68800 | 0 | 626292.1879 | 163.4369 | 0
6695 | 10 | 0 | 0 | 0.30624 | 12.5253 | 0 | 0 | 0 | 0 | 12.5253 | 0 | 68800 | 0 | 626292.1879 | 174.2938 | 0
6696 | 10 | 0 | 0 | 0.35165 | 14.3826 | 0 | 0 | 0 | 0 | 14.3826 | 0 | 68800 | 0 | 626292.1879 | 186.7607 | 0
6697 | 10 | 0 | 0 | 0.264 | 10.7978 | 0 | 0 | 0 | 0 | 10.7978 | 0 | 68800 | 0 | 626292.1879 | 196.1202 | 0
6698 | 10 | 0 | 0 | 0.18024 | 7.3719 | 0 | 0 | 0 | 0 | 7.3719 | 0 | 68800 | 0 | 626292.1879 | 202.5102 | 0
6699 | 10 | 0 | 0 | 0.18618 | 7.6148 | 0 | 0 | 0 | 0 | 7.6148 | 0 | 68800 | 0 | 626292.1879 | 209.1107 | 0
6700 | 10 | 0 | 0 | 0.20679 | 8.4576 | 0 | 0 | 0 | 0 | 8.4576 | 0 | 68800 | 0 | 626292.1879 | 216.4417 | 0
6701 | 10 | 0 | 0 | 0.16459 | 6.7319 | 0 | 0 | 0 | 0 | 6.7319 | 0 | 68800 | 0 | 626292.1879 | 222.277 | 0
6702 | 10 | 0 | 0 | 0.16389 | 6.7033 | 0 | 0 | 0 | 0 | 6.7033 | 0 | 68800 | 0 | 626292.1879 | 228.0874 | 0
6703 | 10 | 0 | 0 | 0.13826 | 5.6548 | 0 | 0 | 0 | 0 | 5.6548 | 0 | 68800 | 0 | 626292.1879 | 232.9889 | 0
6704 | 10 | 1 | 0.15545 | 0.2152 | 53.696 | 200 | 53.696 | 146.304 | 200 | 0 | 0 | 68600 | 200 | 626492.1879 | 86.6849 | 0
6705 | 10 | 1 | 0.4677 | 0.22087 | 144.1041 | 200 | 144.1041 | 55.8959 | 200 | 0 | 0 | 68400 | 200 | 626692.1879 | 30.789 | 0
6706 | 10 | 0 | 0.7966 | 0.26664 | 240.9647 | 0 | 0 | 0 | 0 | 180 | 60.9647 | 68400 | 60.9647 | 626753.1526 | 186.813 | 0
6707 | 10 | 0 | 1 | 0.27995 | 300.2499 | 0 | 0 | 0 | 0 | 180 | 120.2499 | 68400 | 120.2499 | 626873.4024 | 342.837 | 0
6708 | 10 | 0 | 1 | 0.23672 | 298.4819 | 0 | 0 | 0 | 0 | 180 | 118.4819 | 68400 | 118.4819 | 626991.8844 | 498.861 | 0
6709 | 10 | 0 | 1 | 0.17739 | 296.0552 | 0 | 0 | 0 | 0 | 13.7852 | 200 | 68400 | 200 | 627191.8844 | 510.81 | 82.27
6710 | 10 | 0 | 1 | 0.15678 | 295.2124 | 0 | 0 | 0 | 0 | 0 | 200 | 68400 | 200 | 627391.8844 | 510.81 | 95.2124
6711 | 10 | 0 | 1 | 0.17348 | 295.8953 | 0 | 0 | 0 | 0 | 0 | 200 | 68400 | 200 | 627591.8844 | 510.81 | 95.8953
6712 | 10 | 0 | 0.7966 | 0.13376 | 235.5302 | 0 | 0 | 0 | 0 | 0 | 200 | 68400 | 200 | 627791.8844 | 510.81 | 35.5302
6713 | 10 | 0 | 0.4677 | 0.13524 | 140.6018 | 0 | 0 | 0 | 0 | 0 | 140.6018 | 68400 | 140.6018 | 627932.4861 | 510.81 | 0
6714 | 10 | 0 | 0.15545 | 0.096832 | 48.8547 | 0 | 0 | 0 | 0 | 0 | 48.8547 | 68400 | 48.8547 | 627981.3408 | 510.81 | 0
6715 | 10 | 0 | 0 | 0.0907 | 3.7096 | 0 | 0 | 0 | 0 | 0 | 3.7096 | 68400 | 3.7096 | 627985.0504 | 510.81 | 0
6716 | 10 | 1 | 0 | 0.16717 | 6.837 | 200 | 6.837 | 180 | 186.837 | 0 | 0 | 68200 | 186.837 | 628171.8875 | 330.81 | 0
6717 | 10 | 1 | 0 | 0.19108 | 7.8151 | 200 | 7.8151 | 180 | 187.8151 | 0 | 0 | 68000 | 187.8151 | 628359.7026 | 150.81 | 0
6718 | 10 | 0 | 0 | 0.31595 | 12.9222 | 0 | 0 | 0 | 0 | 12.9222 | 0 | 68000 | 0 | 628359.7026 | 162.011 | 0
6719 | 10 | 0 | 0 | 0.23925 | 9.7853 | 0 | 0 | 0 | 0 | 9.7853 | 0 | 68000 | 0 | 628359.7026 | 170.4928 | 0
6720 | 10 | 0 | 0 | 0.2944 | 12.0411 | 0 | 0 | 0 | 0 | 12.0411 | 0 | 68000 | 0 | 628359.7026 | 180.9301 | 0
6721 | 10 | 0 | 0 | 0.24284 | 9.9322 | 0 | 0 | 0 | 0 | 9.9322 | 0 | 68000 | 0 | 628359.7026 | 189.5393 | 0
6722 | 10 | 0 | 0 | 0.21272 | 8.7001 | 0 | 0 | 0 | 0 | 8.7001 | 0 | 68000 | 0 | 628359.7026 | 197.0805 | 0
6723 | 10 | 0 | 0 | 0.22147 | 9.0582 | 0 | 0 | 0 | 0 | 9.0582 | 0 | 68000 | 0 | 628359.7026 | 204.9322 | 0
6724 | 10 | 0 | 0 | 0.20135 | 8.2353 | 0 | 0 | 0 | 0 | 8.2353 | 0 | 68000 | 0 | 628359.7026 | 212.0706 | 0
6725 | 10 | 0 | 0 | 0.21466 | 8.7796 | 0 | 0 | 0 | 0 | 8.7796 | 0 | 68000 | 0 | 628359.7026 | 219.6807 | 0
6726 | 10 | 0 | 0 | 0.25856 | 10.5751 | 0 | 0 | 0 | 0 | 10.5751 | 0 | 68000 | 0 | 628359.7026 | 228.8472 | 0
6727 | 10 | 0 | 0 | 0.22642 | 9.2605 | 0 | 0 | 0 | 0 | 9.2605 | 0 | 68000 | 0 | 628359.7026 | 236.8742 | 0
6728 | 10 | 1 | 0.13768 | 0.27103 | 50.8477 | 200 | 50.8477 | 149.1523 | 200 | 0 | 0 | 67800 | 200 | 628559.7026 | 87.7219 | 0
6729 | 10 | 1 | 0.41424 | 0.26254 | 130.3691 | 200 | 130.3691 | 69.6309 | 200 | 0 | 0 | 67600 | 200 | 628759.7026 | 18.091 | 0
6730 | 10 | 0 | 0.70555 | 0.45509 | 222.3753 | 0 | 0 | 0 | 0 | 180 | 42.3753 | 67600 | 42.3753 | 628802.0779 | 174.115 | 0
6731 | 10 | 0 | 0.95543 | 0.56384 | 298.9883 | 0 | 0 | 0 | 0 | 180 | 118.9883 | 67600 | 118.9883 | 628921.0662 | 330.139 | 0
6732 | 10 | 0 | 1 | 0.60145 | 313.3992 | 0 | 0 | 0 | 0 | 180 | 133.3992 | 67600 | 133.3992 | 629054.4654 | 486.163 | 0
6733 | 10 | 0 | 1 | 0.44975 | 307.1948 | 0 | 0 | 0 | 0 | 28.4344 | 200 | 67600 | 200 | 629254.4654 | 510.81 | 78.7604
6734 | 10 | 0 | 1 | 0.57635 | 312.3729 | 0 | 0 | 0 | 0 | 0 | 200 | 67600 | 200 | 629454.4654 | 510.81 | 112.3729
6735 | 10 | 0 | 0.95543 | 0.45615 | 294.5837 | 0 | 0 | 0 | 0 | 0 | 200 | 67600 | 200 | 629654.4654 | 510.81 | 94.5837
6736 | 10 | 0 | 0.70555 | 0.37956 | 219.286 | 0 | 0 | 0 | 0 | 0 | 200 | 67600 | 200 | 629854.4654 | 510.81 | 19.286
6737 | 10 | 0 | 0.41424 | 0.35179 | 134.0197 | 0 | 0 | 0 | 0 | 0 | 134.0197 | 67600 | 134.0197 | 629988.4852 | 510.81 | 0
6738 | 10 | 0 | 0.13768 | 0.25308 | 50.1135 | 0 | 0 | 0 | 0 | 0 | 50.1135 | 67600 | 50.1135 | 630038.5987 | 510.81 | 0
6739 | 10 | 0 | 0 | 0.2365 | 9.6726 | 0 | 0 | 0 | 0 | 0 | 9.6726 | 67600 | 9.6726 | 630048.2713 | 510.81 | 0
6740 | 10 | 1 | 0 | 0.26516 | 10.845 | 200 | 10.845 | 180 | 190.845 | 0 | 0 | 67400 | 190.845 | 630239.1164 | 330.81 | 0
6741 | 10 | 1 | 0 | 0.16942 | 6.9292 | 200 | 6.9292 | 180 | 186.9292 | 0 | 0 | 67200 | 186.9292 | 630426.0455 | 150.81 | 0
6742 | 10 | 0 | 0 | 0.13788 | 5.6393 | 0 | 0 | 0 | 0 | 5.6393 | 0 | 67200 | 0 | 630426.0455 | 155.6982 | 0
6743 | 10 | 0 | 0 | 0.16873 | 6.9011 | 0 | 0 | 0 | 0 | 6.9011 | 0 | 67200 | 0 | 630426.0455 | 161.6801 | 0
6744 | 10 | 0 | 0 | 0.19738 | 8.0729 | 0 | 0 | 0 | 0 | 8.0729 | 0 | 67200 | 0 | 630426.0455 | 168.6777 | 0
6745 | 10 | 0 | 0 | 0.1731 | 7.0797 | 0 | 0 | 0 | 0 | 7.0797 | 0 | 67200 | 0 | 630426.0455 | 174.8143 | 0
6746 | 10 | 0 | 0 | 0.17471 | 7.1457 | 0 | 0 | 0 | 0 | 7.1457 | 0 | 67200 | 0 | 630426.0455 | 181.0082 | 0
6747 | 10 | 0 | 0 | 0.25836 | 10.567 | 0 | 0 | 0 | 0 | 10.567 | 0 | 67200 | 0 | 630426.0455 | 190.1677 | 0
6748 | 10 | 0 | 0 | 0.28063 | 11.4776 | 0 | 0 | 0 | 0 | 11.4776 | 0 | 67200 | 0 | 630426.0455 | 200.1165 | 0
6749 | 10 | 0 | 0 | 0.41164 | 16.836 | 0 | 0 | 0 | 0 | 16.836 | 0 | 67200 | 0 | 630426.0455 | 214.7099 | 0
6750 | 10 | 0 | 0 | 0.49718 | 20.3346 | 0 | 0 | 0 | 0 | 20.3346 | 0 | 67200 | 0 | 630426.0455 | 232.3359 | 0
6751 | 10 | 0 | 0 | 0.3596 | 14.7075 | 0 | 0 | 0 | 0 | 14.7075 | 0 | 67200 | 0 | 630426.0455 | 245.0844 | 0
6752 | 10 | 1 | 0.15188 | 0.34763 | 58.0822 | 200 | 58.0822 | 141.9178 | 200 | 0 | 0 | 67000 | 200 | 630626.0455 | 103.1667 | 0
6753 | 10 | 1 | 0.45696 | 0.45905 | 150.7463 | 200 | 150.7463 | 49.2537 | 200 | 0 | 0 | 66800 | 200 | 630826.0455 | 53.9129 | 0
6754 | 10 | 0 | 0.77832 | 0.38399 | 240.4848 | 0 | 0 | 0 | 0 | 180 | 60.4848 | 66800 | 60.4848 | 630886.5304 | 209.9369 | 0
6755 | 10 | 0 | 1 | 0.51812 | 309.9913 | 0 | 0 | 0 | 0 | 180 | 129.9913 | 66800 | 129.9913 | 631016.5217 | 365.9609 | 0
6756 | 10 | 0 | 1 | 0.5144 | 309.8391 | 0 | 0 | 0 | 0 | 167.1078 | 142.7313 | 66800 | 142.7313 | 631159.253 | 510.81 | 0
6757 | 10 | 0 | 1 | 0.42081 | 306.0113 | 0 | 0 | 0 | 0 | 0 | 200 | 66800 | 200 | 631359.253 | 510.81 | 106.0113
6758 | 10 | 0 | 1 | 0.49761 | 309.1524 | 0 | 0 | 0 | 0 | 0 | 200 | 66800 | 200 | 631559.253 | 510.81 | 109.1524
6759 | 10 | 0 | 1 | 0.47717 | 308.3162 | 0 | 0 | 0 | 0 | 0 | 200 | 66800 | 200 | 631759.253 | 510.81 | 108.3162
6760 | 10 | 0 | 0.77832 | 0.53273 | 246.5685 | 0 | 0 | 0 | 0 | 0 | 200 | 66800 | 200 | 631959.253 | 510.81 | 46.5685
6761 | 10 | 0 | 0.45696 | 0.34896 | 146.2435 | 0 | 0 | 0 | 0 | 0 | 146.2435 | 66800 | 146.2435 | 632105.4965 | 510.81 | 0
6762 | 10 | 0 | 0.15188 | 0.38022 | 59.4149 | 0 | 0 | 0 | 0 | 0 | 59.4149 | 66800 | 59.4149 | 632164.9114 | 510.81 | 0
6763 | 10 | 0 | 0 | 0.32347 | 13.23 | 0 | 0 | 0 | 0 | 0 | 13.23 | 66800 | 13.23 | 632178.1414 | 510.81 | 0
6764 | 10 | 1 | 0 | 0.39345 | 16.092 | 200 | 16.092 | 180 | 196.092 | 0 | 0 | 66600 | 196.092 | 632374.2334 | 330.81 | 0
6765 | 10 | 1 | 0 | 0.2843 | 11.6279 | 200 | 11.6279 | 180 | 191.6279 | 0 | 0 | 66400 | 191.6279 | 632565.8613 | 150.81 | 0
6766 | 10 | 0 | 0 | 0.1967 | 8.0451 | 0 | 0 | 0 | 0 | 8.0451 | 0 | 66400 | 0 | 632565.8613 | 157.7835 | 0
6767 | 10 | 0 | 0 | 0.13443 | 5.4983 | 0 | 0 | 0 | 0 | 5.4983 | 0 | 66400 | 0 | 632565.8613 | 162.5494 | 0
6768 | 10 | 0 | 0 | 0.086797 | 3.55 | 0 | 0 | 0 | 0 | 3.55 | 0 | 66400 | 0 | 632565.8613 | 165.6265 | 0
6769 | 10 | 0 | 0 | 0.080316 | 3.2849 | 0 | 0 | 0 | 0 | 3.2849 | 0 | 66400 | 0 | 632565.8613 | 168.4739 | 0
6770 | 10 | 0 | 0 | 0.097083 | 3.9707 | 0 | 0 | 0 | 0 | 3.9707 | 0 | 66400 | 0 | 632565.8613 | 171.9157 | 0
6771 | 10 | 0 | 0 | 0.11742 | 4.8024 | 0 | 0 | 0 | 0 | 4.8024 | 0 | 66400 | 0 | 632565.8613 | 176.0784 | 0
6772 | 10 | 0 | 0 | 0.10775 | 4.4071 | 0 | 0 | 0 | 0 | 4.4071 | 0 | 66400 | 0 | 632565.8613 | 179.8984 | 0
6773 | 10 | 0 | 0 | 0.15396 | 6.2968 | 0 | 0 | 0 | 0 | 6.2968 | 0 | 66400 | 0 | 632565.8613 | 185.3565 | 0
6774 | 10 | 0 | 0 | 0.16295 | 6.6645 | 0 | 0 | 0 | 0 | 6.6645 | 0 | 66400 | 0 | 632565.8613 | 191.1333 | 0
6775 | 10 | 0 | 0 | 0.19509 | 7.9792 | 0 | 0 | 0 | 0 | 7.9792 | 0 | 66400 | 0 | 632565.8613 | 198.0496 | 0
6776 | 10 | 1 | 0.15209 | 0.16008 | 50.4701 | 200 | 50.4701 | 149.5299 | 200 | 0 | 0 | 66200 | 200 | 632765.8613 | 48.5198 | 0
6777 | 10 | 1 | 0.45757 | 0.11352 | 136.7903 | 200 | 136.7903 | 48.5198 | 185.3101 | 0 | 0 | 66000 | 185.3101 | 632951.1714 | 0 | 0
6778 | 10 | 0 | 0.77936 | 0.1394 | 230.7814 | 0 | 0 | 0 | 0 | 180 | 50.7814 | 66000 | 50.7814 | 633001.9528 | 156.024 | 0
6779 | 10 | 0 | 1 | 0.10611 | 293.1401 | 0 | 0 | 0 | 0 | 180 | 113.1401 | 66000 | 113.1401 | 633115.0928 | 312.048 | 0
6780 | 10 | 0 | 1 | 0.11101 | 293.3402 | 0 | 0 | 0 | 0 | 180 | 113.3402 | 66000 | 113.3402 | 633228.433 | 468.072 | 0
6781 | 10 | 0 | 1 | 0.1663 | 295.6016 | 0 | 0 | 0 | 0 | 49.3055 | 200 | 66000 | 200 | 633428.433 | 510.81 | 46.2961
6782 | 10 | 0 | 1 | 0.13806 | 294.4469 | 0 | 0 | 0 | 0 | 0 | 200 | 66000 | 200 | 633628.433 | 510.81 | 94.4469
6783 | 10 | 0 | 1 | 0.15989 | 295.3396 | 0 | 0 | 0 | 0 | 0 | 200 | 66000 | 200 | 633828.433 | 510.81 | 95.3396
6784 | 10 | 0 | 0.77936 | 0.27636 | 236.3832 | 0 | 0 | 0 | 0 | 0 | 200 | 66000 | 200 | 634028.433 | 510.81 | 36.3832
6785 | 10 | 0 | 0.45757 | 0.37596 | 147.5242 | 0 | 0 | 0 | 0 | 0 | 147.5242 | 66000 | 147.5242 | 634175.9572 | 510.81 | 0
6786 | 10 | 0 | 0.15209 | 0.45054 | 62.3498 | 0 | 0 | 0 | 0 | 0 | 62.3498 | 66000 | 62.3498 | 634238.307 | 510.81 | 0
6787 | 10 | 0 | 0 | 0.4449 | 18.1965 | 0 | 0 | 0 | 0 | 0 | 18.1965 | 66000 | 18.1965 | 634256.5035 | 510.81 | 0
6788 | 10 | 1 | 0 | 0.4277 | 17.4931 | 200 | 17.4931 | 180 | 197.4931 | 0 | 0 | 65800 | 197.4931 | 634453.9966 | 330.81 | 0
6789 | 10 | 1 | 0 | 0.35051 | 14.336 | 200 | 14.336 | 180 | 194.336 | 0 | 0 | 65600 | 194.336 | 634648.3325 | 150.81 | 0
6790 | 10 | 0 | 0 | 0.50944 | 20.8362 | 0 | 0 | 0 | 0 | 20.8362 | 0 | 65600 | 0 | 634648.3325 | 168.8708 | 0
6791 | 10 | 0 | 0 | 0.41802 | 17.0971 | 0 | 0 | 0 | 0 | 17.0971 | 0 | 65600 | 0 | 634648.3325 | 183.6906 | 0
6792 | 10 | 0 | 0 | 0.40643 | 16.6231 | 0 | 0 | 0 | 0 | 16.6231 | 0 | 65600 | 0 | 634648.3325 | 198.0994 | 0
6793 | 10 | 0 | 0 | 0.46317 | 18.9437 | 0 | 0 | 0 | 0 | 18.9437 | 0 | 65600 | 0 | 634648.3325 | 214.5199 | 0
6794 | 10 | 0 | 0 | 0.48452 | 19.8168 | 0 | 0 | 0 | 0 | 19.8168 | 0 | 65600 | 0 | 634648.3325 | 231.6971 | 0
6795 | 10 | 0 | 0 | 0.46823 | 19.1507 | 0 | 0 | 0 | 0 | 19.1507 | 0 | 65600 | 0 | 634648.3325 | 248.2969 | 0
6796 | 10 | 0 | 0 | 0.42896 | 17.5446 | 0 | 0 | 0 | 0 | 17.5446 | 0 | 65600 | 0 | 634648.3325 | 263.5046 | 0
6797 | 10 | 0 | 0 | 0.4854 | 19.853 | 0 | 0 | 0 | 0 | 19.853 | 0 | 65600 | 0 | 634648.3325 | 280.7131 | 0
6798 | 10 | 0 | 0 | 0.62359 | 25.505 | 0 | 0 | 0 | 0 | 25.505 | 0 | 65600 | 0 | 634648.3325 | 302.8209 | 0
6799 | 10 | 0 | 0 | 0.70958 | 29.0218 | 0 | 0 | 0 | 0 | 29.0218 | 0 | 65600 | 0 | 634648.3325 | 327.9769 | 0
6800 | 10 | 1 | 0.15969 | 1 | 87.0176 | 200 | 87.0176 | 112.9824 | 200 | 0 | 0 | 65400 | 200 | 634848.3325 | 214.9945 | 0
6801 | 10 | 1 | 0.48044 | 1 | 179.6511 | 200 | 179.6511 | 20.3489 | 200 | 0 | 0 | 65200 | 200 | 635048.3325 | 194.6456 | 0
6802 | 10 | 0 | 0.81831 | 1 | 277.2276 | 0 | 0 | 0 | 0 | 180 | 97.2276 | 65200 | 97.2276 | 635145.5602 | 350.6696 | 0
6803 | 10 | 0 | 1 | 0.97273 | 328.5847 | 0 | 0 | 0 | 0 | 180 | 148.5847 | 65200 | 148.5847 | 635294.1448 | 506.6936 | 0
6804 | 10 | 0 | 1 | 0.79761 | 321.4224 | 0 | 0 | 0 | 0 | 4.7489 | 200 | 65200 | 200 | 635494.1448 | 510.81 | 116.6734
6805 | 10 | 0 | 1 | 0.78299 | 320.8244 | 0 | 0 | 0 | 0 | 0 | 200 | 65200 | 200 | 635694.1448 | 510.81 | 120.8244
6806 | 10 | 0 | 1 | 0.78146 | 320.7616 | 0 | 0 | 0 | 0 | 0 | 200 | 65200 | 200 | 635894.1448 | 510.81 | 120.7616
6807 | 10 | 0 | 1 | 0.58343 | 312.6624 | 0 | 0 | 0 | 0 | 0 | 200 | 65200 | 200 | 636094.1448 | 510.81 | 112.6624
6808 | 10 | 0 | 0.81831 | 0.4034 | 252.8267 | 0 | 0 | 0 | 0 | 0 | 200 | 65200 | 200 | 636294.1448 | 510.81 | 52.8267
6809 | 10 | 0 | 0.48044 | 0.34062 | 152.6824 | 0 | 0 | 0 | 0 | 0 | 152.6824 | 65200 | 152.6824 | 636446.8272 | 510.81 | 0
6810 | 10 | 0 | 0.15969 | 0.24449 | 56.117 | 0 | 0 | 0 | 0 | 0 | 56.117 | 65200 | 56.117 | 636502.9443 | 510.81 | 0
6811 | 10 | 0 | 0 | 0.3253 | 13.3046 | 0 | 0 | 0 | 0 | 0 | 13.3046 | 65200 | 13.3046 | 636516.2489 | 510.81 | 0
6812 | 10 | 1 | 0 | 0.22914 | 9.3719 | 200 | 9.3719 | 180 | 189.3719 | 0 | 0 | 65000 | 189.3719 | 636705.6208 | 330.81 | 0
6813 | 10 | 1 | 0 | 0.23495 | 9.6095 | 200 | 9.6095 | 180 | 189.6095 | 0 | 0 | 64800 | 189.6095 | 636895.2303 | 150.81 | 0
6814 | 10 | 0 | 0 | 0.2155 | 8.8139 | 0 | 0 | 0 | 0 | 8.8139 | 0 | 64800 | 0 | 636895.2303 | 158.4499 | 0
6815 | 10 | 0 | 0 | 0.19989 | 8.1755 | 0 | 0 | 0 | 0 | 8.1755 | 0 | 64800 | 0 | 636895.2303 | 165.5364 | 0
6816 | 10 | 0 | 0 | 0.22508 | 9.2056 | 0 | 0 | 0 | 0 | 9.2056 | 0 | 64800 | 0 | 636895.2303 | 173.5158 | 0
6817 | 10 | 0 | 0 | 0.19383 | 7.9276 | 0 | 0 | 0 | 0 | 7.9276 | 0 | 64800 | 0 | 636895.2303 | 180.3875 | 0
6818 | 10 | 0 | 0 | 0.17968 | 7.349 | 0 | 0 | 0 | 0 | 7.349 | 0 | 64800 | 0 | 636895.2303 | 186.7576 | 0
6819 | 10 | 0 | 0 | 0.29502 | 12.0662 | 0 | 0 | 0 | 0 | 12.0662 | 0 | 64800 | 0 | 636895.2303 | 197.2166 | 0
6820 | 10 | 0 | 0 | 0.24285 | 9.9324 | 0 | 0 | 0 | 0 | 9.9324 | 0 | 64800 | 0 | 636895.2303 | 205.826 | 0
6821 | 10 | 0 | 0 | 0.24857 | 10.1664 | 0 | 0 | 0 | 0 | 10.1664 | 0 | 64800 | 0 | 636895.2303 | 214.6383 | 0
6822 | 10 | 0 | 0 | 0.24348 | 9.9583 | 0 | 0 | 0 | 0 | 9.9583 | 0 | 64800 | 0 | 636895.2303 | 223.2701 | 0
6823 | 10 | 0 | 0 | 0.33354 | 13.6419 | 0 | 0 | 0 | 0 | 13.6419 | 0 | 64800 | 0 | 636895.2303 | 235.0949 | 0
6824 | 10 | 1 | 0.15625 | 0.33185 | 58.6967 | 200 | 58.6967 | 141.3033 | 200 | 0 | 0 | 64600 | 200 | 637095.2303 | 93.7917 | 0
6825 | 10 | 1 | 0.47009 | 0.30117 | 148.0803 | 200 | 148.0803 | 51.9197 | 200 | 0 | 0 | 64400 | 200 | 637295.2303 | 41.8719 | 0
6826 | 10 | 0 | 0.80068 | 0.43418 | 248.9946 | 0 | 0 | 0 | 0 | 180 | 68.9946 | 64400 | 68.9946 | 637364.2249 | 197.8959 | 0
6827 | 10 | 0 | 1 | 0.54002 | 310.8869 | 0 | 0 | 0 | 0 | 180 | 130.8869 | 64400 | 130.8869 | 637495.1118 | 353.9199 | 0
6828 | 10 | 0 | 1 | 0.55612 | 311.5451 | 0 | 0 | 0 | 0 | 180 | 131.5451 | 64400 | 131.5451 | 637626.657 | 509.9439 | 0
6829 | 10 | 0 | 1 | 0.65596 | 315.6288 | 0 | 0 | 0 | 0 | 0.99914 | 200 | 64400 | 200 | 637826.657 | 510.81 | 114.6297
6830 | 10 | 0 | 1 | 0.52967 | 310.4633 | 0 | 0 | 0 | 0 | 0 | 200 | 64400 | 200 | 638026.657 | 510.81 | 110.4633
6831 | 10 | 0 | 1 | 0.45871 | 307.5612 | 0 | 0 | 0 | 0 | 0 | 200 | 64400 | 200 | 638226.657 | 510.81 | 107.5612
6832 | 10 | 0 | 0.80068 | 0.53833 | 253.2542 | 0 | 0 | 0 | 0 | 0 | 200 | 64400 | 200 | 638426.657 | 510.81 | 53.2542
6833 | 10 | 0 | 0.47009 | 0.43397 | 153.5118 | 0 | 0 | 0 | 0 | 0 | 153.5118 | 64400 | 153.5118 | 638580.1687 | 510.81 | 0
6834 | 10 | 0 | 0.15625 | 0.65986 | 72.1124 | 0 | 0 | 0 | 0 | 0 | 72.1124 | 64400 | 72.1124 | 638652.2811 | 510.81 | 0
6835 | 10 | 0 | 0 | 0.4709 | 19.2599 | 0 | 0 | 0 | 0 | 0 | 19.2599 | 64400 | 19.2599 | 638671.541 | 510.81 | 0
6836 | 10 | 1 | 0 | 0.47246 | 19.3235 | 200 | 19.3235 | 180 | 199.3235 | 0 | 0 | 64200 | 199.3235 | 638870.8645 | 330.81 | 0
6837 | 10 | 1 | 0 | 0.43588 | 17.8273 | 200 | 17.8273 | 180 | 197.8273 | 0 | 0 | 64000 | 197.8273 | 639068.6918 | 150.81 | 0
6838 | 10 | 0 | 0 | 0.49132 | 20.095 | 0 | 0 | 0 | 0 | 20.095 | 0 | 64000 | 0 | 639068.6918 | 168.2283 | 0
6839 | 10 | 0 | 0 | 0.6376 | 26.078 | 0 | 0 | 0 | 0 | 26.078 | 0 | 64000 | 0 | 639068.6918 | 190.8328 | 0
6840 | 10 | 0 | 0 | 0.37511 | 15.342 | 0 | 0 | 0 | 0 | 15.342 | 0 | 64000 | 0 | 639068.6918 | 204.1313 | 0
6841 | 10 | 0 | 0 | 0.41758 | 17.0792 | 0 | 0 | 0 | 0 | 17.0792 | 0 | 64000 | 0 | 639068.6918 | 218.9355 | 0
6842 | 10 | 0 | 0 | 0.42396 | 17.3398 | 0 | 0 | 0 | 0 | 17.3398 | 0 | 64000 | 0 | 639068.6918 | 233.9656 | 0
6843 | 10 | 0 | 0 | 0.56296 | 23.0249 | 0 | 0 | 0 | 0 | 23.0249 | 0 | 64000 | 0 | 639068.6918 | 253.9236 | 0
6844 | 10 | 0 | 0 | 0.68581 | 28.0495 | 0 | 0 | 0 | 0 | 28.0495 | 0 | 64000 | 0 | 639068.6918 | 278.2369 | 0
6845 | 10 | 0 | 0 | 0.50735 | 20.7506 | 0 | 0 | 0 | 0 | 20.7506 | 0 | 64000 | 0 | 639068.6918 | 296.2235 | 0
6846 | 10 | 0 | 0 | 0.46591 | 19.0556 | 0 | 0 | 0 | 0 | 19.0556 | 0 | 64000 | 0 | 639068.6918 | 312.7409 | 0
6847 | 10 | 0 | 0 | 0.42725 | 17.4744 | 0 | 0 | 0 | 0 | 17.4744 | 0 | 64000 | 0 | 639068.6918 | 327.8877 | 0
6848 | 10 | 1 | 0.1761 | 0.58459 | 74.768 | 200 | 74.768 | 125.232 | 200 | 0 | 0 | 63800 | 200 | 639268.6918 | 202.6558 | 0
6849 | 10 | 1 | 0.52983 | 0.65142 | 179.6574 | 200 | 179.6574 | 20.3426 | 200 | 0 | 0 | 63600 | 200 | 639468.6918 | 182.3132 | 0
6850 | 10 | 0 | 0.90243 | 0.57187 | 284.0109 | 0 | 0 | 0 | 0 | 180 | 104.0109 | 63600 | 104.0109 | 639572.7027 | 338.3372 | 0
6851 | 10 | 0 | 1 | 0.65381 | 315.5407 | 0 | 0 | 0 | 0 | 180 | 135.5407 | 63600 | 135.5407 | 639708.2433 | 494.3612 | 0
6852 | 10 | 0 | 1 | 0.68268 | 316.7217 | 0 | 0 | 0 | 0 | 18.9765 | 200 | 63600 | 200 | 639908.2433 | 510.81 | 97.7452
6853 | 10 | 0 | 1 | 0.71443 | 318.0201 | 0 | 0 | 0 | 0 | 0 | 200 | 63600 | 200 | 640108.2433 | 510.81 | 118.0201
6854 | 10 | 0 | 1 | 0.7244 | 318.4278 | 0 | 0 | 0 | 0 | 0 | 200 | 63600 | 200 | 640308.2433 | 510.81 | 118.4278
6855 | 10 | 0 | 1 | 0.58029 | 312.534 | 0 | 0 | 0 | 0 | 0 | 200 | 63600 | 200 | 640508.2433 | 510.81 | 112.534
6856 | 10 | 0 | 0.90243 | 0.56066 | 283.5523 | 0 | 0 | 0 | 0 | 0 | 200 | 63600 | 200 | 640708.2433 | 510.81 | 83.5523
6857 | 10 | 0 | 0.52983 | 0.71677 | 182.3301 | 0 | 0 | 0 | 0 | 0 | 182.3301 | 63600 | 182.3301 | 640890.5734 | 510.81 | 0
6858 | 10 | 0 | 0.1761 | 0.54861 | 73.2964 | 0 | 0 | 0 | 0 | 0 | 73.2964 | 63600 | 73.2964 | 640963.8698 | 510.81 | 0
6859 | 10 | 0 | 0 | 0.64946 | 26.5631 | 0 | 0 | 0 | 0 | 0 | 26.5631 | 63600 | 26.5631 | 640990.4329 | 510.81 | 0
6860 | 10 | 1 | 0 | 0.52171 | 21.338 | 200 | 21.338 | 178.662 | 200 | 0 | 0 | 63400 | 200 | 641190.4329 | 332.148 | 0
6861 | 10 | 1 | 0 | 0.5058 | 20.6872 | 200 | 20.6872 | 179.3128 | 200 | 0 | 0 | 63200 | 200 | 641390.4329 | 152.8352 | 0
6862 | 10 | 0 | 0 | 0.30013 | 12.2754 | 0 | 0 | 0 | 0 | 12.2754 | 0 | 63200 | 0 | 641390.4329 | 163.4756 | 0
6863 | 10 | 0 | 0 | 0.34933 | 14.2878 | 0 | 0 | 0 | 0 | 14.2878 | 0 | 63200 | 0 | 641390.4329 | 175.8602 | 0
6864 | 10 | 0 | 0 | 0.29596 | 12.1047 | 0 | 0 | 0 | 0 | 12.1047 | 0 | 63200 | 0 | 641390.4329 | 186.3526 | 0
6865 | 10 | 0 | 0 | 0.35525 | 14.5296 | 0 | 0 | 0 | 0 | 14.5296 | 0 | 63200 | 0 | 641390.4329 | 198.9468 | 0
6866 | 10 | 0 | 0 | 0.35364 | 14.4638 | 0 | 0 | 0 | 0 | 14.4638 | 0 | 63200 | 0 | 641390.4329 | 211.4841 | 0
6867 | 10 | 0 | 0 | 0.51833 | 21.1995 | 0 | 0 | 0 | 0 | 21.1995 | 0 | 63200 | 0 | 641390.4329 | 229.8598 | 0
6868 | 10 | 0 | 0 | 0.41163 | 16.8355 | 0 | 0 | 0 | 0 | 16.8355 | 0 | 63200 | 0 | 641390.4329 | 244.4528 | 0
6869 | 10 | 0 | 0 | 0.49341 | 20.1803 | 0 | 0 | 0 | 0 | 20.1803 | 0 | 63200 | 0 | 641390.4329 | 261.9451 | 0
6870 | 10 | 0 | 0 | 0.50004 | 20.4515 | 0 | 0 | 0 | 0 | 20.4515 | 0 | 63200 | 0 | 641390.4329 | 279.6725 | 0
6871 | 10 | 0 | 0 | 0.48244 | 19.7319 | 0 | 0 | 0 | 0 | 19.7319 | 0 | 63200 | 0 | 641390.4329 | 296.7761 | 0
6872 | 10 | 1 | 0.15476 | 0.69283 | 73.0301 | 200 | 73.0301 | 126.9699 | 200 | 0 | 0 | 63000 | 200 | 641590.4329 | 169.8062 | 0
6873 | 10 | 1 | 0.4656 | 0.51658 | 155.5943 | 200 | 155.5943 | 44.4057 | 200 | 0 | 0 | 62800 | 200 | 641790.4329 | 125.4005 | 0
6874 | 10 | 0 | 0.79304 | 0.59789 | 253.4833 | 0 | 0 | 0 | 0 | 180 | 73.4833 | 62800 | 73.4833 | 641863.9162 | 281.4245 | 0
6875 | 10 | 0 | 1 | 0.49705 | 309.1293 | 0 | 0 | 0 | 0 | 180 | 129.1293 | 62800 | 129.1293 | 641993.0455 | 437.4485 | 0
6876 | 10 | 0 | 1 | 0.81924 | 322.3069 | 0 | 0 | 0 | 0 | 84.6349 | 200 | 62800 | 200 | 642193.0455 | 510.81 | 37.672
6877 | 10 | 0 | 1 | 0.96272 | 328.1751 | 0 | 0 | 0 | 0 | 0 | 200 | 62800 | 200 | 642393.0455 | 510.81 | 128.1751
6878 | 10 | 0 | 1 | 0.76314 | 320.0123 | 0 | 0 | 0 | 0 | 0 | 200 | 62800 | 200 | 642593.0455 | 510.81 | 120.0123
6879 | 10 | 0 | 1 | 0.76829 | 320.223 | 0 | 0 | 0 | 0 | 0 | 200 | 62800 | 200 | 642793.0455 | 510.81 | 120.223
6880 | 10 | 0 | 0.79304 | 0.58742 | 253.0551 | 0 | 0 | 0 | 0 | 0 | 200 | 62800 | 200 | 642993.0455 | 510.81 | 53.0551
6881 | 10 | 0 | 0.4656 | 0.47576 | 153.9248 | 0 | 0 | 0 | 0 | 0 | 153.9248 | 62800 | 153.9248 | 643146.9703 | 510.81 | 0
6882 | 10 | 0 | 0.15476 | 0.50687 | 65.4242 | 0 | 0 | 0 | 0 | 0 | 65.4242 | 62800 | 65.4242 | 643212.3945 | 510.81 | 0
6883 | 10 | 0 | 0 | 0.48669 | 19.9055 | 0 | 0 | 0 | 0 | 0 | 19.9055 | 62800 | 19.9055 | 643232.3 | 510.81 | 0
6884 | 10 | 1 | 0 | 0.40794 | 16.6846 | 200 | 16.6846 | 180 | 196.6846 | 0 | 0 | 62600 | 196.6846 | 643428.9846 | 330.81 | 0
6885 | 10 | 1 | 0 | 0.40725 | 16.6564 | 200 | 16.6564 | 180 | 196.6564 | 0 | 0 | 62400 | 196.6564 | 643625.6411 | 150.81 | 0
6886 | 10 | 0 | 0 | 0.34713 | 14.1976 | 0 | 0 | 0 | 0 | 14.1976 | 0 | 62400 | 0 | 643625.6411 | 163.1165 | 0
6887 | 10 | 0 | 0 | 0.36518 | 14.9358 | 0 | 0 | 0 | 0 | 14.9358 | 0 | 62400 | 0 | 643625.6411 | 176.0628 | 0
6888 | 10 | 0 | 0 | 0.31744 | 12.9834 | 0 | 0 | 0 | 0 | 12.9834 | 0 | 62400 | 0 | 643625.6411 | 187.3168 | 0
6889 | 10 | 0 | 0 | 0.1884 | 7.7054 | 0 | 0 | 0 | 0 | 7.7054 | 0 | 62400 | 0 | 643625.6411 | 193.9959 | 0
6890 | 10 | 0 | 0 | 0.21389 | 8.7481 | 0 | 0 | 0 | 0 | 8.7481 | 0 | 62400 | 0 | 643625.6411 | 201.5788 | 0
6891 | 10 | 0 | 0 | 0.25655 | 10.4931 | 0 | 0 | 0 | 0 | 10.4931 | 0 | 62400 | 0 | 643625.6411 | 210.6742 | 0
6892 | 10 | 0 | 0 | 0.22428 | 9.173 | 0 | 0 | 0 | 0 | 9.173 | 0 | 62400 | 0 | 643625.6411 | 218.6253 | 0
6893 | 10 | 0 | 0 | 0.17098 | 6.9931 | 0 | 0 | 0 | 0 | 6.9931 | 0 | 62400 | 0 | 643625.6411 | 224.6869 | 0
6894 | 10 | 0 | 0 | 0.1508 | 6.1676 | 0 | 0 | 0 | 0 | 6.1676 | 0 | 62400 | 0 | 643625.6411 | 230.033 | 0
6895 | 10 | 0 | 0 | 0.20872 | 8.5366 | 0 | 0 | 0 | 0 | 8.5366 | 0 | 62400 | 0 | 643625.6411 | 237.4326 | 0
6896 | 10 | 1 | 0.17633 | 0.20628 | 59.3617 | 200 | 59.3617 | 140.6383 | 200 | 0 | 0 | 62200 | 200 | 643825.6411 | 96.7942 | 0
6897 | 10 | 1 | 0.53052 | 0.31208 | 165.9789 | 200 | 165.9789 | 34.0211 | 200 | 0 | 0 | 62000 | 200 | 644025.6411 | 62.7732 | 0
6898 | 10 | 0 | 0.90361 | 0.31182 | 273.7161 | 0 | 0 | 0 | 0 | 180 | 93.7161 | 62000 | 93.7161 | 644119.3572 | 218.7972 | 0
6899 | 10 | 0 | 1 | 0.30848 | 301.417 | 0 | 0 | 0 | 0 | 180 | 121.417 | 62000 | 121.417 | 644240.7742 | 374.8212 | 0
6900 | 10 | 0 | 1 | 0.25823 | 299.3614 | 0 | 0 | 0 | 0 | 156.886 | 142.4754 | 62000 | 142.4754 | 644383.2496 | 510.81 | 0
6901 | 10 | 0 | 1 | 0.35094 | 303.1536 | 0 | 0 | 0 | 0 | 0 | 200 | 62000 | 200 | 644583.2496 | 510.81 | 103.1536
6902 | 10 | 0 | 1 | 0.42766 | 306.2913 | 0 | 0 | 0 | 0 | 0 | 200 | 62000 | 200 | 644783.2496 | 510.81 | 106.2913
6903 | 10 | 0 | 1 | 0.46284 | 307.7303 | 0 | 0 | 0 | 0 | 0 | 200 | 62000 | 200 | 644983.2496 | 510.81 | 107.7303
6904 | 10 | 0 | 0.90361 | 0.44662 | 279.2296 | 0 | 0 | 0 | 0 | 0 | 200 | 62000 | 200 | 645183.2496 | 510.81 | 79.2296
6905 | 10 | 0 | 0.53052 | 0.44012 | 171.2156 | 0 | 0 | 0 | 0 | 0 | 171.2156 | 62000 | 171.2156 | 645354.4652 | 510.81 | 0
6906 | 10 | 0 | 0.17633 | 0.37349 | 66.2003 | 0 | 0 | 0 | 0 | 0 | 66.2003 | 62000 | 66.2003 | 645420.6655 | 510.81 | 0
6907 | 10 | 0 | 0 | 0.33909 | 13.869 | 0 | 0 | 0 | 0 | 0 | 13.869 | 62000 | 13.869 | 645434.5345 | 510.81 | 0
6908 | 10 | 1 | 0 | 0.32162 | 13.1543 | 200 | 13.1543 | 180 | 193.1543 | 0 | 0 | 61800 | 193.1543 | 645627.6888 | 330.81 | 0
6909 | 10 | 1 | 0 | 0.26403 | 10.7988 | 200 | 10.7988 | 180 | 190.7988 | 0 | 0 | 61600 | 190.7988 | 645818.4875 | 150.81 | 0
6910 | 10 | 0 | 0 | 0.38541 | 15.7632 | 0 | 0 | 0 | 0 | 15.7632 | 0 | 61600 | 0 | 645818.4875 | 164.4736 | 0
6911 | 10 | 0 | 0 | 0.35597 | 14.5592 | 0 | 0 | 0 | 0 | 14.5592 | 0 | 61600 | 0 | 645818.4875 | 177.0935 | 0
6912 | 10 | 0 | 0 | 0.36467 | 14.9148 | 0 | 0 | 0 | 0 | 14.9148 | 0 | 61600 | 0 | 645818.4875 | 190.0217 | 0
6913 | 10 | 0 | 0 | 0.3203 | 13.1004 | 0 | 0 | 0 | 0 | 13.1004 | 0 | 61600 | 0 | 645818.4875 | 201.3771 | 0
6914 | 10 | 0 | 0 | 0.41108 | 16.8134 | 0 | 0 | 0 | 0 | 16.8134 | 0 | 61600 | 0 | 645818.4875 | 215.951 | 0
6915 | 10 | 0 | 0 | 0.51905 | 21.229 | 0 | 0 | 0 | 0 | 21.229 | 0 | 61600 | 0 | 645818.4875 | 234.3522 | 0
6916 | 10 | 0 | 0 | 0.64766 | 26.4893 | 0 | 0 | 0 | 0 | 26.4893 | 0 | 61600 | 0 | 645818.4875 | 257.3132 | 0
6917 | 10 | 0 | 0 | 0.66438 | 27.1733 | 0 | 0 | 0 | 0 | 27.1733 | 0 | 61600 | 0 | 645818.4875 | 280.867 | 0
6918 | 10 | 0 | 0 | 0.48098 | 19.6721 | 0 | 0 | 0 | 0 | 19.6721 | 0 | 61600 | 0 | 645818.4875 | 297.9188 | 0
6919 | 10 | 0 | 0 | 0.74139 | 30.3229 | 0 | 0 | 0 | 0 | 30.3229 | 0 | 61600 | 0 | 645818.4875 | 324.2027 | 0
6920 | 10 | 1 | 0.15137 | 0.84836 | 78.4135 | 200 | 78.4135 | 121.5865 | 200 | 0 | 0 | 61400 | 200 | 646018.4875 | 202.6161 | 0
6921 | 10 | 1 | 0.45542 | 1 | 172.425 | 200 | 172.425 | 27.575 | 200 | 0 | 0 | 61200 | 200 | 646218.4875 | 175.0411 | 0
6922 | 10 | 0 | 0.77569 | 0.98905 | 264.4723 | 0 | 0 | 0 | 0 | 180 | 84.4723 | 61200 | 84.4723 | 646302.9598 | 331.0651 | 0
6923 | 10 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 180 | 149.7 | 61200 | 149.7 | 646452.6598 | 487.0891 | 0
6924 | 10 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 27.366 | 200 | 61200 | 200 | 646652.6598 | 510.81 | 102.334
6925 | 10 | 0 | 1 | 0.73324 | 318.7897 | 0 | 0 | 0 | 0 | 0 | 200 | 61200 | 200 | 646852.6598 | 510.81 | 118.7897
6926 | 10 | 0 | 1 | 0.75765 | 319.7879 | 0 | 0 | 0 | 0 | 0 | 200 | 61200 | 200 | 647052.6598 | 510.81 | 119.7879
6927 | 10 | 0 | 1 | 0.82702 | 322.6252 | 0 | 0 | 0 | 0 | 0 | 200 | 61200 | 200 | 647252.6598 | 510.81 | 122.6252
6928 | 10 | 0 | 0.77569 | 0.4215 | 241.2596 | 0 | 0 | 0 | 0 | 0 | 200 | 61200 | 200 | 647452.6598 | 510.81 | 41.2596
6929 | 10 | 0 | 0.45542 | 0.77401 | 163.1819 | 0 | 0 | 0 | 0 | 0 | 163.1819 | 61200 | 163.1819 | 647615.8417 | 510.81 | 0
6930 | 10 | 0 | 0.15137 | 0.67252 | 71.2218 | 0 | 0 | 0 | 0 | 0 | 71.2218 | 61200 | 71.2218 | 647687.0635 | 510.81 | 0
6931 | 10 | 0 | 0 | 0.39533 | 16.169 | 0 | 0 | 0 | 0 | 0 | 16.169 | 61200 | 16.169 | 647703.2325 | 510.81 | 0
6932 | 10 | 1 | 0 | 0.3358 | 13.7341 | 200 | 13.7341 | 180 | 193.7341 | 0 | 0 | 61000 | 193.7341 | 647896.9667 | 330.81 | 0
6933 | 10 | 1 | 0 | 0.37049 | 15.1529 | 200 | 15.1529 | 180 | 195.1529 | 0 | 0 | 60800 | 195.1529 | 648092.1195 | 150.81 | 0
6934 | 10 | 0 | 0 | 0.25519 | 10.4374 | 0 | 0 | 0 | 0 | 10.4374 | 0 | 60800 | 0 | 648092.1195 | 159.8571 | 0
6935 | 10 | 0 | 0 | 0.3066 | 12.54 | 0 | 0 | 0 | 0 | 12.54 | 0 | 60800 | 0 | 648092.1195 | 170.7268 | 0
6936 | 10 | 0 | 0 | 0.27145 | 11.1022 | 0 | 0 | 0 | 0 | 11.1022 | 0 | 60800 | 0 | 648092.1195 | 180.3502 | 0
6937 | 10 | 0 | 0 | 0.162 | 6.6257 | 0 | 0 | 0 | 0 | 6.6257 | 0 | 60800 | 0 | 648092.1195 | 186.0933 | 0
6938 | 10 | 0 | 0 | 0.1439 | 5.8854 | 0 | 0 | 0 | 0 | 5.8854 | 0 | 60800 | 0 | 648092.1195 | 191.1948 | 0
6939 | 10 | 0 | 0 | 0.15049 | 6.155 | 0 | 0 | 0 | 0 | 6.155 | 0 | 60800 | 0 | 648092.1195 | 196.5299 | 0
6940 | 10 | 0 | 0 | 0.16185 | 6.6196 | 0 | 0 | 0 | 0 | 6.6196 | 0 | 60800 | 0 | 648092.1195 | 202.2678 | 0
6941 | 10 | 0 | 0 | 0.17605 | 7.2002 | 0 | 0 | 0 | 0 | 7.2002 | 0 | 60800 | 0 | 648092.1195 | 208.509 | 0
6942 | 10 | 0 | 0 | 0.13504 | 5.5232 | 0 | 0 | 0 | 0 | 5.5232 | 0 | 60800 | 0 | 648092.1195 | 213.2965 | 0
6943 | 10 | 0 | 0 | 0.17935 | 7.3352 | 0 | 0 | 0 | 0 | 7.3352 | 0 | 60800 | 0 | 648092.1195 | 219.6546 | 0
6944 | 10 | 1 | 0.15591 | 0.17183 | 52.0546 | 200 | 52.0546 | 147.9454 | 200 | 0 | 0 | 60600 | 200 | 648292.1195 | 71.7092 | 0
6945 | 10 | 1 | 0.46908 | 0.18725 | 143.1274 | 200 | 143.1274 | 56.8726 | 200 | 0 | 0 | 60400 | 200 | 648492.1195 | 14.8366 | 0
6946 | 10 | 0 | 0.79895 | 0.19909 | 238.8802 | 0 | 0 | 0 | 0 | 180 | 58.8802 | 60400 | 58.8802 | 648550.9997 | 170.8606 | 0
6947 | 10 | 0 | 1 | 0.15684 | 295.2149 | 0 | 0 | 0 | 0 | 180 | 115.2149 | 60400 | 115.2149 | 648666.2146 | 326.8846 | 0
6948 | 10 | 0 | 1 | 0.22224 | 297.8897 | 0 | 0 | 0 | 0 | 180 | 117.8897 | 60400 | 117.8897 | 648784.1043 | 482.9086 | 0
6949 | 10 | 0 | 1 | 0.22846 | 298.144 | 0 | 0 | 0 | 0 | 32.1889 | 200 | 60400 | 200 | 648984.1043 | 510.81 | 65.9551
6950 | 10 | 0 | 1 | 0.2301 | 298.2112 | 0 | 0 | 0 | 0 | 0 | 200 | 60400 | 200 | 649184.1043 | 510.81 | 98.2112
6951 | 10 | 0 | 1 | 0.21738 | 297.6908 | 0 | 0 | 0 | 0 | 0 | 200 | 60400 | 200 | 649384.1043 | 510.81 | 97.6908
6952 | 10 | 0 | 0.79895 | 0.2193 | 239.7066 | 0 | 0 | 0 | 0 | 0 | 200 | 60400 | 200 | 649584.1043 | 510.81 | 39.7066
6953 | 10 | 0 | 0.46908 | 0.20249 | 143.7506 | 0 | 0 | 0 | 0 | 0 | 143.7506 | 60400 | 143.7506 | 649727.8549 | 510.81 | 0
6954 | 10 | 0 | 0.15591 | 0.15684 | 51.4412 | 0 | 0 | 0 | 0 | 0 | 51.4412 | 60400 | 51.4412 | 649779.2961 | 510.81 | 0
6955 | 10 | 0 | 0 | 0.18509 | 7.5703 | 0 | 0 | 0 | 0 | 0 | 7.5703 | 60400 | 7.5703 | 649786.8664 | 510.81 | 0
6956 | 10 | 1 | 0 | 0.21074 | 8.6195 | 200 | 8.6195 | 180 | 188.6195 | 0 | 0 | 60200 | 188.6195 | 649975.4859 | 330.81 | 0
6957 | 10 | 1 | 0 | 0.22005 | 8.9999 | 200 | 8.9999 | 180 | 188.9999 | 0 | 0 | 60000 | 188.9999 | 650164.4858 | 150.81 | 0
6958 | 10 | 0 | 0 | 0.18386 | 7.5199 | 0 | 0 | 0 | 0 | 7.5199 | 0 | 60000 | 0 | 650164.4858 | 157.3283 | 0
6959 | 10 | 0 | 0 | 0.28932 | 11.8333 | 0 | 0 | 0 | 0 | 11.8333 | 0 | 60000 | 0 | 650164.4858 | 167.5854 | 0
6960 | 10 | 0 | 0 | 0.26085 | 10.6688 | 0 | 0 | 0 | 0 | 10.6688 | 0 | 60000 | 0 | 650164.4858 | 176.8331 | 0
6961 | 10 | 0 | 0 | 0.38117 | 15.5897 | 0 | 0 | 0 | 0 | 15.5897 | 0 | 60000 | 0 | 650164.4858 | 190.3463 | 0
6962 | 10 | 0 | 0 | 0.35575 | 14.5501 | 0 | 0 | 0 | 0 | 14.5501 | 0 | 60000 | 0 | 650164.4858 | 202.9583 | 0
6963 | 10 | 0 | 0 | 0.27414 | 11.2124 | 0 | 0 | 0 | 0 | 11.2124 | 0 | 60000 | 0 | 650164.4858 | 212.6773 | 0
6964 | 10 | 0 | 0 | 0.33391 | 13.657 | 0 | 0 | 0 | 0 | 13.657 | 0 | 60000 | 0 | 650164.4858 | 224.5152 | 0
6965 | 10 | 0 | 0 | 0.34057 | 13.9294 | 0 | 0 | 0 | 0 | 13.9294 | 0 | 60000 | 0 | 650164.4858 | 236.5892 | 0
6966 | 10 | 0 | 0 | 0.46981 | 19.2151 | 0 | 0 | 0 | 0 | 19.2151 | 0 | 60000 | 0 | 650164.4858 | 253.2449 | 0
6967 | 10 | 0 | 0 | 0.44055 | 18.0186 | 0 | 0 | 0 | 0 | 18.0186 | 0 | 60000 | 0 | 650164.4858 | 268.8634 | 0
6968 | 10 | 1 | 0.15719 | 0.44861 | 63.744 | 200 | 63.744 | 136.256 | 200 | 0 | 0 | 59800 | 200 | 650364.4858 | 132.6074 | 0
6969 | 10 | 1 | 0.47292 | 0.36201 | 151.3862 | 200 | 151.3862 | 48.6138 | 200 | 0 | 0 | 59600 | 200 | 650564.4858 | 83.9936 | 0
6970 | 10 | 0 | 0.80551 | 0.45409 | 251.2025 | 0 | 0 | 0 | 0 | 180 | 71.2025 | 59600 | 71.2025 | 650635.6882 | 240.0176 | 0
6971 | 10 | 0 | 1 | 0.7065 | 317.6958 | 0 | 0 | 0 | 0 | 180 | 137.6958 | 59600 | 137.6958 | 650773.3841 | 396.0416 | 0
6972 | 10 | 0 | 1 | 0.83094 | 322.7856 | 0 | 0 | 0 | 0 | 132.4047 | 190.381 | 59600 | 190.381 | 650963.765 | 510.81 | 0
6973 | 10 | 0 | 1 | 0.8101 | 321.933 | 0 | 0 | 0 | 0 | 0 | 200 | 59600 | 200 | 651163.765 | 510.81 | 121.933
6974 | 10 | 0 | 1 | 0.97395 | 328.6346 | 0 | 0 | 0 | 0 | 0 | 200 | 59600 | 200 | 651363.765 | 510.81 | 128.6346
6975 | 10 | 0 | 1 | 0.73808 | 318.9876 | 0 | 0 | 0 | 0 | 0 | 200 | 59600 | 200 | 651563.765 | 510.81 | 118.9876
6976 | 10 | 0 | 0.80551 | 0.46289 | 251.5623 | 0 | 0 | 0 | 0 | 0 | 200 | 59600 | 200 | 651763.765 | 510.81 | 51.5623
6977 | 10 | 0 | 0.47292 | 0.54562 | 158.8962 | 0 | 0 | 0 | 0 | 0 | 158.8962 | 59600 | 158.8962 | 651922.6612 | 510.81 | 0
6978 | 10 | 0 | 0.15719 | 0.42178 | 62.6467 | 0 | 0 | 0 | 0 | 0 | 62.6467 | 59600 | 62.6467 | 651985.3079 | 510.81 | 0
6979 | 10 | 0 | 0 | 0.38351 | 15.6855 | 0 | 0 | 0 | 0 | 0 | 15.6855 | 59600 | 15.6855 | 652000.9934 | 510.81 | 0
6980 | 10 | 1 | 0 | 0.55276 | 22.608 | 200 | 22.608 | 177.392 | 200 | 0 | 0 | 59400 | 200 | 652200.9934 | 333.418 | 0
6981 | 10 | 1 | 0 | 0.31875 | 13.0369 | 200 | 13.0369 | 180 | 193.0369 | 0 | 0 | 59200 | 193.0369 | 652394.0302 | 153.418 | 0
6982 | 10 | 0 | 0 | 0.29729 | 12.1593 | 0 | 0 | 0 | 0 | 12.1593 | 0 | 59200 | 0 | 652394.0302 | 163.9577 | 0
6983 | 10 | 0 | 0 | 0.40853 | 16.7091 | 0 | 0 | 0 | 0 | 16.7091 | 0 | 59200 | 0 | 652394.0302 | 178.4411 | 0
6984 | 10 | 0 | 0 | 0.4495 | 18.3845 | 0 | 0 | 0 | 0 | 18.3845 | 0 | 59200 | 0 | 652394.0302 | 194.3768 | 0
6985 | 10 | 0 | 0 | 0.59005 | 24.133 | 0 | 0 | 0 | 0 | 24.133 | 0 | 59200 | 0 | 652394.0302 | 215.2953 | 0
6986 | 10 | 0 | 0 | 0.54796 | 22.4116 | 0 | 0 | 0 | 0 | 22.4116 | 0 | 59200 | 0 | 652394.0302 | 234.7216 | 0
6987 | 10 | 0 | 0 | 0.54076 | 22.1171 | 0 | 0 | 0 | 0 | 22.1171 | 0 | 59200 | 0 | 652394.0302 | 253.8927 | 0
6988 | 10 | 0 | 0 | 0.61266 | 25.0577 | 0 | 0 | 0 | 0 | 25.0577 | 0 | 59200 | 0 | 652394.0302 | 275.6127 | 0
6989 | 10 | 0 | 0 | 0.50746 | 20.7552 | 0 | 0 | 0 | 0 | 20.7552 | 0 | 59200 | 0 | 652394.0302 | 293.6033 | 0
6990 | 10 | 0 | 0 | 0.39752 | 16.2585 | 0 | 0 | 0 | 0 | 16.2585 | 0 | 59200 | 0 | 652394.0302 | 307.6962 | 0
6991 | 10 | 0 | 0 | 0.4664 | 19.0758 | 0 | 0 | 0 | 0 | 19.0758 | 0 | 59200 | 0 | 652394.0302 | 324.2311 | 0
6992 | 10 | 1 | 0.16855 | 0.45883 | 67.4418 | 200 | 67.4418 | 132.5582 | 200 | 0 | 0 | 59000 | 200 | 652594.0302 | 191.6729 | 0
6993 | 10 | 1 | 0.50709 | 0.34795 | 160.6792 | 200 | 160.6792 | 39.3208 | 200 | 0 | 0 | 58800 | 200 | 652794.0302 | 152.352 | 0
6994 | 10 | 0 | 0.8637 | 0.34047 | 263.3634 | 0 | 0 | 0 | 0 | 180 | 83.3634 | 58800 | 83.3634 | 652877.3936 | 308.376 | 0
6995 | 10 | 0 | 1 | 0.28262 | 300.3593 | 0 | 0 | 0 | 0 | 180 | 120.3593 | 58800 | 120.3593 | 652997.7529 | 464.4 | 0
6996 | 10 | 0 | 1 | 0.39209 | 304.8366 | 0 | 0 | 0 | 0 | 53.5417 | 200 | 58800 | 200 | 653197.7529 | 510.81 | 51.2949
6997 | 10 | 0 | 1 | 0.33267 | 302.4062 | 0 | 0 | 0 | 0 | 0 | 200 | 58800 | 200 | 653397.7529 | 510.81 | 102.4062
6998 | 10 | 0 | 1 | 0.3944 | 304.9309 | 0 | 0 | 0 | 0 | 0 | 200 | 58800 | 200 | 653597.7529 | 510.81 | 104.9309
6999 | 10 | 0 | 1 | 0.44588 | 307.0365 | 0 | 0 | 0 | 0 | 0 | 200 | 58800 | 200 | 653797.7529 | 510.81 | 107.0365
7000 | 10 | 0 | 0.8637 | 0.49906 | 269.8496 | 0 | 0 | 0 | 0 | 0 | 200 | 58800 | 200 | 653997.7529 | 510.81 | 69.8496
7001 | 10 | 0 | 0.50709 | 0.44835 | 164.7857 | 0 | 0 | 0 | 0 | 0 | 164.7857 | 58800 | 164.7857 | 654162.5386 | 510.81 | 0
7002 | 10 | 0 | 0.16855 | 0.48977 | 68.7074 | 0 | 0 | 0 | 0 | 0 | 68.7074 | 58800 | 68.7074 | 654231.246 | 510.81 | 0
7003 | 10 | 0 | 0 | 0.33504 | 13.7032 | 0 | 0 | 0 | 0 | 0 | 13.7032 | 58800 | 13.7032 | 654244.9492 | 510.81 | 0
7004 | 10 | 1 | 0 | 0.53133 | 21.7312 | 200 | 21.7312 | 178.2688 | 200 | 0 | 0 | 58600 | 200 | 654444.9492 | 332.5412 | 0
7005 | 10 | 1 | 0 | 0.57899 | 23.6809 | 200 | 23.6809 | 176.3191 | 200 | 0 | 0 | 58400 | 200 | 654644.9492 | 156.222 | 0
7006 | 10 | 0 | 0 | 0.49109 | 20.0857 | 0 | 0 | 0 | 0 | 20.0857 | 0 | 58400 | 0 | 654644.9492 | 173.6324 | 0
7007 | 10 | 0 | 0 | 0.45286 | 18.5218 | 0 | 0 | 0 | 0 | 18.5218 | 0 | 58400 | 0 | 654644.9492 | 189.6871 | 0
7008 | 10 | 0 | 0 | 0.54565 | 22.317 | 0 | 0 | 0 | 0 | 22.317 | 0 | 58400 | 0 | 654644.9492 | 209.0314 | 0
7009 | 10 | 0 | 0 | 0.65436 | 26.7633 | 0 | 0 | 0 | 0 | 26.7633 | 0 | 58400 | 0 | 654644.9492 | 232.2299 | 0
7010 | 10 | 0 | 0 | 0.58683 | 24.0013 | 0 | 0 | 0 | 0 | 24.0013 | 0 | 58400 | 0 | 654644.9492 | 253.0342 | 0
7011 | 10 | 0 | 0 | 0.55996 | 22.9025 | 0 | 0 | 0 | 0 | 22.9025 | 0 | 58400 | 0 | 654644.9492 | 272.8861 | 0
7012 | 10 | 0 | 0 | 0.67138 | 27.4592 | 0 | 0 | 0 | 0 | 27.4592 | 0 | 58400 | 0 | 654644.9492 | 296.6878 | 0
7013 | 10 | 0 | 0 | 0.50263 | 20.5576 | 0 | 0 | 0 | 0 | 20.5576 | 0 | 58400 | 0 | 654644.9492 | 314.5071 | 0
7014 | 10 | 0 | 0 | 0.64412 | 26.3446 | 0 | 0 | 0 | 0 | 26.3446 | 0 | 58400 | 0 | 654644.9492 | 337.3427 | 0
7015 | 10 | 0 | 0 | 0.79706 | 32.5997 | 0 | 0 | 0 | 0 | 32.5997 | 0 | 58400 | 0 | 654644.9492 | 365.6001 | 0
7016 | 10 | 1 | 0.143 | 0.80628 | 74.2762 | 200 | 74.2762 | 125.7238 | 200 | 0 | 0 | 58200 | 200 | 654844.9492 | 239.8763 | 0
7017 | 10 | 1 | 0.43024 | 0.96787 | 163.8405 | 200 | 163.8405 | 36.1595 | 200 | 0 | 0 | 58000 | 200 | 655044.9492 | 203.7168 | 0
7018 | 10 | 0 | 0.73281 | 0.97191 | 251.3873 | 0 | 0 | 0 | 0 | 180 | 71.3873 | 58000 | 71.3873 | 655116.3366 | 359.7408 | 0
7019 | 10 | 0 | 0.99235 | 1 | 327.4904 | 0 | 0 | 0 | 0 | 174.2838 | 153.2066 | 58000 | 153.2066 | 655269.5432 | 510.81 | 0
7020 | 10 | 0 | 1 | 0.93263 | 326.9445 | 0 | 0 | 0 | 0 | 0 | 200 | 58000 | 200 | 655469.5432 | 510.81 | 126.9445
7021 | 10 | 0 | 1 | 0.79249 | 321.2129 | 0 | 0 | 0 | 0 | 0 | 200 | 58000 | 200 | 655669.5432 | 510.81 | 121.2129
7022 | 10 | 0 | 1 | 0.66946 | 316.181 | 0 | 0 | 0 | 0 | 0 | 200 | 58000 | 200 | 655869.5432 | 510.81 | 116.181
7023 | 10 | 0 | 0.99235 | 0.99027 | 327.0926 | 0 | 0 | 0 | 0 | 0 | 200 | 58000 | 200 | 656069.5432 | 510.81 | 127.0926
7024 | 10 | 0 | 0.73281 | 0.61174 | 236.6563 | 0 | 0 | 0 | 0 | 0 | 200 | 58000 | 200 | 656269.5432 | 510.81 | 36.6563
7025 | 10 | 0 | 0.43024 | 0.63792 | 150.3453 | 0 | 0 | 0 | 0 | 0 | 150.3453 | 58000 | 150.3453 | 656419.8885 | 510.81 | 0
7026 | 10 | 0 | 0.143 | 0.69873 | 69.8772 | 0 | 0 | 0 | 0 | 0 | 69.8772 | 58000 | 69.8772 | 656489.7657 | 510.81 | 0
7027 | 10 | 0 | 0 | 0.83265 | 34.0552 | 0 | 0 | 0 | 0 | 0 | 34.0552 | 58000 | 34.0552 | 656523.8209 | 510.81 | 0
7028 | 10 | 1 | 0 | 0.6738 | 27.5585 | 200 | 27.5585 | 172.4415 | 200 | 0 | 0 | 57800 | 200 | 656723.8209 | 338.3685 | 0
7029 | 10 | 1 | 0 | 0.80556 | 32.9475 | 200 | 32.9475 | 167.0525 | 200 | 0 | 0 | 57600 | 200 | 656923.8209 | 171.3161 | 0
7030 | 10 | 0 | 0 | 0.70854 | 28.9792 | 0 | 0 | 0 | 0 | 28.9792 | 0 | 57600 | 0 | 656923.8209 | 196.4353 | 0
7031 | 10 | 0 | 0 | 0.65255 | 26.6895 | 0 | 0 | 0 | 0 | 26.6895 | 0 | 57600 | 0 | 656923.8209 | 219.5697 | 0
7032 | 10 | 0 | 0 | 0.63465 | 25.957 | 0 | 0 | 0 | 0 | 25.957 | 0 | 57600 | 0 | 656923.8209 | 242.0693 | 0
7033 | 10 | 0 | 0 | 0.5479 | 22.4092 | 0 | 0 | 0 | 0 | 22.4092 | 0 | 57600 | 0 | 656923.8209 | 261.4936 | 0
7034 | 10 | 0 | 0 | 0.39595 | 16.1943 | 0 | 0 | 0 | 0 | 16.1943 | 0 | 57600 | 0 | 656923.8209 | 275.5308 | 0
7035 | 10 | 0 | 0 | 0.31121 | 12.7283 | 0 | 0 | 0 | 0 | 12.7283 | 0 | 57600 | 0 | 656923.8209 | 286.5636 | 0
7036 | 10 | 0 | 0 | 0.23343 | 9.5474 | 0 | 0 | 0 | 0 | 9.5474 | 0 | 57600 | 0 | 656923.8209 | 294.8393 | 0
7037 | 10 | 0 | 0 | 0.2294 | 9.3825 | 0 | 0 | 0 | 0 | 9.3825 | 0 | 57600 | 0 | 656923.8209 | 302.9721 | 0
7038 | 10 | 0 | 0 | 0.21028 | 8.6004 | 0 | 0 | 0 | 0 | 8.6004 | 0 | 57600 | 0 | 656923.8209 | 310.4269 | 0
7039 | 10 | 0 | 0 | 0.27791 | 11.3664 | 0 | 0 | 0 | 0 | 11.3664 | 0 | 57600 | 0 | 656923.8209 | 320.2793 | 0
7040 | 10 | 1 | 0.15086 | 0.29089 | 55.4672 | 200 | 55.4672 | 144.5328 | 200 | 0 | 0 | 57400 | 200 | 657123.8209 | 175.7465 | 0
7041 | 10 | 1 | 0.4539 | 0.18924 | 138.8259 | 200 | 138.8259 | 61.1741 | 200 | 0 | 0 | 57200 | 200 | 657323.8209 | 114.5724 | 0
7042 | 10 | 0 | 0.7731 | 0.19056 | 231.0661 | 0 | 0 | 0 | 0 | 180 | 51.0661 | 57200 | 51.0661 | 657374.8871 | 270.5964 | 0
7043 | 10 | 0 | 1 | 0.21872 | 297.7455 | 0 | 0 | 0 | 0 | 180 | 117.7455 | 57200 | 117.7455 | 657492.6326 | 426.6204 | 0
7044 | 10 | 0 | 1 | 0.21938 | 297.7727 | 0 | 0 | 0 | 0 | 97.1269 | 200 | 57200 | 200 | 657692.6326 | 510.81 | 0.64578
7045 | 10 | 0 | 1 | 0.25549 | 299.2496 | 0 | 0 | 0 | 0 | 0 | 200 | 57200 | 200 | 657892.6326 | 510.81 | 99.2496
7046 | 10 | 0 | 1 | 0.20844 | 297.3251 | 0 | 0 | 0 | 0 | 0 | 200 | 57200 | 200 | 658092.6326 | 510.81 | 97.3251
7047 | 10 | 0 | 1 | 0.31993 | 301.8852 | 0 | 0 | 0 | 0 | 0 | 200 | 57200 | 200 | 658292.6326 | 510.81 | 101.8852
7048 | 10 | 0 | 0.7731 | 0.38819 | 239.1492 | 0 | 0 | 0 | 0 | 0 | 200 | 57200 | 200 | 658492.6326 | 510.81 | 39.1492
7049 | 10 | 0 | 0.4539 | 0.37448 | 146.4023 | 0 | 0 | 0 | 0 | 0 | 146.4023 | 57200 | 146.4023 | 658639.0349 | 510.81 | 0
7050 | 10 | 0 | 0.15086 | 0.30124 | 55.8907 | 0 | 0 | 0 | 0 | 0 | 55.8907 | 57200 | 55.8907 | 658694.9255 | 510.81 | 0
7051 | 10 | 0 | 0 | 0.44899 | 18.3637 | 0 | 0 | 0 | 0 | 0 | 18.3637 | 57200 | 18.3637 | 658713.2892 | 510.81 | 0
7052 | 10 | 1 | 0 | 0.61484 | 25.1469 | 200 | 25.1469 | 174.8531 | 200 | 0 | 0 | 57000 | 200 | 658913.2892 | 335.9569 | 0
7053 | 10 | 1 | 0 | 0.39106 | 15.9943 | 200 | 15.9943 | 180 | 195.9943 | 0 | 0 | 56800 | 195.9943 | 659109.2835 | 155.9569 | 0
7054 | 10 | 0 | 0 | 0.41043 | 16.7865 | 0 | 0 | 0 | 0 | 16.7865 | 0 | 56800 | 0 | 659109.2835 | 170.5075 | 0
7055 | 10 | 0 | 0 | 0.30531 | 12.4873 | 0 | 0 | 0 | 0 | 12.4873 | 0 | 56800 | 0 | 659109.2835 | 181.3314 | 0
7056 | 10 | 0 | 0 | 0.31105 | 12.7219 | 0 | 0 | 0 | 0 | 12.7219 | 0 | 56800 | 0 | 659109.2835 | 192.3588 | 0
7057 | 10 | 0 | 0 | 0.41184 | 16.8441 | 0 | 0 | 0 | 0 | 16.8441 | 0 | 56800 | 0 | 659109.2835 | 206.9593 | 0
7058 | 10 | 0 | 0 | 0.40466 | 16.5506 | 0 | 0 | 0 | 0 | 16.5506 | 0 | 56800 | 0 | 659109.2835 | 221.3053 | 0
7059 | 10 | 0 | 0 | 0.34471 | 14.0987 | 0 | 0 | 0 | 0 | 14.0987 | 0 | 56800 | 0 | 659109.2835 | 233.5261 | 0
7060 | 10 | 0 | 0 | 0.36528 | 14.9401 | 0 | 0 | 0 | 0 | 14.9401 | 0 | 56800 | 0 | 659109.2835 | 246.4761 | 0
7061 | 10 | 0 | 0 | 0.31623 | 12.9338 | 0 | 0 | 0 | 0 | 12.9338 | 0 | 56800 | 0 | 659109.2835 | 257.6872 | 0
7062 | 10 | 0 | 0 | 0.43475 | 17.7814 | 0 | 0 | 0 | 0 | 17.7814 | 0 | 56800 | 0 | 659109.2835 | 273.1001 | 0
7063 | 10 | 0 | 0 | 0.43856 | 17.9373 | 0 | 0 | 0 | 0 | 17.9373 | 0 | 56800 | 0 | 659109.2835 | 288.6481 | 0
7064 | 10 | 1 | 0.15887 | 0.43105 | 63.5115 | 200 | 63.5115 | 136.4885 | 200 | 0 | 0 | 56600 | 200 | 659309.2835 | 152.1596 | 0
7065 | 10 | 1 | 0.47798 | 0.50433 | 158.6689 | 200 | 158.6689 | 41.3311 | 200 | 0 | 0 | 56400 | 200 | 659509.2835 | 110.8285 | 0
7066 | 10 | 0 | 0.81413 | 0.36915 | 250.2183 | 0 | 0 | 0 | 0 | 180 | 70.2183 | 56400 | 70.2183 | 659579.5018 | 266.8525 | 0
7067 | 10 | 0 | 1 | 0.23557 | 298.4349 | 0 | 0 | 0 | 0 | 180 | 118.4349 | 56400 | 118.4349 | 659697.9367 | 422.8765 | 0
7068 | 10 | 0 | 1 | 0.19623 | 296.8259 | 0 | 0 | 0 | 0 | 101.4461 | 195.3799 | 56400 | 195.3799 | 659893.3166 | 510.81 | 0
7069 | 10 | 0 | 1 | 0.12234 | 293.8037 | 0 | 0 | 0 | 0 | 0 | 200 | 56400 | 200 | 660093.3166 | 510.81 | 93.8037
7070 | 10 | 0 | 1 | 0.09307 | 292.6066 | 0 | 0 | 0 | 0 | 0 | 200 | 56400 | 200 | 660293.3166 | 510.81 | 92.6066
7071 | 10 | 0 | 1 | 0.071654 | 291.7306 | 0 | 0 | 0 | 0 | 0 | 200 | 56400 | 200 | 660493.3166 | 510.81 | 91.7306
7072 | 10 | 0 | 0.81413 | 0.10477 | 239.4048 | 0 | 0 | 0 | 0 | 0 | 200 | 56400 | 200 | 660693.3166 | 510.81 | 39.4048
7073 | 10 | 0 | 0.47798 | 0.16277 | 144.699 | 0 | 0 | 0 | 0 | 0 | 144.699 | 56400 | 144.699 | 660838.0156 | 510.81 | 0
7074 | 10 | 0 | 0.15887 | 0.17317 | 52.9643 | 0 | 0 | 0 | 0 | 0 | 52.9643 | 56400 | 52.9643 | 660890.9799 | 510.81 | 0
7075 | 10 | 0 | 0 | 0.15342 | 6.275 | 0 | 0 | 0 | 0 | 0 | 6.275 | 56400 | 6.275 | 660897.2549 | 510.81 | 0
7076 | 10 | 1 | 0 | 0.13579 | 5.5537 | 200 | 5.5537 | 180 | 185.5537 | 0 | 0 | 56200 | 185.5537 | 661082.8086 | 330.81 | 0
7077 | 10 | 1 | 0 | 0.1319 | 5.3945 | 200 | 5.3945 | 180 | 185.3945 | 0 | 0 | 56000 | 185.3945 | 661268.2032 | 150.81 | 0
7078 | 10 | 0 | 0 | 0.10783 | 4.4102 | 0 | 0 | 0 | 0 | 4.4102 | 0 | 56000 | 0 | 661268.2032 | 154.6327 | 0
7079 | 10 | 0 | 0 | 0.10287 | 4.2072 | 0 | 0 | 0 | 0 | 4.2072 | 0 | 56000 | 0 | 661268.2032 | 158.2795 | 0
7080 | 10 | 0 | 0 | 0.088498 | 3.6196 | 0 | 0 | 0 | 0 | 3.6196 | 0 | 56000 | 0 | 661268.2032 | 161.417 | 0
7081 | 10 | 0 | 0 | 0.066135 | 2.7049 | 0 | 0 | 0 | 0 | 2.7049 | 0 | 56000 | 0 | 661268.2032 | 163.7616 | 0
7082 | 10 | 0 | 0 | 0.048421 | 1.9804 | 0 | 0 | 0 | 0 | 1.9804 | 0 | 56000 | 0 | 661268.2032 | 165.4782 | 0
7083 | 10 | 0 | 0 | 0.033215 | 1.3585 | 0 | 0 | 0 | 0 | 1.3585 | 0 | 56000 | 0 | 661268.2032 | 166.6558 | 0
7084 | 10 | 0 | 0 | 0.045268 | 1.8515 | 0 | 0 | 0 | 0 | 1.8515 | 0 | 56000 | 0 | 661268.2032 | 168.2606 | 0
7085 | 10 | 0 | 0 | 0.049623 | 2.0296 | 0 | 0 | 0 | 0 | 2.0296 | 0 | 56000 | 0 | 661268.2032 | 170.0199 | 0
7086 | 10 | 0 | 0 | 0.049204 | 2.0124 | 0 | 0 | 0 | 0 | 2.0124 | 0 | 56000 | 0 | 661268.2032 | 171.7643 | 0
7087 | 10 | 0 | 0 | 0.074546 | 3.0489 | 0 | 0 | 0 | 0 | 3.0489 | 0 | 56000 | 0 | 661268.2032 | 174.4071 | 0
7088 | 10 | 1 | 0.15469 | 0.06174 | 47.1988 | 200 | 47.1988 | 152.8012 | 200 | 0 | 0 | 55800 | 200 | 661468.2032 | 21.6058 | 0
7089 | 10 | 1 | 0.4654 | 0.067824 | 137.1815 | 200 | 137.1815 | 21.6058 | 158.7874 | 0 | 0 | 55600 | 158.7874 | 661626.9905 | 0 | 0
7090 | 10 | 0 | 0.79269 | 0.097882 | 232.9325 | 0 | 0 | 0 | 0 | 180 | 52.9325 | 55600 | 52.9325 | 661679.9231 | 156.024 | 0
7091 | 10 | 0 | 1 | 0.11302 | 293.4226 | 0 | 0 | 0 | 0 | 180 | 113.4226 | 55600 | 113.4226 | 661793.3456 | 312.048 | 0
7092 | 10 | 0 | 1 | 0.19804 | 296.8997 | 0 | 0 | 0 | 0 | 180 | 116.8997 | 55600 | 116.8997 | 661910.2453 | 468.072 | 0
7093 | 10 | 0 | 1 | 0.32738 | 302.1897 | 0 | 0 | 0 | 0 | 49.3055 | 200 | 55600 | 200 | 662110.2453 | 510.81 | 52.8842
7094 | 10 | 0 | 1 | 0.41343 | 305.7094 | 0 | 0 | 0 | 0 | 0 | 200 | 55600 | 200 | 662310.2453 | 510.81 | 105.7094
7095 | 10 | 0 | 1 | 0.5094 | 309.6347 | 0 | 0 | 0 | 0 | 0 | 200 | 55600 | 200 | 662510.2453 | 510.81 | 109.6347
7096 | 10 | 0 | 0.79269 | 0.52138 | 250.2536 | 0 | 0 | 0 | 0 | 0 | 200 | 55600 | 200 | 662710.2453 | 510.81 | 50.2536
7097 | 10 | 0 | 0.4654 | 0.36745 | 149.436 | 0 | 0 | 0 | 0 | 0 | 149.436 | 55600 | 149.436 | 662859.6813 | 510.81 | 0
7098 | 10 | 0 | 0.15469 | 0.38476 | 60.4103 | 0 | 0 | 0 | 0 | 0 | 60.4103 | 55600 | 60.4103 | 662920.0916 | 510.81 | 0
7099 | 10 | 0 | 0 | 0.53335 | 21.8139 | 0 | 0 | 0 | 0 | 0 | 21.8139 | 55600 | 21.8139 | 662941.9055 | 510.81 | 0
7100 | 10 | 1 | 0 | 0.32806 | 13.4175 | 200 | 13.4175 | 180 | 193.4175 | 0 | 0 | 55400 | 193.4175 | 663135.323 | 330.81 | 0
7101 | 10 | 1 | 0 | 0.35039 | 14.3308 | 200 | 14.3308 | 180 | 194.3308 | 0 | 0 | 55200 | 194.3308 | 663329.6538 | 150.81 | 0
7102 | 10 | 0 | 0 | 0.48522 | 19.8453 | 0 | 0 | 0 | 0 | 19.8453 | 0 | 55200 | 0 | 663329.6538 | 168.0119 | 0
7103 | 10 | 0 | 0 | 0.47965 | 19.6178 | 0 | 0 | 0 | 0 | 19.6178 | 0 | 55200 | 0 | 663329.6538 | 185.0166 | 0
7104 | 10 | 0 | 0 | 0.4591 | 18.7771 | 0 | 0 | 0 | 0 | 18.7771 | 0 | 55200 | 0 | 663329.6538 | 201.2925 | 0
7105 | 10 | 0 | 0 | 0.32584 | 13.3269 | 0 | 0 | 0 | 0 | 13.3269 | 0 | 55200 | 0 | 663329.6538 | 212.8443 | 0
7106 | 10 | 0 | 0 | 0.29667 | 12.1338 | 0 | 0 | 0 | 0 | 12.1338 | 0 | 55200 | 0 | 663329.6538 | 223.3619 | 0
7107 | 10 | 0 | 0 | 0.2098 | 8.581 | 0 | 0 | 0 | 0 | 8.581 | 0 | 55200 | 0 | 663329.6538 | 230.7999 | 0
7108 | 10 | 0 | 0 | 0.31825 | 13.0163 | 0 | 0 | 0 | 0 | 13.0163 | 0 | 55200 | 0 | 663329.6538 | 242.0824 | 0
7109 | 10 | 0 | 0 | 0.38499 | 15.7459 | 0 | 0 | 0 | 0 | 15.7459 | 0 | 55200 | 0 | 663329.6538 | 255.731 | 0
7110 | 10 | 0 | 0 | 0.56364 | 23.0528 | 0 | 0 | 0 | 0 | 23.0528 | 0 | 55200 | 0 | 663329.6538 | 275.7131 | 0
7111 | 10 | 0 | 0 | 0.4492 | 18.3724 | 0 | 0 | 0 | 0 | 18.3724 | 0 | 55200 | 0 | 663329.6538 | 291.6383 | 0
7112 | 10 | 1 | 0.18438 | 0.42066 | 70.4544 | 200 | 70.4544 | 129.5456 | 200 | 0 | 0 | 55000 | 200 | 663529.6538 | 162.0927 | 0
7113 | 10 | 1 | 0.55474 | 0.58196 | 184.0107 | 200 | 184.0107 | 15.9893 | 200 | 0 | 0 | 54800 | 200 | 663729.6538 | 146.1034 | 0
7114 | 10 | 0 | 0.94486 | 0.66512 | 300.0786 | 0 | 0 | 0 | 0 | 180 | 120.0786 | 54800 | 120.0786 | 663849.7324 | 302.1274 | 0
7115 | 10 | 0 | 1 | 0.84926 | 323.5346 | 0 | 0 | 0 | 0 | 180 | 143.5346 | 54800 | 143.5346 | 663993.267 | 458.1514 | 0
7116 | 10 | 0 | 1 | 0.69115 | 317.0681 | 0 | 0 | 0 | 0 | 60.7506 | 200 | 54800 | 200 | 664193.267 | 510.81 | 56.3174
7117 | 10 | 0 | 1 | 0.91154 | 326.0821 | 0 | 0 | 0 | 0 | 0 | 200 | 54800 | 200 | 664393.267 | 510.81 | 126.0821
7118 | 10 | 0 | 1 | 0.81814 | 322.2618 | 0 | 0 | 0 | 0 | 0 | 200 | 54800 | 200 | 664593.267 | 510.81 | 122.2618
7119 | 10 | 0 | 1 | 0.84478 | 323.3516 | 0 | 0 | 0 | 0 | 0 | 200 | 54800 | 200 | 664793.267 | 510.81 | 123.3516
7120 | 10 | 0 | 0.94486 | 0.84258 | 307.3368 | 0 | 0 | 0 | 0 | 0 | 200 | 54800 | 200 | 664993.267 | 510.81 | 107.3368
7121 | 10 | 0 | 0.55474 | 0.68306 | 188.1457 | 0 | 0 | 0 | 0 | 0 | 188.1457 | 54800 | 188.1457 | 665181.4128 | 510.81 | 0
7122 | 10 | 0 | 0.18438 | 0.61482 | 78.3957 | 0 | 0 | 0 | 0 | 0 | 78.3957 | 54800 | 78.3957 | 665259.8085 | 510.81 | 0
7123 | 10 | 0 | 0 | 0.78995 | 32.309 | 0 | 0 | 0 | 0 | 0 | 32.309 | 54800 | 32.309 | 665292.1175 | 510.81 | 0
7124 | 10 | 1 | 0 | 0.98515 | 40.2928 | 200 | 40.2928 | 159.7072 | 200 | 0 | 0 | 54600 | 200 | 665492.1175 | 351.1028 | 0
7125 | 10 | 1 | 0 | 0.83874 | 34.3045 | 200 | 34.3045 | 165.6955 | 200 | 0 | 0 | 54400 | 200 | 665692.1175 | 185.4073 | 0
7126 | 10 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 54400 | 0 | 665692.1175 | 220.8595 | 0
7127 | 10 | 0 | 0 | 0.7139 | 29.1985 | 0 | 0 | 0 | 0 | 29.1985 | 0 | 54400 | 0 | 665692.1175 | 246.1687 | 0
7128 | 10 | 0 | 0 | 0.44722 | 18.2913 | 0 | 0 | 0 | 0 | 18.2913 | 0 | 54400 | 0 | 665692.1175 | 262.0236 | 0
7129 | 10 | 0 | 0 | 0.51746 | 21.1643 | 0 | 0 | 0 | 0 | 21.1643 | 0 | 54400 | 0 | 665692.1175 | 280.3689 | 0
7130 | 10 | 0 | 0 | 0.40556 | 16.5873 | 0 | 0 | 0 | 0 | 16.5873 | 0 | 54400 | 0 | 665692.1175 | 294.7467 | 0
7131 | 10 | 0 | 0 | 0.38782 | 15.8617 | 0 | 0 | 0 | 0 | 15.8617 | 0 | 54400 | 0 | 665692.1175 | 308.4957 | 0
7132 | 10 | 0 | 0 | 0.48871 | 19.988 | 0 | 0 | 0 | 0 | 19.988 | 0 | 54400 | 0 | 665692.1175 | 325.8213 | 0
7133 | 10 | 0 | 0 | 0.44738 | 18.2979 | 0 | 0 | 0 | 0 | 18.2979 | 0 | 54400 | 0 | 665692.1175 | 341.6819 | 0
7134 | 10 | 0 | 0 | 0.36433 | 14.901 | 0 | 0 | 0 | 0 | 14.901 | 0 | 54400 | 0 | 665692.1175 | 354.5981 | 0
7135 | 10 | 0 | 0 | 0.40529 | 16.5763 | 0 | 0 | 0 | 0 | 16.5763 | 0 | 54400 | 0 | 665692.1175 | 368.9665 | 0
7136 | 10 | 1 | 0.16081 | 0.40143 | 62.861 | 200 | 62.861 | 137.139 | 200 | 0 | 0 | 54200 | 200 | 665892.1175 | 231.8274 | 0
7137 | 10 | 1 | 0.48383 | 0.30289 | 152.1175 | 200 | 152.1175 | 47.8825 | 200 | 0 | 0 | 54000 | 200 | 666092.1175 | 183.9449 | 0
7138 | 10 | 0 | 0.82408 | 0.4375 | 255.8873 | 0 | 0 | 0 | 0 | 180 | 75.8873 | 54000 | 75.8873 | 666168.0048 | 339.9689 | 0
7139 | 10 | 0 | 1 | 0.36237 | 303.6208 | 0 | 0 | 0 | 0 | 180 | 123.6208 | 54000 | 123.6208 | 666291.6256 | 495.9929 | 0
7140 | 10 | 0 | 1 | 0.34722 | 303.0014 | 0 | 0 | 0 | 0 | 17.094 | 200 | 54000 | 200 | 666491.6256 | 510.81 | 85.9074
7141 | 10 | 0 | 1 | 0.3808 | 304.3746 | 0 | 0 | 0 | 0 | 0 | 200 | 54000 | 200 | 666691.6256 | 510.81 | 104.3746
7142 | 10 | 0 | 1 | 0.38576 | 304.5775 | 0 | 0 | 0 | 0 | 0 | 200 | 54000 | 200 | 666891.6256 | 510.81 | 104.5775
7143 | 10 | 0 | 1 | 0.37499 | 304.137 | 0 | 0 | 0 | 0 | 0 | 200 | 54000 | 200 | 667091.6256 | 510.81 | 104.137
7144 | 10 | 0 | 0.82408 | 0.31443 | 250.8537 | 0 | 0 | 0 | 0 | 0 | 200 | 54000 | 200 | 667291.6256 | 510.81 | 50.8537
7145 | 10 | 0 | 0.48383 | 0.33649 | 153.4918 | 0 | 0 | 0 | 0 | 0 | 153.4918 | 54000 | 153.4918 | 667445.1174 | 510.81 | 0
7146 | 10 | 0 | 0.16081 | 0.23234 | 55.9453 | 0 | 0 | 0 | 0 | 0 | 55.9453 | 54000 | 55.9453 | 667501.0627 | 510.81 | 0
7147 | 10 | 0 | 0 | 0.21079 | 8.6215 | 0 | 0 | 0 | 0 | 0 | 8.6215 | 54000 | 8.6215 | 667509.6841 | 510.81 | 0
7148 | 10 | 1 | 0 | 0.19265 | 7.8795 | 200 | 7.8795 | 180 | 187.8795 | 0 | 0 | 53800 | 187.8795 | 667697.5637 | 330.81 | 0
7149 | 10 | 1 | 0 | 0.2545 | 10.4091 | 200 | 10.4091 | 180 | 190.4091 | 0 | 0 | 53600 | 190.4091 | 667887.9727 | 150.81 | 0
7150 | 10 | 0 | 0 | 0.17232 | 7.0478 | 0 | 0 | 0 | 0 | 7.0478 | 0 | 53600 | 0 | 667887.9727 | 156.9191 | 0
7151 | 10 | 0 | 0 | 0.12969 | 5.3043 | 0 | 0 | 0 | 0 | 5.3043 | 0 | 53600 | 0 | 667887.9727 | 161.5168 | 0
7152 | 10 | 0 | 0 | 0.14825 | 6.0635 | 0 | 0 | 0 | 0 | 6.0635 | 0 | 53600 | 0 | 667887.9727 | 166.7726 | 0
7153 | 10 | 0 | 0 | 0.21269 | 8.699 | 0 | 0 | 0 | 0 | 8.699 | 0 | 53600 | 0 | 667887.9727 | 174.3129 | 0
7154 | 10 | 0 | 0 | 0.30976 | 12.6693 | 0 | 0 | 0 | 0 | 12.6693 | 0 | 53600 | 0 | 667887.9727 | 185.2947 | 0
7155 | 10 | 0 | 0 | 0.32623 | 13.3427 | 0 | 0 | 0 | 0 | 13.3427 | 0 | 53600 | 0 | 667887.9727 | 196.8601 | 0
7156 | 10 | 0 | 0 | 0.27963 | 11.4367 | 0 | 0 | 0 | 0 | 11.4367 | 0 | 53600 | 0 | 667887.9727 | 206.7734 | 0
7157 | 10 | 0 | 0 | 0.3053 | 12.4868 | 0 | 0 | 0 | 0 | 12.4868 | 0 | 53600 | 0 | 667887.9727 | 217.597 | 0
7158 | 10 | 0 | 0 | 0.30652 | 12.5366 | 0 | 0 | 0 | 0 | 12.5366 | 0 | 53600 | 0 | 667887.9727 | 228.4637 | 0
7159 | 10 | 0 | 0 | 0.45189 | 18.4823 | 0 | 0 | 0 | 0 | 18.4823 | 0 | 53600 | 0 | 667887.9727 | 244.4842 | 0
7160 | 10 | 1 | 0.15678 | 0.44853 | 63.6234 | 200 | 63.6234 | 136.3766 | 200 | 0 | 0 | 53400 | 200 | 668087.9727 | 108.1076 | 0
7161 | 10 | 1 | 0.4717 | 0.60816 | 161.1012 | 200 | 161.1012 | 38.8988 | 200 | 0 | 0 | 53200 | 200 | 668287.9727 | 69.2088 | 0
7162 | 10 | 0 | 0.80342 | 0.58322 | 255.883 | 0 | 0 | 0 | 0 | 180 | 75.883 | 53200 | 75.883 | 668363.8557 | 225.2328 | 0
7163 | 10 | 0 | 1 | 0.52539 | 310.2884 | 0 | 0 | 0 | 0 | 180 | 130.2884 | 53200 | 130.2884 | 668494.1442 | 381.2568 | 0
7164 | 10 | 0 | 1 | 0.5417 | 310.9554 | 0 | 0 | 0 | 0 | 149.4615 | 161.4939 | 53200 | 161.4939 | 668655.638 | 510.81 | 0
7165 | 10 | 0 | 1 | 0.76116 | 319.9314 | 0 | 0 | 0 | 0 | 0 | 200 | 53200 | 200 | 668855.638 | 510.81 | 119.9314
7166 | 10 | 0 | 1 | 0.51883 | 310.0202 | 0 | 0 | 0 | 0 | 0 | 200 | 53200 | 200 | 669055.638 | 510.81 | 110.0202
7167 | 10 | 0 | 1 | 0.65573 | 315.6195 | 0 | 0 | 0 | 0 | 0 | 200 | 53200 | 200 | 669255.638 | 510.81 | 115.6195
7168 | 10 | 0 | 0.80342 | 0.43368 | 249.7668 | 0 | 0 | 0 | 0 | 0 | 200 | 53200 | 200 | 669455.638 | 510.81 | 49.7668
7169 | 10 | 0 | 0.4717 | 0.46027 | 155.0525 | 0 | 0 | 0 | 0 | 0 | 155.0525 | 53200 | 155.0525 | 669610.6905 | 510.81 | 0
7170 | 10 | 0 | 0.15678 | 0.37426 | 60.5858 | 0 | 0 | 0 | 0 | 0 | 60.5858 | 53200 | 60.5858 | 669671.2763 | 510.81 | 0
7171 | 10 | 0 | 0 | 0.30348 | 12.4123 | 0 | 0 | 0 | 0 | 0 | 12.4123 | 53200 | 12.4123 | 669683.6886 | 510.81 | 0
7172 | 10 | 1 | 0 | 0.33316 | 13.6261 | 200 | 13.6261 | 180 | 193.6261 | 0 | 0 | 53000 | 193.6261 | 669877.3146 | 330.81 | 0
7173 | 10 | 1 | 0 | 0.35028 | 14.3264 | 200 | 14.3264 | 180 | 194.3264 | 0 | 0 | 52800 | 194.3264 | 670071.6411 | 150.81 | 0
7174 | 10 | 0 | 0 | 0.33463 | 13.6863 | 0 | 0 | 0 | 0 | 13.6863 | 0 | 52800 | 0 | 670071.6411 | 162.6733 | 0
7175 | 10 | 0 | 0 | 0.23319 | 9.5373 | 0 | 0 | 0 | 0 | 9.5373 | 0 | 52800 | 0 | 670071.6411 | 170.9403 | 0
7176 | 10 | 0 | 0 | 0.27677 | 11.3199 | 0 | 0 | 0 | 0 | 11.3199 | 0 | 52800 | 0 | 670071.6411 | 180.7523 | 0
7177 | 10 | 0 | 0 | 0.26927 | 11.0132 | 0 | 0 | 0 | 0 | 11.0132 | 0 | 52800 | 0 | 670071.6411 | 190.2986 | 0
7178 | 10 | 0 | 0 | 0.31335 | 12.8159 | 0 | 0 | 0 | 0 | 12.8159 | 0 | 52800 | 0 | 670071.6411 | 201.4074 | 0
7179 | 10 | 0 | 0 | 0.22539 | 9.2185 | 0 | 0 | 0 | 0 | 9.2185 | 0 | 52800 | 0 | 670071.6411 | 209.398 | 0
7180 | 10 | 0 | 0 | 0.19768 | 8.0849 | 0 | 0 | 0 | 0 | 8.0849 | 0 | 52800 | 0 | 670071.6411 | 216.4061 | 0
7181 | 10 | 0 | 0 | 0.28071 | 11.481 | 0 | 0 | 0 | 0 | 11.481 | 0 | 52800 | 0 | 670071.6411 | 226.3578 | 0
7182 | 10 | 0 | 0 | 0.25052 | 10.2464 | 0 | 0 | 0 | 0 | 10.2464 | 0 | 52800 | 0 | 670071.6411 | 235.2394 | 0
7183 | 10 | 0 | 0 | 0.39787 | 16.2729 | 0 | 0 | 0 | 0 | 16.2729 | 0 | 52800 | 0 | 670071.6411 | 249.3447 | 0
7184 | 10 | 1 | 0.16259 | 0.49865 | 67.3514 | 200 | 67.3514 | 132.6486 | 200 | 0 | 0 | 52600 | 200 | 670271.6411 | 116.6961 | 0
7185 | 10 | 1 | 0.48918 | 0.51735 | 162.435 | 200 | 162.435 | 37.565 | 200 | 0 | 0 | 52400 | 200 | 670471.6411 | 79.1311 | 0
7186 | 10 | 0 | 0.8332 | 0.61612 | 265.8262 | 0 | 0 | 0 | 0 | 180 | 85.8262 | 52400 | 85.8262 | 670557.4672 | 235.1551 | 0
7187 | 10 | 0 | 1 | 0.46812 | 307.946 | 0 | 0 | 0 | 0 | 180 | 127.946 | 52400 | 127.946 | 670685.4132 | 391.1791 | 0
7188 | 10 | 0 | 1 | 0.48487 | 308.631 | 0 | 0 | 0 | 0 | 138.0145 | 170.6165 | 52400 | 170.6165 | 670856.0298 | 510.81 | 0
7189 | 10 | 0 | 1 | 0.55007 | 311.2978 | 0 | 0 | 0 | 0 | 0 | 200 | 52400 | 200 | 671056.0298 | 510.81 | 111.2978
7190 | 10 | 0 | 1 | 0.59791 | 313.2543 | 0 | 0 | 0 | 0 | 0 | 200 | 52400 | 200 | 671256.0298 | 510.81 | 113.2543
7191 | 10 | 0 | 1 | 0.50229 | 309.3438 | 0 | 0 | 0 | 0 | 0 | 200 | 52400 | 200 | 671456.0298 | 510.81 | 109.3438
7192 | 10 | 0 | 0.8332 | 0.6199 | 265.981 | 0 | 0 | 0 | 0 | 0 | 200 | 52400 | 200 | 671656.0298 | 510.81 | 65.981
7193 | 10 | 0 | 0.48918 | 0.77196 | 172.8485 | 0 | 0 | 0 | 0 | 0 | 172.8485 | 52400 | 172.8485 | 671828.8783 | 510.81 | 0
7194 | 10 | 0 | 0.16259 | 0.69125 | 75.2289 | 0 | 0 | 0 | 0 | 0 | 75.2289 | 52400 | 75.2289 | 671904.1071 | 510.81 | 0
7195 | 10 | 0 | 0 | 0.84548 | 34.5803 | 0 | 0 | 0 | 0 | 0 | 34.5803 | 52400 | 34.5803 | 671938.6874 | 510.81 | 0
7196 | 10 | 1 | 0 | 1 | 40.9 | 200 | 40.9 | 159.1 | 200 | 0 | 0 | 52200 | 200 | 672138.6874 | 351.71 | 0
7197 | 10 | 1 | 0 | 0.7099 | 29.0347 | 200 | 29.0347 | 170.9653 | 200 | 0 | 0 | 52000 | 200 | 672338.6874 | 180.7447 | 0
7198 | 10 | 0 | 0 | 0.57206 | 23.3972 | 0 | 0 | 0 | 0 | 23.3972 | 0 | 52000 | 0 | 672338.6874 | 201.0254 | 0
7199 | 10 | 0 | 0 | 0.58907 | 24.0929 | 0 | 0 | 0 | 0 | 24.0929 | 0 | 52000 | 0 | 672338.6874 | 221.9091 | 0
7200 | 10 | 0 | 0 | 0.65106 | 26.6281 | 0 | 0 | 0 | 0 | 26.6281 | 0 | 52000 | 0 | 672338.6874 | 244.9904 | 0
7201 | 10 | 0 | 0 | 0.54964 | 22.4802 | 0 | 0 | 0 | 0 | 22.4802 | 0 | 52000 | 0 | 672338.6874 | 264.4762 | 0
7202 | 10 | 0 | 0 | 0.57277 | 23.4261 | 0 | 0 | 0 | 0 | 23.4261 | 0 | 52000 | 0 | 672338.6874 | 284.7819 | 0
7203 | 10 | 0 | 0 | 0.39937 | 16.3341 | 0 | 0 | 0 | 0 | 16.3341 | 0 | 52000 | 0 | 672338.6874 | 298.9403 | 0
7204 | 10 | 0 | 0 | 0.58421 | 23.8944 | 0 | 0 | 0 | 0 | 23.8944 | 0 | 52000 | 0 | 672338.6874 | 319.652 | 0
7205 | 10 | 0 | 0 | 0.22006 | 9.0005 | 0 | 0 | 0 | 0 | 9.0005 | 0 | 52000 | 0 | 672338.6874 | 327.4536 | 0
7206 | 10 | 0 | 0 | 0.21688 | 8.8704 | 0 | 0 | 0 | 0 | 8.8704 | 0 | 52000 | 0 | 672338.6874 | 335.1424 | 0
7207 | 10 | 0 | 0 | 0.25655 | 10.4929 | 0 | 0 | 0 | 0 | 10.4929 | 0 | 52000 | 0 | 672338.6874 | 344.2377 | 0
7208 | 10 | 1 | 0.16 | 0.23431 | 55.7921 | 200 | 55.7921 | 144.2079 | 200 | 0 | 0 | 51800 | 200 | 672538.6874 | 200.0298 | 0
7209 | 10 | 1 | 0.48139 | 0.15309 | 145.2869 | 200 | 145.2869 | 54.7131 | 200 | 0 | 0 | 51600 | 200 | 672738.6874 | 145.3166 | 0
7210 | 10 | 0 | 0.81993 | 0.12622 | 241.9575 | 0 | 0 | 0 | 0 | 180 | 61.9575 | 51600 | 61.9575 | 672800.6449 | 301.3406 | 0
7211 | 10 | 0 | 1 | 0.13268 | 294.2265 | 0 | 0 | 0 | 0 | 180 | 114.2265 | 51600 | 114.2265 | 672914.8714 | 457.3646 | 0
7212 | 10 | 0 | 1 | 0.15483 | 295.1325 | 0 | 0 | 0 | 0 | 61.6582 | 200 | 51600 | 200 | 673114.8714 | 510.81 | 33.4743
7213 | 10 | 0 | 1 | 0.12732 | 294.0073 | 0 | 0 | 0 | 0 | 0 | 200 | 51600 | 200 | 673314.8714 | 510.81 | 94.0073
7214 | 10 | 0 | 1 | 0.11611 | 293.5489 | 0 | 0 | 0 | 0 | 0 | 200 | 51600 | 200 | 673514.8714 | 510.81 | 93.5489
7215 | 10 | 0 | 1 | 0.10798 | 293.2165 | 0 | 0 | 0 | 0 | 0 | 200 | 51600 | 200 | 673714.8714 | 510.81 | 93.2165
7216 | 10 | 0 | 0.81993 | 0.082451 | 240.1672 | 0 | 0 | 0 | 0 | 0 | 200 | 51600 | 200 | 673914.8714 | 510.81 | 40.1672
7217 | 10 | 0 | 0.48139 | 0.079246 | 142.2666 | 0 | 0 | 0 | 0 | 0 | 142.2666 | 51600 | 142.2666 | 674057.138 | 510.81 | 0
7218 | 10 | 0 | 0.16 | 0.088659 | 49.8347 | 0 | 0 | 0 | 0 | 0 | 49.8347 | 51600 | 49.8347 | 674106.9727 | 510.81 | 0
7219 | 10 | 0 | 0 | 0.11063 | 4.5246 | 0 | 0 | 0 | 0 | 0 | 4.5246 | 51600 | 4.5246 | 674111.4974 | 510.81 | 0
7220 | 10 | 1 | 0 | 0.114 | 4.6628 | 200 | 4.6628 | 180 | 184.6628 | 0 | 0 | 51400 | 184.6628 | 674296.1601 | 330.81 | 0
7221 | 10 | 1 | 0 | 0.091407 | 3.7385 | 200 | 3.7385 | 180 | 183.7385 | 0 | 0 | 51200 | 183.7385 | 674479.8987 | 150.81 | 0
7222 | 10 | 0 | 0 | 0.10392 | 4.2502 | 0 | 0 | 0 | 0 | 4.2502 | 0 | 51200 | 0 | 674479.8987 | 154.4941 | 0
7223 | 10 | 0 | 0 | 0.13685 | 5.5972 | 0 | 0 | 0 | 0 | 5.5972 | 0 | 51200 | 0 | 674479.8987 | 159.3458 | 0
7224 | 10 | 0 | 0 | 0.12927 | 5.2873 | 0 | 0 | 0 | 0 | 5.2873 | 0 | 51200 | 0 | 674479.8987 | 163.9288 | 0
7225 | 10 | 0 | 0 | 0.14307 | 5.8515 | 0 | 0 | 0 | 0 | 5.8515 | 0 | 51200 | 0 | 674479.8987 | 169.0009 | 0
7226 | 10 | 0 | 0 | 0.1567 | 6.409 | 0 | 0 | 0 | 0 | 6.409 | 0 | 51200 | 0 | 674479.8987 | 174.5562 | 0
7227 | 10 | 0 | 0 | 0.21741 | 8.8919 | 0 | 0 | 0 | 0 | 8.8919 | 0 | 51200 | 0 | 674479.8987 | 182.2637 | 0
7228 | 10 | 0 | 0 | 0.14981 | 6.1271 | 0 | 0 | 0 | 0 | 6.1271 | 0 | 51200 | 0 | 674479.8987 | 187.5747 | 0
7229 | 10 | 0 | 0 | 0.12698 | 5.1934 | 0 | 0 | 0 | 0 | 5.1934 | 0 | 51200 | 0 | 674479.8987 | 192.0763 | 0
7230 | 10 | 0 | 0 | 0.14349 | 5.8689 | 0 | 0 | 0 | 0 | 5.8689 | 0 | 51200 | 0 | 674479.8987 | 197.1635 | 0
7231 | 10 | 0 | 0 | 0.13546 | 5.5404 | 0 | 0 | 0 | 0 | 5.5404 | 0 | 51200 | 0 | 674479.8987 | 201.9659 | 0
7232 | 10 | 1 | 0.13726 | 0.1303 | 44.9707 | 200 | 44.9707 | 155.0293 | 200 | 0 | 0 | 51000 | 200 | 674679.8987 | 46.9366 | 0
7233 | 10 | 1 | 0.41298 | 0.2111 | 127.9016 | 200 | 127.9016 | 46.9366 | 174.8382 | 0 | 0 | 50800 | 174.8382 | 674854.7369 | 0 | 0
7234 | 10 | 0 | 0.7034 | 0.25603 | 213.6139 | 0 | 0 | 0 | 0 | 180 | 33.6139 | 50800 | 33.6139 | 674888.3508 | 156.024 | 0
7235 | 10 | 0 | 0.95252 | 0.22357 | 284.2324 | 0 | 0 | 0 | 0 | 180 | 104.2324 | 50800 | 104.2324 | 674992.5832 | 312.048 | 0
7236 | 10 | 0 | 1 | 0.16186 | 295.42 | 0 | 0 | 0 | 0 | 180 | 115.42 | 50800 | 115.42 | 675108.0032 | 468.072 | 0
7237 | 10 | 0 | 1 | 0.22767 | 298.1118 | 0 | 0 | 0 | 0 | 49.3055 | 200 | 50800 | 200 | 675308.0032 | 510.81 | 48.8063
7238 | 10 | 0 | 1 | 0.28135 | 300.3073 | 0 | 0 | 0 | 0 | 0 | 200 | 50800 | 200 | 675508.0032 | 510.81 | 100.3073
7239 | 10 | 0 | 0.95252 | 0.18743 | 282.7542 | 0 | 0 | 0 | 0 | 0 | 200 | 50800 | 200 | 675708.0032 | 510.81 | 82.7542
7240 | 10 | 0 | 0.7034 | 0.21121 | 211.7808 | 0 | 0 | 0 | 0 | 0 | 200 | 50800 | 200 | 675908.0032 | 510.81 | 11.7808
7241 | 10 | 0 | 0.41298 | 0.20005 | 127.4497 | 0 | 0 | 0 | 0 | 0 | 127.4497 | 50800 | 127.4497 | 676035.4528 | 510.81 | 0
7242 | 10 | 0 | 0.13726 | 0.2943 | 51.6783 | 0 | 0 | 0 | 0 | 0 | 51.6783 | 50800 | 51.6783 | 676087.1311 | 510.81 | 0
7243 | 10 | 0 | 0 | 0.33582 | 13.7352 | 0 | 0 | 0 | 0 | 0 | 13.7352 | 50800 | 13.7352 | 676100.8664 | 510.81 | 0
7244 | 10 | 1 | 0 | 0.23238 | 9.5043 | 200 | 9.5043 | 180 | 189.5043 | 0 | 0 | 50600 | 189.5043 | 676290.3707 | 330.81 | 0
7245 | 10 | 1 | 0 | 0.10896 | 4.4566 | 200 | 4.4566 | 180 | 184.4566 | 0 | 0 | 50400 | 184.4566 | 676474.8273 | 150.81 | 0
7246 | 10 | 0 | 0 | 0.15471 | 6.3278 | 0 | 0 | 0 | 0 | 6.3278 | 0 | 50400 | 0 | 676474.8273 | 156.295 | 0
7247 | 10 | 0 | 0 | 0.20528 | 8.3957 | 0 | 0 | 0 | 0 | 8.3957 | 0 | 50400 | 0 | 676474.8273 | 163.5724 | 0
7248 | 10 | 0 | 0 | 0.22386 | 9.156 | 0 | 0 | 0 | 0 | 9.156 | 0 | 50400 | 0 | 676474.8273 | 171.5089 | 0
7249 | 10 | 0 | 0 | 0.18989 | 7.7665 | 0 | 0 | 0 | 0 | 7.7665 | 0 | 50400 | 0 | 676474.8273 | 178.2408 | 0
7250 | 10 | 0 | 0 | 0.19704 | 8.0591 | 0 | 0 | 0 | 0 | 8.0591 | 0 | 50400 | 0 | 676474.8273 | 185.2264 | 0
7251 | 10 | 0 | 0 | 0.14558 | 5.9541 | 0 | 0 | 0 | 0 | 5.9541 | 0 | 50400 | 0 | 676474.8273 | 190.3874 | 0
7252 | 10 | 0 | 0 | 0.169 | 6.9121 | 0 | 0 | 0 | 0 | 6.9121 | 0 | 50400 | 0 | 676474.8273 | 196.3789 | 0
7253 | 10 | 0 | 0 | 0.21639 | 8.8503 | 0 | 0 | 0 | 0 | 8.8503 | 0 | 50400 | 0 | 676474.8273 | 204.0503 | 0
7254 | 10 | 0 | 0 | 0.2926 | 11.9675 | 0 | 0 | 0 | 0 | 11.9675 | 0 | 50400 | 0 | 676474.8273 | 214.4237 | 0
7255 | 10 | 0 | 0 | 0.32058 | 13.1116 | 0 | 0 | 0 | 0 | 13.1116 | 0 | 50400 | 0 | 676474.8273 | 225.7889 | 0
7256 | 10 | 1 | 0.13967 | 0.38706 | 56.1691 | 200 | 56.1691 | 143.8309 | 200 | 0 | 0 | 50200 | 200 | 676674.8273 | 81.958 | 0
7257 | 10 | 1 | 0.42023 | 0.43851 | 139.2982 | 200 | 139.2982 | 60.7018 | 200 | 0 | 0 | 50000 | 200 | 676874.8273 | 21.2562 | 0
7258 | 10 | 0 | 0.71576 | 0.89125 | 243.1635 | 0 | 0 | 0 | 0 | 180 | 63.1635 | 50000 | 63.1635 | 676937.9908 | 177.2802 | 0
7259 | 10 | 0 | 0.96926 | 1 | 320.8214 | 0 | 0 | 0 | 0 | 180 | 140.8214 | 50000 | 140.8214 | 677078.8122 | 333.3042 | 0
7260 | 10 | 0 | 1 | 0.92318 | 326.5579 | 0 | 0 | 0 | 0 | 180 | 146.5579 | 50000 | 146.5579 | 677225.3701 | 489.3282 | 0
7261 | 10 | 0 | 1 | 0.67631 | 316.4613 | 0 | 0 | 0 | 0 | 24.7829 | 200 | 50000 | 200 | 677425.3701 | 510.81 | 91.6784
7262 | 10 | 0 | 1 | 0.59508 | 313.1388 | 0 | 0 | 0 | 0 | 0 | 200 | 50000 | 200 | 677625.3701 | 510.81 | 113.1388
7263 | 10 | 0 | 0.96926 | 0.32876 | 293.3676 | 0 | 0 | 0 | 0 | 0 | 200 | 50000 | 200 | 677825.3701 | 510.81 | 93.3676
7264 | 10 | 0 | 0.71576 | 0.29589 | 218.8136 | 0 | 0 | 0 | 0 | 0 | 200 | 50000 | 200 | 678025.3701 | 510.81 | 18.8136
7265 | 10 | 0 | 0.42023 | 0.31562 | 134.2717 | 0 | 0 | 0 | 0 | 0 | 134.2717 | 50000 | 134.2717 | 678159.6418 | 510.81 | 0
7266 | 10 | 0 | 0.13967 | 0.3821 | 55.9659 | 0 | 0 | 0 | 0 | 0 | 55.9659 | 50000 | 55.9659 | 678215.6077 | 510.81 | 0
7267 | 10 | 0 | 0 | 0.40074 | 16.3901 | 0 | 0 | 0 | 0 | 0 | 16.3901 | 50000 | 16.3901 | 678231.9978 | 510.81 | 0
7268 | 10 | 1 | 0 | 0.71236 | 29.1355 | 200 | 29.1355 | 170.8645 | 200 | 0 | 0 | 49800 | 200 | 678431.9978 | 339.9455 | 0
7269 | 10 | 1 | 0 | 0.64168 | 26.2449 | 200 | 26.2449 | 173.7551 | 200 | 0 | 0 | 49600 | 200 | 678631.9978 | 166.1904 | 0
7270 | 10 | 0 | 0 | 0.85665 | 35.037 | 0 | 0 | 0 | 0 | 35.037 | 0 | 49600 | 0 | 678631.9978 | 196.5604 | 0
7271 | 10 | 0 | 0 | 0.83716 | 34.2397 | 0 | 0 | 0 | 0 | 34.2397 | 0 | 49600 | 0 | 678631.9978 | 226.2394 | 0
7272 | 10 | 0 | 0 | 0.60718 | 24.8337 | 0 | 0 | 0 | 0 | 24.8337 | 0 | 49600 | 0 | 678631.9978 | 247.7653 | 0
7273 | 10 | 0 | 0 | 0.35096 | 14.3541 | 0 | 0 | 0 | 0 | 14.3541 | 0 | 49600 | 0 | 678631.9978 | 260.2074 | 0
7274 | 10 | 0 | 0 | 0.32076 | 13.119 | 0 | 0 | 0 | 0 | 13.119 | 0 | 49600 | 0 | 678631.9978 | 271.5789 | 0
7275 | 10 | 0 | 0 | 0.24969 | 10.2125 | 0 | 0 | 0 | 0 | 10.2125 | 0 | 49600 | 0 | 678631.9978 | 280.4311 | 0
7276 | 10 | 0 | 0 | 0.34693 | 14.1894 | 0 | 0 | 0 | 0 | 14.1894 | 0 | 49600 | 0 | 678631.9978 | 292.7305 | 0
7277 | 10 | 0 | 0 | 0.34019 | 13.9136 | 0 | 0 | 0 | 0 | 13.9136 | 0 | 49600 | 0 | 678631.9978 | 304.7908 | 0
7278 | 10 | 0 | 0 | 0.27398 | 11.2056 | 0 | 0 | 0 | 0 | 11.2056 | 0 | 49600 | 0 | 678631.9978 | 314.5038 | 0
7279 | 10 | 0 | 0 | 0.30526 | 12.4852 | 0 | 0 | 0 | 0 | 12.4852 | 0 | 49600 | 0 | 678631.9978 | 325.326 | 0
7280 | 10 | 1 | 0.14995 | 0.32939 | 56.777 | 200 | 56.777 | 143.223 | 200 | 0 | 0 | 49400 | 200 | 678831.9978 | 182.103 | 0
7281 | 10 | 1 | 0.45114 | 0.29456 | 142.337 | 200 | 142.337 | 57.663 | 200 | 0 | 0 | 49200 | 200 | 679031.9978 | 124.44 | 0
7282 | 10 | 0 | 0.76841 | 0.3454 | 236.0423 | 0 | 0 | 0 | 0 | 180 | 56.0423 | 49200 | 56.0423 | 679088.0401 | 280.464 | 0
7283 | 10 | 0 | 1 | 0.63579 | 314.8039 | 0 | 0 | 0 | 0 | 180 | 134.8039 | 49200 | 134.8039 | 679222.8439 | 436.488 | 0
7284 | 10 | 0 | 1 | 0.87186 | 324.4592 | 0 | 0 | 0 | 0 | 85.743 | 200 | 49200 | 200 | 679422.8439 | 510.81 | 38.7162
7285 | 10 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 0 | 200 | 49200 | 200 | 679622.8439 | 510.81 | 129.7
7286 | 10 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 0 | 200 | 49200 | 200 | 679822.8439 | 510.81 | 129.7
7287 | 10 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 0 | 200 | 49200 | 200 | 680022.8439 | 510.81 | 129.7
7288 | 10 | 0 | 0.76841 | 0.94366 | 260.5109 | 0 | 0 | 0 | 0 | 0 | 200 | 49200 | 200 | 680222.8439 | 510.81 | 60.5109
7289 | 10 | 0 | 0.45114 | 0.67126 | 157.7442 | 0 | 0 | 0 | 0 | 0 | 157.7442 | 49200 | 157.7442 | 680380.5882 | 510.81 | 0
7290 | 10 | 0 | 0.14995 | 0.79173 | 75.6868 | 0 | 0 | 0 | 0 | 0 | 75.6868 | 49200 | 75.6868 | 680456.2749 | 510.81 | 0
7291 | 10 | 0 | 0 | 0.44784 | 18.3168 | 0 | 0 | 0 | 0 | 0 | 18.3168 | 49200 | 18.3168 | 680474.5918 | 510.81 | 0
7292 | 10 | 1 | 0 | 0.40009 | 16.3637 | 200 | 16.3637 | 180 | 196.3637 | 0 | 0 | 49000 | 196.3637 | 680670.9555 | 330.81 | 0
7293 | 10 | 1 | 0 | 0.26239 | 10.7317 | 200 | 10.7317 | 180 | 190.7317 | 0 | 0 | 48800 | 190.7317 | 680861.6872 | 150.81 | 0
7294 | 10 | 0 | 0 | 0.1392 | 5.6933 | 0 | 0 | 0 | 0 | 5.6933 | 0 | 48800 | 0 | 680861.6872 | 155.745 | 0
7295 | 10 | 0 | 0 | 0.16406 | 6.7103 | 0 | 0 | 0 | 0 | 6.7103 | 0 | 48800 | 0 | 680861.6872 | 161.5614 | 0
7296 | 10 | 0 | 0 | 0.15284 | 6.2511 | 0 | 0 | 0 | 0 | 6.2511 | 0 | 48800 | 0 | 680861.6872 | 166.9799 | 0
7297 | 11 | 0 | 0 | 0.10271 | 4.2006 | 0 | 0 | 0 | 0 | 4.2006 | 0 | 48800 | 0 | 680861.6872 | 170.621 | 0
7298 | 11 | 0 | 0 | 0.077925 | 3.1871 | 0 | 0 | 0 | 0 | 3.1871 | 0 | 48800 | 0 | 680861.6872 | 173.3836 | 0
7299 | 11 | 0 | 0 | 0.092586 | 3.7868 | 0 | 0 | 0 | 0 | 3.7868 | 0 | 48800 | 0 | 680861.6872 | 176.6659 | 0
7300 | 11 | 0 | 0 | 0.16167 | 6.6122 | 0 | 0 | 0 | 0 | 6.6122 | 0 | 48800 | 0 | 680861.6872 | 182.3974 | 0
7301 | 11 | 0 | 0 | 0.1559 | 6.3761 | 0 | 0 | 0 | 0 | 6.3761 | 0 | 48800 | 0 | 680861.6872 | 187.9242 | 0
7302 | 11 | 0 | 0 | 0.17 | 6.9529 | 0 | 0 | 0 | 0 | 6.9529 | 0 | 48800 | 0 | 680861.6872 | 193.951 | 0
7303 | 11 | 0 | 0 | 0.2222 | 9.0881 | 0 | 0 | 0 | 0 | 9.0881 | 0 | 48800 | 0 | 680861.6872 | 201.8286 | 0
7304 | 11 | 1 | 0.08065 | 0.31136 | 36.0263 | 200 | 36.0263 | 163.9737 | 200 | 0 | 0 | 48600 | 200 | 681061.6872 | 37.8549 | 0
7305 | 11 | 1 | 0.37765 | 0.40415 | 125.5955 | 200 | 125.5955 | 37.8549 | 163.4504 | 0 | 0 | 48400 | 163.4504 | 681225.1376 | 0 | 0
7306 | 11 | 0 | 0.71158 | 0.53425 | 227.3551 | 0 | 0 | 0 | 0 | 180 | 47.3551 | 48400 | 47.3551 | 681272.4927 | 156.024 | 0
7307 | 11 | 0 | 1 | 0.31146 | 301.5388 | 0 | 0 | 0 | 0 | 180 | 121.5388 | 48400 | 121.5388 | 681394.0315 | 312.048 | 0
7308 | 11 | 0 | 1 | 0.27857 | 300.1933 | 0 | 0 | 0 | 0 | 180 | 120.1933 | 48400 | 120.1933 | 681514.2249 | 468.072 | 0
7309 | 11 | 0 | 1 | 0.23728 | 298.5048 | 0 | 0 | 0 | 0 | 49.3055 | 200 | 48400 | 200 | 681714.2249 | 510.81 | 49.1993
7310 | 11 | 0 | 1 | 0.25531 | 299.2422 | 0 | 0 | 0 | 0 | 0 | 200 | 48400 | 200 | 681914.2249 | 510.81 | 99.2422
7311 | 11 | 0 | 1 | 0.2247 | 297.9902 | 0 | 0 | 0 | 0 | 0 | 200 | 48400 | 200 | 682114.2249 | 510.81 | 97.9902
7312 | 11 | 0 | 0.71158 | 0.19383 | 213.432 | 0 | 0 | 0 | 0 | 0 | 200 | 48400 | 200 | 682314.2249 | 510.81 | 13.432
7313 | 11 | 0 | 0.37765 | 0.21586 | 117.8943 | 0 | 0 | 0 | 0 | 0 | 117.8943 | 48400 | 117.8943 | 682432.1191 | 510.81 | 0
7314 | 11 | 0 | 0.08065 | 0.22891 | 32.6543 | 0 | 0 | 0 | 0 | 0 | 32.6543 | 48400 | 32.6543 | 682464.7734 | 510.81 | 0
7315 | 11 | 0 | 0 | 0.1422 | 5.8162 | 0 | 0 | 0 | 0 | 0 | 5.8162 | 48400 | 5.8162 | 682470.5896 | 510.81 | 0
7316 | 11 | 1 | 0 | 0.18464 | 7.5518 | 200 | 7.5518 | 180 | 187.5518 | 0 | 0 | 48200 | 187.5518 | 682658.1414 | 330.81 | 0
7317 | 11 | 1 | 0 | 0.1961 | 8.0204 | 200 | 8.0204 | 180 | 188.0204 | 0 | 0 | 48000 | 188.0204 | 682846.1619 | 150.81 | 0
7318 | 11 | 0 | 0 | 0.4184 | 17.1127 | 0 | 0 | 0 | 0 | 17.1127 | 0 | 48000 | 0 | 682846.1619 | 165.6433 | 0
7319 | 11 | 0 | 0 | 0.34965 | 14.3006 | 0 | 0 | 0 | 0 | 14.3006 | 0 | 48000 | 0 | 682846.1619 | 178.0391 | 0
7320 | 11 | 0 | 0 | 0.31477 | 12.8742 | 0 | 0 | 0 | 0 | 12.8742 | 0 | 48000 | 0 | 682846.1619 | 189.1984 | 0
7321 | 11 | 0 | 0 | 0.35386 | 14.4728 | 0 | 0 | 0 | 0 | 14.4728 | 0 | 48000 | 0 | 682846.1619 | 201.7434 | 0
7322 | 11 | 0 | 0 | 0.40408 | 16.5269 | 0 | 0 | 0 | 0 | 16.5269 | 0 | 48000 | 0 | 682846.1619 | 216.0689 | 0
7323 | 11 | 0 | 0 | 0.42492 | 17.3794 | 0 | 0 | 0 | 0 | 17.3794 | 0 | 48000 | 0 | 682846.1619 | 231.1334 | 0
7324 | 11 | 0 | 0 | 0.41684 | 17.0487 | 0 | 0 | 0 | 0 | 17.0487 | 0 | 48000 | 0 | 682846.1619 | 245.9112 | 0
7325 | 11 | 0 | 0 | 0.40816 | 16.6938 | 0 | 0 | 0 | 0 | 16.6938 | 0 | 48000 | 0 | 682846.1619 | 260.3814 | 0
7326 | 11 | 0 | 0 | 0.61333 | 25.0854 | 0 | 0 | 0 | 0 | 25.0854 | 0 | 48000 | 0 | 682846.1619 | 282.1254 | 0
7327 | 11 | 0 | 0 | 0.76582 | 31.3222 | 0 | 0 | 0 | 0 | 31.3222 | 0 | 48000 | 0 | 682846.1619 | 309.2755 | 0
7328 | 11 | 1 | 0.086069 | 0.83062 | 58.8292 | 200 | 58.8292 | 141.1708 | 200 | 0 | 0 | 47800 | 200 | 683046.1619 | 168.1047 | 0
7329 | 11 | 1 | 0.40303 | 0.77449 | 148.0712 | 200 | 148.0712 | 51.9288 | 200 | 0 | 0 | 47600 | 200 | 683246.1619 | 116.1759 | 0
7330 | 11 | 0 | 0.7594 | 0.66693 | 246.5916 | 0 | 0 | 0 | 0 | 180 | 66.5916 | 47600 | 66.5916 | 683312.7534 | 272.1999 | 0
7331 | 11 | 0 | 1 | 0.67361 | 316.3506 | 0 | 0 | 0 | 0 | 180 | 136.3506 | 47600 | 136.3506 | 683449.104 | 428.2239 | 0
7332 | 11 | 0 | 1 | 0.94303 | 327.37 | 0 | 0 | 0 | 0 | 95.277 | 200 | 47600 | 200 | 683649.104 | 510.81 | 32.093
7333 | 11 | 0 | 1 | 0.99023 | 329.3006 | 0 | 0 | 0 | 0 | 0 | 200 | 47600 | 200 | 683849.104 | 510.81 | 129.3006
7334 | 11 | 0 | 1 | 0.80941 | 321.9048 | 0 | 0 | 0 | 0 | 0 | 200 | 47600 | 200 | 684049.104 | 510.81 | 121.9048
7335 | 11 | 0 | 1 | 0.65598 | 315.6297 | 0 | 0 | 0 | 0 | 0 | 200 | 47600 | 200 | 684249.104 | 510.81 | 115.6297
7336 | 11 | 0 | 0.7594 | 0.37668 | 234.7203 | 0 | 0 | 0 | 0 | 0 | 200 | 47600 | 200 | 684449.104 | 510.81 | 34.7203
7337 | 11 | 0 | 0.40303 | 0.35833 | 131.0503 | 0 | 0 | 0 | 0 | 0 | 131.0503 | 47600 | 131.0503 | 684580.1543 | 510.81 | 0
7338 | 11 | 0 | 0.086069 | 0.3634 | 39.7199 | 0 | 0 | 0 | 0 | 0 | 39.7199 | 47600 | 39.7199 | 684619.8742 | 510.81 | 0
7339 | 11 | 0 | 0 | 0.41322 | 16.9008 | 0 | 0 | 0 | 0 | 0 | 16.9008 | 47600 | 16.9008 | 684636.775 | 510.81 | 0
7340 | 11 | 1 | 0 | 0.2949 | 12.0614 | 200 | 12.0614 | 180 | 192.0614 | 0 | 0 | 47400 | 192.0614 | 684828.8364 | 330.81 | 0
7341 | 11 | 1 | 0 | 0.2378 | 9.726 | 200 | 9.726 | 180 | 189.726 | 0 | 0 | 47200 | 189.726 | 685018.5623 | 150.81 | 0
7342 | 11 | 0 | 0 | 0.19446 | 7.9536 | 0 | 0 | 0 | 0 | 7.9536 | 0 | 47200 | 0 | 685018.5623 | 157.7042 | 0
7343 | 11 | 0 | 0 | 0.19121 | 7.8206 | 0 | 0 | 0 | 0 | 7.8206 | 0 | 47200 | 0 | 685018.5623 | 164.483 | 0
7344 | 11 | 0 | 0 | 0.23937 | 9.7901 | 0 | 0 | 0 | 0 | 9.7901 | 0 | 47200 | 0 | 685018.5623 | 172.9691 | 0
7345 | 11 | 0 | 0 | 0.14305 | 5.8508 | 0 | 0 | 0 | 0 | 5.8508 | 0 | 47200 | 0 | 685018.5623 | 178.0405 | 0
7346 | 11 | 0 | 0 | 0.15129 | 6.1879 | 0 | 0 | 0 | 0 | 6.1879 | 0 | 47200 | 0 | 685018.5623 | 183.4042 | 0
7347 | 11 | 0 | 0 | 0.14252 | 5.8291 | 0 | 0 | 0 | 0 | 5.8291 | 0 | 47200 | 0 | 685018.5623 | 188.4568 | 0
7348 | 11 | 0 | 0 | 0.13267 | 5.426 | 0 | 0 | 0 | 0 | 5.426 | 0 | 47200 | 0 | 685018.5623 | 193.1601 | 0
7349 | 11 | 0 | 0 | 0.14257 | 5.8312 | 0 | 0 | 0 | 0 | 5.8312 | 0 | 47200 | 0 | 685018.5623 | 198.2146 | 0
7350 | 11 | 0 | 0 | 0.15336 | 6.2726 | 0 | 0 | 0 | 0 | 6.2726 | 0 | 47200 | 0 | 685018.5623 | 203.6516 | 0
7351 | 11 | 0 | 0 | 0.14891 | 6.0902 | 0 | 0 | 0 | 0 | 6.0902 | 0 | 47200 | 0 | 685018.5623 | 208.9306 | 0
7352 | 11 | 1 | 0.090522 | 0.20204 | 34.4062 | 200 | 34.4062 | 165.5938 | 200 | 0 | 0 | 47000 | 200 | 685218.5623 | 43.3368 | 0
7353 | 11 | 1 | 0.42388 | 0.18657 | 130.0468 | 200 | 130.0468 | 43.3368 | 173.3836 | 0 | 0 | 46800 | 173.3836 | 685391.946 | 0 | 0
7354 | 11 | 0 | 0.79868 | 0.1839 | 238.1815 | 0 | 0 | 0 | 0 | 180 | 58.1815 | 46800 | 58.1815 | 685450.1275 | 156.024 | 0
7355 | 11 | 0 | 1 | 0.23747 | 298.5127 | 0 | 0 | 0 | 0 | 180 | 118.5127 | 46800 | 118.5127 | 685568.6402 | 312.048 | 0
7356 | 11 | 0 | 1 | 0.287 | 300.5384 | 0 | 0 | 0 | 0 | 180 | 120.5384 | 46800 | 120.5384 | 685689.1786 | 468.072 | 0
7357 | 11 | 0 | 1 | 0.28528 | 300.4681 | 0 | 0 | 0 | 0 | 49.3055 | 200 | 46800 | 200 | 685889.1786 | 510.81 | 51.1626
7358 | 11 | 0 | 1 | 0.24739 | 298.9183 | 0 | 0 | 0 | 0 | 0 | 200 | 46800 | 200 | 686089.1786 | 510.81 | 98.9183
7359 | 11 | 0 | 1 | 0.27206 | 299.9271 | 0 | 0 | 0 | 0 | 0 | 200 | 46800 | 200 | 686289.1786 | 510.81 | 99.9271
7360 | 11 | 0 | 0.79868 | 0.25302 | 241.0086 | 0 | 0 | 0 | 0 | 0 | 200 | 46800 | 200 | 686489.1786 | 510.81 | 41.0086
7361 | 11 | 0 | 0.42388 | 0.3418 | 136.396 | 0 | 0 | 0 | 0 | 0 | 136.396 | 46800 | 136.396 | 686625.5746 | 510.81 | 0
7362 | 11 | 0 | 0.090522 | 0.40622 | 42.7573 | 0 | 0 | 0 | 0 | 0 | 42.7573 | 46800 | 42.7573 | 686668.3318 | 510.81 | 0
7363 | 11 | 0 | 0 | 0.38615 | 15.7934 | 0 | 0 | 0 | 0 | 0 | 15.7934 | 46800 | 15.7934 | 686684.1252 | 510.81 | 0
7364 | 11 | 1 | 0 | 0.25683 | 10.5043 | 200 | 10.5043 | 180 | 190.5043 | 0 | 0 | 46600 | 190.5043 | 686874.6295 | 330.81 | 0
7365 | 11 | 1 | 0 | 0.18723 | 7.6577 | 200 | 7.6577 | 180 | 187.6577 | 0 | 0 | 46400 | 187.6577 | 687062.2872 | 150.81 | 0
7366 | 11 | 0 | 0 | 0.24577 | 10.0521 | 0 | 0 | 0 | 0 | 10.0521 | 0 | 46400 | 0 | 687062.2872 | 159.5231 | 0
7367 | 11 | 0 | 0 | 0.23679 | 9.6847 | 0 | 0 | 0 | 0 | 9.6847 | 0 | 46400 | 0 | 687062.2872 | 167.9178 | 0
7368 | 11 | 0 | 0 | 0.26778 | 10.9523 | 0 | 0 | 0 | 0 | 10.9523 | 0 | 46400 | 0 | 687062.2872 | 177.4113 | 0
7369 | 11 | 0 | 0 | 0.20499 | 8.3839 | 0 | 0 | 0 | 0 | 8.3839 | 0 | 46400 | 0 | 687062.2872 | 184.6785 | 0
7370 | 11 | 0 | 0 | 0.11432 | 4.6756 | 0 | 0 | 0 | 0 | 4.6756 | 0 | 46400 | 0 | 687062.2872 | 188.7313 | 0
7371 | 11 | 0 | 0 | 0.12406 | 5.0741 | 0 | 0 | 0 | 0 | 5.0741 | 0 | 46400 | 0 | 687062.2872 | 193.1295 | 0
7372 | 11 | 0 | 0 | 0.13437 | 5.4959 | 0 | 0 | 0 | 0 | 5.4959 | 0 | 46400 | 0 | 687062.2872 | 197.8934 | 0
7373 | 11 | 0 | 0 | 0.13577 | 5.553 | 0 | 0 | 0 | 0 | 5.553 | 0 | 46400 | 0 | 687062.2872 | 202.7067 | 0
7374 | 11 | 0 | 0 | 0.13496 | 5.52 | 0 | 0 | 0 | 0 | 5.52 | 0 | 46400 | 0 | 687062.2872 | 207.4914 | 0
7375 | 11 | 0 | 0 | 0.14954 | 6.1163 | 0 | 0 | 0 | 0 | 6.1163 | 0 | 46400 | 0 | 687062.2872 | 212.793 | 0
7376 | 11 | 1 | 0.086486 | 0.13334 | 30.4307 | 200 | 30.4307 | 169.5693 | 200 | 0 | 0 | 46200 | 200 | 687262.2872 | 43.2237 | 0
7377 | 11 | 1 | 0.40498 | 0.23322 | 126.4966 | 200 | 126.4966 | 43.2237 | 169.7203 | 0 | 0 | 46000 | 169.7203 | 687432.0075 | 0 | 0
7378 | 11 | 0 | 0.76307 | 0.25994 | 231.0072 | 0 | 0 | 0 | 0 | 180 | 51.0072 | 46000 | 51.0072 | 687483.0147 | 156.024 | 0
7379 | 11 | 0 | 1 | 0.28507 | 300.4594 | 0 | 0 | 0 | 0 | 180 | 120.4594 | 46000 | 120.4594 | 687603.474 | 312.048 | 0
7380 | 11 | 0 | 1 | 0.31682 | 301.7578 | 0 | 0 | 0 | 0 | 180 | 121.7578 | 46000 | 121.7578 | 687725.2318 | 468.072 | 0
7381 | 11 | 0 | 1 | 0.27486 | 300.0417 | 0 | 0 | 0 | 0 | 49.3055 | 200 | 46000 | 200 | 687925.2318 | 510.81 | 50.7362
7382 | 11 | 0 | 1 | 0.38484 | 304.5398 | 0 | 0 | 0 | 0 | 0 | 200 | 46000 | 200 | 688125.2318 | 510.81 | 104.5398
7383 | 11 | 0 | 1 | 0.33118 | 302.3451 | 0 | 0 | 0 | 0 | 0 | 200 | 46000 | 200 | 688325.2318 | 510.81 | 102.3451
7384 | 11 | 0 | 0.76307 | 0.2694 | 231.3942 | 0 | 0 | 0 | 0 | 0 | 200 | 46000 | 200 | 688525.2318 | 510.81 | 31.3942
7385 | 11 | 0 | 0.40498 | 0.20004 | 125.1395 | 0 | 0 | 0 | 0 | 0 | 125.1395 | 46000 | 125.1395 | 688650.3713 | 510.81 | 0
7386 | 11 | 0 | 0.086486 | 0.18527 | 32.5545 | 0 | 0 | 0 | 0 | 0 | 32.5545 | 46000 | 32.5545 | 688682.9258 | 510.81 | 0
7387 | 11 | 0 | 0 | 0.20082 | 8.2135 | 0 | 0 | 0 | 0 | 0 | 8.2135 | 46000 | 8.2135 | 688691.1393 | 510.81 | 0
7388 | 11 | 1 | 0 | 0.17391 | 7.1128 | 200 | 7.1128 | 180 | 187.1128 | 0 | 0 | 45800 | 187.1128 | 688878.2521 | 330.81 | 0
7389 | 11 | 1 | 0 | 0.14403 | 5.8909 | 200 | 5.8909 | 180 | 185.8909 | 0 | 0 | 45600 | 185.8909 | 689064.143 | 150.81 | 0
7390 | 11 | 0 | 0 | 0.16043 | 6.5616 | 0 | 0 | 0 | 0 | 6.5616 | 0 | 45600 | 0 | 689064.143 | 156.4976 | 0
7391 | 11 | 0 | 0 | 0.20161 | 8.2456 | 0 | 0 | 0 | 0 | 8.2456 | 0 | 45600 | 0 | 689064.143 | 163.6449 | 0
7392 | 11 | 0 | 0 | 0.24427 | 9.9906 | 0 | 0 | 0 | 0 | 9.9906 | 0 | 45600 | 0 | 689064.143 | 172.3048 | 0
7393 | 11 | 0 | 0 | 0.22901 | 9.3666 | 0 | 0 | 0 | 0 | 9.3666 | 0 | 45600 | 0 | 689064.143 | 180.4238 | 0
7394 | 11 | 0 | 0 | 0.1769 | 7.2351 | 0 | 0 | 0 | 0 | 7.2351 | 0 | 45600 | 0 | 689064.143 | 186.6952 | 0
7395 | 11 | 0 | 0 | 0.12275 | 5.0204 | 0 | 0 | 0 | 0 | 5.0204 | 0 | 45600 | 0 | 689064.143 | 191.0468 | 0
7396 | 11 | 0 | 0 | 0.1733 | 7.0881 | 0 | 0 | 0 | 0 | 7.0881 | 0 | 45600 | 0 | 689064.143 | 197.1908 | 0
7397 | 11 | 0 | 0 | 0.34438 | 14.0853 | 0 | 0 | 0 | 0 | 14.0853 | 0 | 45600 | 0 | 689064.143 | 209.4 | 0
7398 | 11 | 0 | 0 | 0.34795 | 14.231 | 0 | 0 | 0 | 0 | 14.231 | 0 | 45600 | 0 | 689064.143 | 221.7354 | 0
7399 | 11 | 0 | 0 | 0.31103 | 12.7213 | 0 | 0 | 0 | 0 | 12.7213 | 0 | 45600 | 0 | 689064.143 | 232.7623 | 0
7400 | 11 | 1 | 0.091204 | 0.33351 | 39.9804 | 200 | 39.9804 | 160.0196 | 200 | 0 | 0 | 45400 | 200 | 689264.143 | 72.7427 | 0
7401 | 11 | 1 | 0.42707 | 0.32925 | 136.8042 | 200 | 136.8042 | 63.1958 | 200 | 0 | 0 | 45200 | 200 | 689464.143 | 9.5469 | 0
7402 | 11 | 0 | 0.8047 | 0.24001 | 242.2136 | 0 | 0 | 0 | 0 | 180 | 62.2136 | 45200 | 62.2136 | 689526.3566 | 165.5709 | 0
7403 | 11 | 0 | 1 | 0.20183 | 297.0548 | 0 | 0 | 0 | 0 | 180 | 117.0548 | 45200 | 117.0548 | 689643.4113 | 321.5949 | 0
7404 | 11 | 0 | 1 | 0.12689 | 293.9898 | 0 | 0 | 0 | 0 | 180 | 113.9898 | 45200 | 113.9898 | 689757.4012 | 477.6189 | 0
7405 | 11 | 0 | 1 | 0.19315 | 296.7 | 0 | 0 | 0 | 0 | 38.2916 | 200 | 45200 | 200 | 689957.4012 | 510.81 | 58.4084
7406 | 11 | 0 | 1 | 0.15494 | 295.137 | 0 | 0 | 0 | 0 | 0 | 200 | 45200 | 200 | 690157.4012 | 510.81 | 95.137
7407 | 11 | 0 | 1 | 0.23876 | 298.5653 | 0 | 0 | 0 | 0 | 0 | 200 | 45200 | 200 | 690357.4012 | 510.81 | 98.5653
7408 | 11 | 0 | 0.8047 | 0.1932 | 240.2991 | 0 | 0 | 0 | 0 | 0 | 200 | 45200 | 200 | 690557.4012 | 510.81 | 40.2991
7409 | 11 | 0 | 0.42707 | 0.12442 | 128.427 | 0 | 0 | 0 | 0 | 0 | 128.427 | 45200 | 128.427 | 690685.8281 | 510.81 | 0
7410 | 11 | 0 | 0.091204 | 0.15466 | 32.6652 | 0 | 0 | 0 | 0 | 0 | 32.6652 | 45200 | 32.6652 | 690718.4933 | 510.81 | 0
7411 | 11 | 0 | 0 | 0.1486 | 6.0777 | 0 | 0 | 0 | 0 | 0 | 6.0777 | 45200 | 6.0777 | 690724.5711 | 510.81 | 0
7412 | 11 | 1 | 0 | 0.25928 | 10.6048 | 200 | 10.6048 | 180 | 190.6048 | 0 | 0 | 45000 | 190.6048 | 690915.1758 | 330.81 | 0
7413 | 11 | 1 | 0 | 0.30991 | 12.6753 | 200 | 12.6753 | 180 | 192.6753 | 0 | 0 | 44800 | 192.6753 | 691107.8511 | 150.81 | 0
7414 | 11 | 0 | 0 | 0.19611 | 8.0207 | 0 | 0 | 0 | 0 | 8.0207 | 0 | 44800 | 0 | 691107.8511 | 157.7624 | 0
7415 | 11 | 0 | 0 | 0.19579 | 8.0078 | 0 | 0 | 0 | 0 | 8.0078 | 0 | 44800 | 0 | 691107.8511 | 164.7035 | 0
7416 | 11 | 0 | 0 | 0.15141 | 6.1928 | 0 | 0 | 0 | 0 | 6.1928 | 0 | 44800 | 0 | 691107.8511 | 170.0714 | 0
7417 | 11 | 0 | 0 | 0.18669 | 7.6357 | 0 | 0 | 0 | 0 | 7.6357 | 0 | 44800 | 0 | 691107.8511 | 176.69 | 0
7418 | 11 | 0 | 0 | 0.35472 | 14.5082 | 0 | 0 | 0 | 0 | 14.5082 | 0 | 44800 | 0 | 691107.8511 | 189.2657 | 0
7419 | 11 | 0 | 0 | 0.27402 | 11.2074 | 0 | 0 | 0 | 0 | 11.2074 | 0 | 44800 | 0 | 691107.8511 | 198.9803 | 0
7420 | 11 | 0 | 0 | 0.37989 | 15.5377 | 0 | 0 | 0 | 0 | 15.5377 | 0 | 44800 | 0 | 691107.8511 | 212.4483 | 0
7421 | 11 | 0 | 0 | 0.22795 | 9.3231 | 0 | 0 | 0 | 0 | 9.3231 | 0 | 44800 | 0 | 691107.8511 | 220.5296 | 0
7422 | 11 | 0 | 0 | 0.23089 | 9.4435 | 0 | 0 | 0 | 0 | 9.4435 | 0 | 44800 | 0 | 691107.8511 | 228.7152 | 0
7423 | 11 | 0 | 0 | 0.22217 | 9.0867 | 0 | 0 | 0 | 0 | 9.0867 | 0 | 44800 | 0 | 691107.8511 | 236.5915 | 0
7424 | 11 | 1 | 0.097551 | 0.40572 | 44.7666 | 200 | 44.7666 | 155.2334 | 200 | 0 | 0 | 44600 | 200 | 691307.8511 | 81.3581 | 0
7425 | 11 | 1 | 0.45679 | 0.31732 | 144.9003 | 200 | 144.9003 | 55.0997 | 200 | 0 | 0 | 44400 | 200 | 691507.8511 | 26.2584 | 0
7426 | 11 | 0 | 0.8607 | 0.40528 | 265.1468 | 0 | 0 | 0 | 0 | 180 | 85.1468 | 44400 | 85.1468 | 691592.9979 | 182.2824 | 0
7427 | 11 | 0 | 1 | 0.39168 | 304.8198 | 0 | 0 | 0 | 0 | 180 | 124.8198 | 44400 | 124.8198 | 691717.8177 | 338.3064 | 0
7428 | 11 | 0 | 1 | 0.83145 | 322.8065 | 0 | 0 | 0 | 0 | 180 | 142.8065 | 44400 | 142.8065 | 691860.6242 | 494.3304 | 0
7429 | 11 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 19.012 | 200 | 44400 | 200 | 692060.6242 | 510.81 | 110.688
7430 | 11 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 0 | 200 | 44400 | 200 | 692260.6242 | 510.81 | 129.7
7431 | 11 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 0 | 200 | 44400 | 200 | 692460.6242 | 510.81 | 129.7
7432 | 11 | 0 | 0.8607 | 1 | 289.4707 | 0 | 0 | 0 | 0 | 0 | 200 | 44400 | 200 | 692660.6242 | 510.81 | 89.4707
7433 | 11 | 0 | 0.45679 | 0.76083 | 163.0399 | 0 | 0 | 0 | 0 | 0 | 163.0399 | 44400 | 163.0399 | 692823.6641 | 510.81 | 0
7434 | 11 | 0 | 0.097551 | 0.60042 | 52.7297 | 0 | 0 | 0 | 0 | 0 | 52.7297 | 44400 | 52.7297 | 692876.3938 | 510.81 | 0
7435 | 11 | 0 | 0 | 0.37316 | 15.2623 | 0 | 0 | 0 | 0 | 0 | 15.2623 | 44400 | 15.2623 | 692891.6561 | 510.81 | 0
7436 | 11 | 1 | 0 | 0.30798 | 12.5963 | 200 | 12.5963 | 180 | 192.5963 | 0 | 0 | 44200 | 192.5963 | 693084.2524 | 330.81 | 0
7437 | 11 | 1 | 0 | 0.2617 | 10.7034 | 200 | 10.7034 | 180 | 190.7034 | 0 | 0 | 44000 | 190.7034 | 693274.9558 | 150.81 | 0
7438 | 11 | 0 | 0 | 0.27603 | 11.2896 | 0 | 0 | 0 | 0 | 11.2896 | 0 | 44000 | 0 | 693274.9558 | 160.5958 | 0
7439 | 11 | 0 | 0 | 0.28035 | 11.4664 | 0 | 0 | 0 | 0 | 11.4664 | 0 | 44000 | 0 | 693274.9558 | 170.5349 | 0
7440 | 11 | 0 | 0 | 0.24487 | 10.0152 | 0 | 0 | 0 | 0 | 10.0152 | 0 | 44000 | 0 | 693274.9558 | 179.2161 | 0
7441 | 11 | 0 | 0 | 0.24115 | 9.8632 | 0 | 0 | 0 | 0 | 9.8632 | 0 | 44000 | 0 | 693274.9558 | 187.7655 | 0
7442 | 11 | 0 | 0 | 0.28694 | 11.7357 | 0 | 0 | 0 | 0 | 11.7357 | 0 | 44000 | 0 | 693274.9558 | 197.938 | 0
7443 | 11 | 0 | 0 | 0.24407 | 9.9824 | 0 | 0 | 0 | 0 | 9.9824 | 0 | 44000 | 0 | 693274.9558 | 206.5908 | 0
7444 | 11 | 0 | 0 | 0.1857 | 7.595 | 0 | 0 | 0 | 0 | 7.595 | 0 | 44000 | 0 | 693274.9558 | 213.1741 | 0
7445 | 11 | 0 | 0 | 0.11667 | 4.7718 | 0 | 0 | 0 | 0 | 4.7718 | 0 | 44000 | 0 | 693274.9558 | 217.3103 | 0
7446 | 11 | 0 | 0 | 0.11185 | 4.5748 | 0 | 0 | 0 | 0 | 4.5748 | 0 | 44000 | 0 | 693274.9558 | 221.2758 | 0
7447 | 11 | 0 | 0 | 0.12294 | 5.0281 | 0 | 0 | 0 | 0 | 5.0281 | 0 | 44000 | 0 | 693274.9558 | 225.6341 | 0
7448 | 11 | 1 | 0.084335 | 0.12299 | 29.3864 | 200 | 29.3864 | 170.6136 | 200 | 0 | 0 | 43800 | 200 | 693474.9558 | 55.0205 | 0
7449 | 11 | 1 | 0.39491 | 0.20375 | 122.3823 | 200 | 122.3823 | 55.0205 | 177.4028 | 0 | 0 | 43600 | 177.4028 | 693652.3586 | 0 | 0
7450 | 11 | 0 | 0.7441 | 0.23775 | 224.6187 | 0 | 0 | 0 | 0 | 180 | 44.6187 | 43600 | 44.6187 | 693696.9773 | 156.024 | 0
7451 | 11 | 0 | 1 | 0.20274 | 297.092 | 0 | 0 | 0 | 0 | 180 | 117.092 | 43600 | 117.092 | 693814.0694 | 312.048 | 0
7452 | 11 | 0 | 1 | 0.23973 | 298.605 | 0 | 0 | 0 | 0 | 180 | 118.605 | 43600 | 118.605 | 693932.6744 | 468.072 | 0
7453 | 11 | 0 | 1 | 0.2687 | 299.7898 | 0 | 0 | 0 | 0 | 49.3055 | 200 | 43600 | 200 | 694132.6744 | 510.81 | 50.4843
7454 | 11 | 0 | 1 | 0.18684 | 296.4416 | 0 | 0 | 0 | 0 | 0 | 200 | 43600 | 200 | 694332.6744 | 510.81 | 96.4416
7455 | 11 | 0 | 1 | 0.14184 | 294.6011 | 0 | 0 | 0 | 0 | 0 | 200 | 43600 | 200 | 694532.6744 | 510.81 | 94.6011
7456 | 11 | 0 | 0.7441 | 0.17802 | 222.1761 | 0 | 0 | 0 | 0 | 0 | 200 | 43600 | 200 | 694732.6744 | 510.81 | 22.1761
7457 | 11 | 0 | 0.39491 | 0.15877 | 120.5428 | 0 | 0 | 0 | 0 | 0 | 120.5428 | 43600 | 120.5428 | 694853.2172 | 510.81 | 0
7458 | 11 | 0 | 0.084335 | 0.16704 | 31.1881 | 0 | 0 | 0 | 0 | 0 | 31.1881 | 43600 | 31.1881 | 694884.4052 | 510.81 | 0
7459 | 11 | 0 | 0 | 0.1806 | 7.3864 | 0 | 0 | 0 | 0 | 0 | 7.3864 | 43600 | 7.3864 | 694891.7916 | 510.81 | 0
7460 | 11 | 1 | 0 | 0.20576 | 8.4157 | 200 | 8.4157 | 180 | 188.4157 | 0 | 0 | 43400 | 188.4157 | 695080.2074 | 330.81 | 0
7461 | 11 | 1 | 0 | 0.17699 | 7.2389 | 200 | 7.2389 | 180 | 187.2389 | 0 | 0 | 43200 | 187.2389 | 695267.4462 | 150.81 | 0
7462 | 11 | 0 | 0 | 0.13867 | 5.6717 | 0 | 0 | 0 | 0 | 5.6717 | 0 | 43200 | 0 | 695267.4462 | 155.7262 | 0
7463 | 11 | 0 | 0 | 0.17508 | 7.1606 | 0 | 0 | 0 | 0 | 7.1606 | 0 | 43200 | 0 | 695267.4462 | 161.933 | 0
7464 | 11 | 0 | 0 | 0.13173 | 5.3876 | 0 | 0 | 0 | 0 | 5.3876 | 0 | 43200 | 0 | 695267.4462 | 166.603 | 0
7465 | 11 | 0 | 0 | 0.14952 | 6.1154 | 0 | 0 | 0 | 0 | 6.1154 | 0 | 43200 | 0 | 695267.4462 | 171.9038 | 0
7466 | 11 | 0 | 0 | 0.10299 | 4.2124 | 0 | 0 | 0 | 0 | 4.2124 | 0 | 43200 | 0 | 695267.4462 | 175.5551 | 0
7467 | 11 | 0 | 0 | 0.08999 | 3.6806 | 0 | 0 | 0 | 0 | 3.6806 | 0 | 43200 | 0 | 695267.4462 | 178.7454 | 0
7468 | 11 | 0 | 0 | 0.084451 | 3.454 | 0 | 0 | 0 | 0 | 3.454 | 0 | 43200 | 0 | 695267.4462 | 181.7394 | 0
7469 | 11 | 0 | 0 | 0.10298 | 4.2119 | 0 | 0 | 0 | 0 | 4.2119 | 0 | 43200 | 0 | 695267.4462 | 185.3903 | 0
7470 | 11 | 0 | 0 | 0.092605 | 3.7875 | 0 | 0 | 0 | 0 | 3.7875 | 0 | 43200 | 0 | 695267.4462 | 188.6733 | 0
7471 | 11 | 0 | 0 | 0.12535 | 5.1269 | 0 | 0 | 0 | 0 | 5.1269 | 0 | 43200 | 0 | 695267.4462 | 193.1173 | 0
7472 | 11 | 1 | 0.078207 | 0.20012 | 30.771 | 200 | 30.771 | 169.229 | 200 | 0 | 0 | 43000 | 200 | 695467.4462 | 23.8883 | 0
7473 | 11 | 1 | 0.36621 | 0.32817 | 119.1845 | 200 | 119.1845 | 23.8883 | 143.0728 | 0 | 0 | 42800 | 143.0728 | 695610.519 | 0 | 0
7474 | 11 | 0 | 0.69003 | 0.47991 | 218.9089 | 0 | 0 | 0 | 0 | 180 | 38.9089 | 42800 | 38.9089 | 695649.4279 | 156.024 | 0
7475 | 11 | 0 | 0.9752 | 0.70387 | 310.426 | 0 | 0 | 0 | 0 | 180 | 130.426 | 42800 | 130.426 | 695779.8539 | 312.048 | 0
7476 | 11 | 0 | 1 | 0.64725 | 315.2726 | 0 | 0 | 0 | 0 | 180 | 135.2726 | 42800 | 135.2726 | 695915.1266 | 468.072 | 0
7477 | 11 | 0 | 1 | 0.44655 | 307.0641 | 0 | 0 | 0 | 0 | 49.3055 | 200 | 42800 | 200 | 696115.1266 | 510.81 | 57.7586
7478 | 11 | 0 | 1 | 0.27746 | 300.1482 | 0 | 0 | 0 | 0 | 0 | 200 | 42800 | 200 | 696315.1266 | 510.81 | 100.1482
7479 | 11 | 0 | 0.9752 | 0.29007 | 293.5017 | 0 | 0 | 0 | 0 | 0 | 200 | 42800 | 200 | 696515.1266 | 510.81 | 93.5017
7480 | 11 | 0 | 0.69003 | 0.32722 | 212.6639 | 0 | 0 | 0 | 0 | 0 | 200 | 42800 | 200 | 696715.1266 | 510.81 | 12.6639
7481 | 11 | 0 | 0.36621 | 0.33688 | 119.5407 | 0 | 0 | 0 | 0 | 0 | 119.5407 | 42800 | 119.5407 | 696834.6673 | 510.81 | 0
7482 | 11 | 0 | 0.078207 | 0.31635 | 35.5248 | 0 | 0 | 0 | 0 | 0 | 35.5248 | 42800 | 35.5248 | 696870.1921 | 510.81 | 0
7483 | 11 | 0 | 0 | 0.41127 | 16.821 | 0 | 0 | 0 | 0 | 0 | 16.821 | 42800 | 16.821 | 696887.0131 | 510.81 | 0
7484 | 11 | 1 | 0 | 0.29377 | 12.0152 | 200 | 12.0152 | 180 | 192.0152 | 0 | 0 | 42600 | 192.0152 | 697079.0283 | 330.81 | 0
7485 | 11 | 1 | 0 | 0.42207 | 17.2628 | 200 | 17.2628 | 180 | 197.2628 | 0 | 0 | 42400 | 197.2628 | 697276.2911 | 150.81 | 0
7486 | 11 | 0 | 0 | 0.42149 | 17.2389 | 0 | 0 | 0 | 0 | 17.2389 | 0 | 42400 | 0 | 697276.2911 | 165.7527 | 0
7487 | 11 | 0 | 0 | 0.50798 | 20.7762 | 0 | 0 | 0 | 0 | 20.7762 | 0 | 42400 | 0 | 697276.2911 | 183.7615 | 0
7488 | 11 | 0 | 0 | 0.26583 | 10.8725 | 0 | 0 | 0 | 0 | 10.8725 | 0 | 42400 | 0 | 697276.2911 | 193.1858 | 0
7489 | 11 | 0 | 0 | 0.23298 | 9.5289 | 0 | 0 | 0 | 0 | 9.5289 | 0 | 42400 | 0 | 697276.2911 | 201.4454 | 0
7490 | 11 | 0 | 0 | 0.25598 | 10.4697 | 0 | 0 | 0 | 0 | 10.4697 | 0 | 42400 | 0 | 697276.2911 | 210.5206 | 0
7491 | 11 | 0 | 0 | 0.37926 | 15.5117 | 0 | 0 | 0 | 0 | 15.5117 | 0 | 42400 | 0 | 697276.2911 | 223.9661 | 0
7492 | 11 | 0 | 0 | 0.28603 | 11.6986 | 0 | 0 | 0 | 0 | 11.6986 | 0 | 42400 | 0 | 697276.2911 | 234.1065 | 0
7493 | 11 | 0 | 0 | 0.42519 | 17.3904 | 0 | 0 | 0 | 0 | 17.3904 | 0 | 42400 | 0 | 697276.2911 | 249.1805 | 0
7494 | 11 | 0 | 0 | 0.31459 | 12.8666 | 0 | 0 | 0 | 0 | 12.8666 | 0 | 42400 | 0 | 697276.2911 | 260.3333 | 0
7495 | 11 | 0 | 0 | 0.3114 | 12.7364 | 0 | 0 | 0 | 0 | 12.7364 | 0 | 42400 | 0 | 697276.2911 | 271.3732 | 0
7496 | 11 | 1 | 0.09592 | 0.31488 | 40.5801 | 200 | 40.5801 | 159.4199 | 200 | 0 | 0 | 42200 | 200 | 697476.2911 | 111.9533 | 0
7497 | 11 | 1 | 0.44916 | 0.45448 | 148.3046 | 200 | 148.3046 | 51.6954 | 200 | 0 | 0 | 42000 | 200 | 697676.2911 | 60.2579 | 0
7498 | 11 | 0 | 0.84631 | 0.34644 | 258.585 | 0 | 0 | 0 | 0 | 180 | 78.585 | 42000 | 78.585 | 697754.8761 | 216.2819 | 0
7499 | 11 | 0 | 1 | 0.3855 | 304.5668 | 0 | 0 | 0 | 0 | 180 | 124.5668 | 42000 | 124.5668 | 697879.443 | 372.3059 | 0
7500 | 11 | 0 | 1 | 0.39279 | 304.865 | 0 | 0 | 0 | 0 | 159.7879 | 145.0771 | 42000 | 145.0771 | 698024.5201 | 510.81 | 0
7501 | 11 | 0 | 1 | 0.3086 | 301.4217 | 0 | 0 | 0 | 0 | 0 | 200 | 42000 | 200 | 698224.5201 | 510.81 | 101.4217
7502 | 11 | 0 | 1 | 0.25353 | 299.1695 | 0 | 0 | 0 | 0 | 0 | 200 | 42000 | 200 | 698424.5201 | 510.81 | 99.1695
7503 | 11 | 0 | 1 | 0.34691 | 302.9888 | 0 | 0 | 0 | 0 | 0 | 200 | 42000 | 200 | 698624.5201 | 510.81 | 102.9888
7504 | 11 | 0 | 0.84631 | 0.41016 | 261.1909 | 0 | 0 | 0 | 0 | 0 | 200 | 42000 | 200 | 698824.5201 | 510.81 | 61.1909
7505 | 11 | 0 | 0.44916 | 0.53106 | 151.4365 | 0 | 0 | 0 | 0 | 0 | 151.4365 | 42000 | 151.4365 | 698975.9566 | 510.81 | 0
7506 | 11 | 0 | 0.09592 | 0.50351 | 48.2953 | 0 | 0 | 0 | 0 | 0 | 48.2953 | 42000 | 48.2953 | 699024.2519 | 510.81 | 0
7507 | 11 | 0 | 0 | 0.54297 | 22.2074 | 0 | 0 | 0 | 0 | 0 | 22.2074 | 42000 | 22.2074 | 699046.4593 | 510.81 | 0
7508 | 11 | 1 | 0 | 0.82931 | 33.9187 | 200 | 33.9187 | 166.0813 | 200 | 0 | 0 | 41800 | 200 | 699246.4593 | 344.7287 | 0
7509 | 11 | 1 | 0 | 0.74594 | 30.5089 | 200 | 30.5089 | 169.4911 | 200 | 0 | 0 | 41600 | 200 | 699446.4593 | 175.2376 | 0
7510 | 11 | 0 | 0 | 0.67132 | 27.457 | 0 | 0 | 0 | 0 | 27.457 | 0 | 41600 | 0 | 699446.4593 | 199.0374 | 0
7511 | 11 | 0 | 0 | 0.69603 | 28.4675 | 0 | 0 | 0 | 0 | 28.4675 | 0 | 41600 | 0 | 699446.4593 | 223.713 | 0
7512 | 11 | 0 | 0 | 0.6013 | 24.593 | 0 | 0 | 0 | 0 | 24.593 | 0 | 41600 | 0 | 699446.4593 | 245.0302 | 0
7513 | 11 | 0 | 0 | 0.45699 | 18.6908 | 0 | 0 | 0 | 0 | 18.6908 | 0 | 41600 | 0 | 699446.4593 | 261.2314 | 0
7514 | 11 | 0 | 0 | 0.4558 | 18.6423 | 0 | 0 | 0 | 0 | 18.6423 | 0 | 41600 | 0 | 699446.4593 | 277.3906 | 0
7515 | 11 | 0 | 0 | 0.35654 | 14.5826 | 0 | 0 | 0 | 0 | 14.5826 | 0 | 41600 | 0 | 699446.4593 | 290.0308 | 0
7516 | 11 | 0 | 0 | 0.39195 | 16.0309 | 0 | 0 | 0 | 0 | 16.0309 | 0 | 41600 | 0 | 699446.4593 | 303.9264 | 0
7517 | 11 | 0 | 0 | 0.46372 | 18.9664 | 0 | 0 | 0 | 0 | 18.9664 | 0 | 41600 | 0 | 699446.4593 | 320.3664 | 0
7518 | 11 | 0 | 0 | 0.37616 | 15.3851 | 0 | 0 | 0 | 0 | 15.3851 | 0 | 41600 | 0 | 699446.4593 | 333.7022 | 0
7519 | 11 | 0 | 0 | 0.44784 | 18.3167 | 0 | 0 | 0 | 0 | 18.3167 | 0 | 41600 | 0 | 699446.4593 | 349.5791 | 0
7520 | 11 | 1 | 0.083715 | 0.54132 | 46.3168 | 200 | 46.3168 | 153.6832 | 200 | 0 | 0 | 41400 | 200 | 699646.4593 | 195.896 | 0
7521 | 11 | 1 | 0.39201 | 0.40768 | 129.8854 | 200 | 129.8854 | 70.1146 | 200 | 0 | 0 | 41200 | 200 | 699846.4593 | 125.7814 | 0
7522 | 11 | 0 | 0.73863 | 0.60788 | 238.1788 | 0 | 0 | 0 | 0 | 180 | 58.1788 | 41200 | 58.1788 | 699904.6381 | 281.8054 | 0
7523 | 11 | 0 | 1 | 0.45358 | 307.3513 | 0 | 0 | 0 | 0 | 180 | 127.3513 | 41200 | 127.3513 | 700031.9894 | 437.8294 | 0
7524 | 11 | 0 | 1 | 0.42944 | 306.3639 | 0 | 0 | 0 | 0 | 84.1955 | 200 | 41200 | 200 | 700231.9894 | 510.81 | 22.1684
7525 | 11 | 0 | 1 | 0.48417 | 308.6024 | 0 | 0 | 0 | 0 | 0 | 200 | 41200 | 200 | 700431.9894 | 510.81 | 108.6024
7526 | 11 | 0 | 1 | 0.62993 | 314.5643 | 0 | 0 | 0 | 0 | 0 | 200 | 41200 | 200 | 700631.9894 | 510.81 | 114.5643
7527 | 11 | 0 | 1 | 0.69641 | 317.283 | 0 | 0 | 0 | 0 | 0 | 200 | 41200 | 200 | 700831.9894 | 510.81 | 117.283
7528 | 11 | 0 | 0.73863 | 0.67133 | 240.7739 | 0 | 0 | 0 | 0 | 0 | 200 | 41200 | 200 | 701031.9894 | 510.81 | 40.7739
7529 | 11 | 0 | 0.39201 | 0.43235 | 130.8945 | 0 | 0 | 0 | 0 | 0 | 130.8945 | 41200 | 130.8945 | 701162.8839 | 510.81 | 0
7530 | 11 | 0 | 0.083715 | 0.47071 | 43.429 | 0 | 0 | 0 | 0 | 0 | 43.429 | 41200 | 43.429 | 701206.3129 | 510.81 | 0
7531 | 11 | 0 | 0 | 0.51265 | 20.9675 | 0 | 0 | 0 | 0 | 0 | 20.9675 | 41200 | 20.9675 | 701227.2803 | 510.81 | 0
7532 | 11 | 1 | 0 | 0.61684 | 25.2288 | 200 | 25.2288 | 174.7712 | 200 | 0 | 0 | 41000 | 200 | 701427.2803 | 336.0388 | 0
7533 | 11 | 1 | 0 | 0.32206 | 13.1725 | 200 | 13.1725 | 180 | 193.1725 | 0 | 0 | 40800 | 193.1725 | 701620.4528 | 156.0388 | 0
7534 | 11 | 0 | 0 | 0.37361 | 15.2806 | 0 | 0 | 0 | 0 | 15.2806 | 0 | 40800 | 0 | 701620.4528 | 169.2841 | 0
7535 | 11 | 0 | 0 | 0.31555 | 12.906 | 0 | 0 | 0 | 0 | 12.906 | 0 | 40800 | 0 | 701620.4528 | 180.4711 | 0
7536 | 11 | 0 | 0 | 0.36884 | 15.0854 | 0 | 0 | 0 | 0 | 15.0854 | 0 | 40800 | 0 | 701620.4528 | 193.5471 | 0
7537 | 11 | 0 | 0 | 0.42192 | 17.2565 | 0 | 0 | 0 | 0 | 17.2565 | 0 | 40800 | 0 | 701620.4528 | 208.505 | 0
7538 | 11 | 0 | 0 | 0.45334 | 18.5417 | 0 | 0 | 0 | 0 | 18.5417 | 0 | 40800 | 0 | 701620.4528 | 224.577 | 0
7539 | 11 | 0 | 0 | 0.51871 | 21.2152 | 0 | 0 | 0 | 0 | 21.2152 | 0 | 40800 | 0 | 701620.4528 | 242.9663 | 0
7540 | 11 | 0 | 0 | 0.32029 | 13.0999 | 0 | 0 | 0 | 0 | 13.0999 | 0 | 40800 | 0 | 701620.4528 | 254.3214 | 0
7541 | 11 | 0 | 0 | 0.39026 | 15.9618 | 0 | 0 | 0 | 0 | 15.9618 | 0 | 40800 | 0 | 701620.4528 | 268.1571 | 0
7542 | 11 | 0 | 0 | 0.28204 | 11.5353 | 0 | 0 | 0 | 0 | 11.5353 | 0 | 40800 | 0 | 701620.4528 | 278.1559 | 0
7543 | 11 | 0 | 0 | 0.16582 | 6.7822 | 0 | 0 | 0 | 0 | 6.7822 | 0 | 40800 | 0 | 701620.4528 | 284.0346 | 0
7544 | 11 | 1 | 0.08601 | 0.10098 | 28.9698 | 200 | 28.9698 | 171.0302 | 200 | 0 | 0 | 40600 | 200 | 701820.4528 | 113.0044 | 0
7545 | 11 | 1 | 0.40275 | 0.093772 | 120.1492 | 200 | 120.1492 | 79.8508 | 200 | 0 | 0 | 40400 | 200 | 702020.4528 | 33.1536 | 0
7546 | 11 | 0 | 0.75887 | 0.10966 | 223.647 | 0 | 0 | 0 | 0 | 180 | 43.647 | 40400 | 43.647 | 702064.0998 | 189.1776 | 0
7547 | 11 | 0 | 1 | 0.19464 | 296.7609 | 0 | 0 | 0 | 0 | 180 | 116.7609 | 40400 | 116.7609 | 702180.8607 | 345.2016 | 0
7548 | 11 | 0 | 1 | 0.20077 | 297.0115 | 0 | 0 | 0 | 0 | 180 | 117.0115 | 40400 | 117.0115 | 702297.8722 | 501.2256 | 0
7549 | 11 | 0 | 1 | 0.26673 | 299.7095 | 0 | 0 | 0 | 0 | 11.0572 | 200 | 40400 | 200 | 702497.8722 | 510.81 | 88.6522
7550 | 11 | 0 | 1 | 0.23053 | 298.2285 | 0 | 0 | 0 | 0 | 0 | 200 | 40400 | 200 | 702697.8722 | 510.81 | 98.2285
7551 | 11 | 0 | 1 | 0.27365 | 299.9922 | 0 | 0 | 0 | 0 | 0 | 200 | 40400 | 200 | 702897.8722 | 510.81 | 99.9922
7552 | 11 | 0 | 0.75887 | 0.28276 | 230.727 | 0 | 0 | 0 | 0 | 0 | 200 | 40400 | 200 | 703097.8722 | 510.81 | 30.727
7553 | 11 | 0 | 0.40275 | 0.38857 | 132.2063 | 0 | 0 | 0 | 0 | 0 | 132.2063 | 40400 | 132.2063 | 703230.0784 | 510.81 | 0
7554 | 11 | 0 | 0.08601 | 0.35016 | 39.1612 | 0 | 0 | 0 | 0 | 0 | 39.1612 | 40400 | 39.1612 | 703269.2396 | 510.81 | 0
7555 | 11 | 0 | 0 | 0.37383 | 15.2895 | 0 | 0 | 0 | 0 | 0 | 15.2895 | 40400 | 15.2895 | 703284.5291 | 510.81 | 0
7556 | 11 | 1 | 0 | 0.46712 | 19.1051 | 200 | 19.1051 | 180 | 199.1051 | 0 | 0 | 40200 | 199.1051 | 703483.6342 | 330.81 | 0
7557 | 11 | 1 | 0 | 0.38643 | 15.8049 | 200 | 15.8049 | 180 | 195.8049 | 0 | 0 | 40000 | 195.8049 | 703679.4391 | 150.81 | 0
7558 | 11 | 0 | 0 | 0.41495 | 16.9713 | 0 | 0 | 0 | 0 | 16.9713 | 0 | 40000 | 0 | 703679.4391 | 165.5207 | 0
7559 | 11 | 0 | 0 | 0.35981 | 14.7162 | 0 | 0 | 0 | 0 | 14.7162 | 0 | 40000 | 0 | 703679.4391 | 178.2767 | 0
7560 | 11 | 0 | 0 | 0.23381 | 9.5626 | 0 | 0 | 0 | 0 | 9.5626 | 0 | 40000 | 0 | 703679.4391 | 186.5656 | 0
7561 | 11 | 0 | 0 | 0.21614 | 8.8402 | 0 | 0 | 0 | 0 | 8.8402 | 0 | 40000 | 0 | 703679.4391 | 194.2282 | 0
7562 | 11 | 0 | 0 | 0.26414 | 10.8034 | 0 | 0 | 0 | 0 | 10.8034 | 0 | 40000 | 0 | 703679.4391 | 203.5926 | 0
7563 | 11 | 0 | 0 | 0.28324 | 11.5845 | 0 | 0 | 0 | 0 | 11.5845 | 0 | 40000 | 0 | 703679.4391 | 213.6341 | 0
7564 | 11 | 0 | 0 | 0.36717 | 15.0173 | 0 | 0 | 0 | 0 | 15.0173 | 0 | 40000 | 0 | 703679.4391 | 226.6511 | 0
7565 | 11 | 0 | 0 | 0.46831 | 19.154 | 0 | 0 | 0 | 0 | 19.154 | 0 | 40000 | 0 | 703679.4391 | 243.2537 | 0
7566 | 11 | 0 | 0 | 0.66352 | 27.138 | 0 | 0 | 0 | 0 | 27.138 | 0 | 40000 | 0 | 703679.4391 | 266.777 | 0
7567 | 11 | 0 | 0 | 0.65103 | 26.627 | 0 | 0 | 0 | 0 | 26.627 | 0 | 40000 | 0 | 703679.4391 | 289.8572 | 0
7568 | 11 | 1 | 0.094716 | 0.59644 | 51.7483 | 200 | 51.7483 | 148.2517 | 200 | 0 | 0 | 39800 | 200 | 703879.4391 | 141.6055 | 0
7569 | 11 | 1 | 0.44352 | 0.66521 | 155.2958 | 200 | 155.2958 | 44.7042 | 200 | 0 | 0 | 39600 | 200 | 704079.4391 | 96.9013 | 0
7570 | 11 | 0 | 0.83569 | 0.77214 | 272.9288 | 0 | 0 | 0 | 0 | 180 | 92.9288 | 39600 | 92.9288 | 704172.3679 | 252.9253 | 0
7571 | 11 | 0 | 1 | 0.37568 | 304.1653 | 0 | 0 | 0 | 0 | 180 | 124.1653 | 39600 | 124.1653 | 704296.5332 | 408.9493 | 0
7572 | 11 | 0 | 1 | 0.38509 | 304.5503 | 0 | 0 | 0 | 0 | 117.5135 | 187.0367 | 39600 | 187.0367 | 704483.5699 | 510.81 | 0
7573 | 11 | 0 | 1 | 0.42097 | 306.0175 | 0 | 0 | 0 | 0 | 0 | 200 | 39600 | 200 | 704683.5699 | 510.81 | 106.0175
7574 | 11 | 0 | 1 | 0.33034 | 302.3109 | 0 | 0 | 0 | 0 | 0 | 200 | 39600 | 200 | 704883.5699 | 510.81 | 102.3109
7575 | 11 | 0 | 1 | 0.28298 | 300.3738 | 0 | 0 | 0 | 0 | 0 | 200 | 39600 | 200 | 705083.5699 | 510.81 | 100.3738
7576 | 11 | 0 | 0.83569 | 0.37399 | 256.6442 | 0 | 0 | 0 | 0 | 0 | 200 | 39600 | 200 | 705283.5699 | 510.81 | 56.6442
7577 | 11 | 0 | 0.44352 | 0.38583 | 143.8691 | 0 | 0 | 0 | 0 | 0 | 143.8691 | 39600 | 143.8691 | 705427.439 | 510.81 | 0
7578 | 11 | 0 | 0.094716 | 0.35481 | 41.8659 | 0 | 0 | 0 | 0 | 0 | 41.8659 | 39600 | 41.8659 | 705469.3049 | 510.81 | 0
7579 | 11 | 0 | 0 | 0.532 | 21.7588 | 0 | 0 | 0 | 0 | 0 | 21.7588 | 39600 | 21.7588 | 705491.0637 | 510.81 | 0
7580 | 11 | 1 | 0 | 0.40234 | 16.4557 | 200 | 16.4557 | 180 | 196.4557 | 0 | 0 | 39400 | 196.4557 | 705687.5194 | 330.81 | 0
7581 | 11 | 1 | 0 | 0.39632 | 16.2097 | 200 | 16.2097 | 180 | 196.2097 | 0 | 0 | 39200 | 196.2097 | 705883.7291 | 150.81 | 0
7582 | 11 | 0 | 0 | 0.50999 | 20.8586 | 0 | 0 | 0 | 0 | 20.8586 | 0 | 39200 | 0 | 705883.7291 | 168.8902 | 0
7583 | 11 | 0 | 0 | 0.30739 | 12.5723 | 0 | 0 | 0 | 0 | 12.5723 | 0 | 39200 | 0 | 705883.7291 | 179.7879 | 0
7584 | 11 | 0 | 0 | 0.22343 | 9.1381 | 0 | 0 | 0 | 0 | 9.1381 | 0 | 39200 | 0 | 705883.7291 | 187.7087 | 0
7585 | 11 | 0 | 0 | 0.17802 | 7.2811 | 0 | 0 | 0 | 0 | 7.2811 | 0 | 39200 | 0 | 705883.7291 | 194.02 | 0
7586 | 11 | 0 | 0 | 0.20101 | 8.2215 | 0 | 0 | 0 | 0 | 8.2215 | 0 | 39200 | 0 | 705883.7291 | 201.1464 | 0
7587 | 11 | 0 | 0 | 0.20887 | 8.5427 | 0 | 0 | 0 | 0 | 8.5427 | 0 | 39200 | 0 | 705883.7291 | 208.5512 | 0
7588 | 11 | 0 | 0 | 0.23043 | 9.4246 | 0 | 0 | 0 | 0 | 9.4246 | 0 | 39200 | 0 | 705883.7291 | 216.7204 | 0
7589 | 11 | 0 | 0 | 0.2158 | 8.8264 | 0 | 0 | 0 | 0 | 8.8264 | 0 | 39200 | 0 | 705883.7291 | 224.3712 | 0
7590 | 11 | 0 | 0 | 0.11714 | 4.7911 | 0 | 0 | 0 | 0 | 4.7911 | 0 | 39200 | 0 | 705883.7291 | 228.5241 | 0
7591 | 11 | 0 | 0 | 0.10197 | 4.1707 | 0 | 0 | 0 | 0 | 4.1707 | 0 | 39200 | 0 | 705883.7291 | 232.1392 | 0
7592 | 11 | 1 | 0.092844 | 0.070088 | 29.6799 | 200 | 29.6799 | 170.3201 | 200 | 0 | 0 | 39000 | 200 | 706083.7291 | 61.8191 | 0
7593 | 11 | 1 | 0.43475 | 0.086937 | 129.1115 | 200 | 129.1115 | 61.8191 | 190.9307 | 0 | 0 | 38800 | 190.9307 | 706274.6598 | 0 | 0
7594 | 11 | 0 | 0.81917 | 0.068761 | 239.388 | 0 | 0 | 0 | 0 | 180 | 59.388 | 38800 | 59.388 | 706334.0478 | 156.024 | 0
7595 | 11 | 0 | 1 | 0.07291 | 291.782 | 0 | 0 | 0 | 0 | 180 | 111.782 | 38800 | 111.782 | 706445.8298 | 312.048 | 0
7596 | 11 | 0 | 1 | 0.098542 | 292.8304 | 0 | 0 | 0 | 0 | 180 | 112.8304 | 38800 | 112.8304 | 706558.6602 | 468.072 | 0
7597 | 11 | 0 | 1 | 0.13446 | 294.2996 | 0 | 0 | 0 | 0 | 49.3055 | 200 | 38800 | 200 | 706758.6602 | 510.81 | 44.9941
7598 | 11 | 0 | 1 | 0.14147 | 294.5863 | 0 | 0 | 0 | 0 | 0 | 200 | 38800 | 200 | 706958.6602 | 510.81 | 94.5863
7599 | 11 | 0 | 1 | 0.2133 | 297.5241 | 0 | 0 | 0 | 0 | 0 | 200 | 38800 | 200 | 707158.6602 | 510.81 | 97.5241
7600 | 11 | 0 | 0.81917 | 0.27987 | 248.0226 | 0 | 0 | 0 | 0 | 0 | 200 | 38800 | 200 | 707358.6602 | 510.81 | 48.0226
7601 | 11 | 0 | 0.43475 | 0.28666 | 137.2802 | 0 | 0 | 0 | 0 | 0 | 137.2802 | 38800 | 137.2802 | 707495.9404 | 510.81 | 0
7602 | 11 | 0 | 0.092844 | 0.46526 | 45.8423 | 0 | 0 | 0 | 0 | 0 | 45.8423 | 38800 | 45.8423 | 707541.7827 | 510.81 | 0
7603 | 11 | 0 | 0 | 0.50128 | 20.5024 | 0 | 0 | 0 | 0 | 0 | 20.5024 | 38800 | 20.5024 | 707562.2851 | 510.81 | 0
7604 | 11 | 1 | 0 | 0.30655 | 12.538 | 200 | 12.538 | 180 | 192.538 | 0 | 0 | 38600 | 192.538 | 707754.8231 | 330.81 | 0
7605 | 11 | 1 | 0 | 0.40289 | 16.4784 | 200 | 16.4784 | 180 | 196.4784 | 0 | 0 | 38400 | 196.4784 | 707951.3015 | 150.81 | 0
7606 | 11 | 0 | 0 | 0.42079 | 17.2104 | 0 | 0 | 0 | 0 | 17.2104 | 0 | 38400 | 0 | 707951.3015 | 165.7279 | 0
7607 | 11 | 0 | 0 | 0.35013 | 14.3204 | 0 | 0 | 0 | 0 | 14.3204 | 0 | 38400 | 0 | 707951.3015 | 178.1409 | 0
7608 | 11 | 0 | 0 | 0.42806 | 17.5074 | 0 | 0 | 0 | 0 | 17.5074 | 0 | 38400 | 0 | 707951.3015 | 193.3163 | 0
7609 | 11 | 0 | 0 | 0.58714 | 24.0142 | 0 | 0 | 0 | 0 | 24.0142 | 0 | 38400 | 0 | 707951.3015 | 214.1318 | 0
7610 | 11 | 0 | 0 | 0.38359 | 15.689 | 0 | 0 | 0 | 0 | 15.689 | 0 | 38400 | 0 | 707951.3015 | 227.731 | 0
7611 | 11 | 0 | 0 | 0.32571 | 13.3216 | 0 | 0 | 0 | 0 | 13.3216 | 0 | 38400 | 0 | 707951.3015 | 239.2782 | 0
7612 | 11 | 0 | 0 | 0.22956 | 9.3892 | 0 | 0 | 0 | 0 | 9.3892 | 0 | 38400 | 0 | 707951.3015 | 247.4168 | 0
7613 | 11 | 0 | 0 | 0.18357 | 7.508 | 0 | 0 | 0 | 0 | 7.508 | 0 | 38400 | 0 | 707951.3015 | 253.9247 | 0
7614 | 11 | 0 | 0 | 0.24302 | 9.9397 | 0 | 0 | 0 | 0 | 9.9397 | 0 | 38400 | 0 | 707951.3015 | 262.5404 | 0
7615 | 11 | 0 | 0 | 0.21038 | 8.6045 | 0 | 0 | 0 | 0 | 8.6045 | 0 | 38400 | 0 | 707951.3015 | 269.9988 | 0
7616 | 11 | 1 | 0.082503 | 0.14454 | 29.7387 | 200 | 29.7387 | 170.2613 | 200 | 0 | 0 | 38200 | 200 | 708151.3015 | 99.7374 | 0
7617 | 11 | 1 | 0.38633 | 0.14624 | 117.5523 | 200 | 117.5523 | 82.4477 | 200 | 0 | 0 | 38000 | 200 | 708351.3015 | 17.2897 | 0
7618 | 11 | 0 | 0.72793 | 0.15446 | 216.5435 | 0 | 0 | 0 | 0 | 180 | 36.5435 | 38000 | 36.5435 | 708387.8449 | 173.3137 | 0
7619 | 11 | 0 | 1 | 0.14771 | 294.8411 | 0 | 0 | 0 | 0 | 180 | 114.8411 | 38000 | 114.8411 | 708502.6861 | 329.3377 | 0
7620 | 11 | 0 | 1 | 0.15203 | 295.0179 | 0 | 0 | 0 | 0 | 180 | 115.0179 | 38000 | 115.0179 | 708617.704 | 485.3617 | 0
7621 | 11 | 0 | 1 | 0.0946 | 292.6691 | 0 | 0 | 0 | 0 | 29.3589 | 200 | 38000 | 200 | 708817.704 | 510.81 | 63.3103
7622 | 11 | 0 | 1 | 0.162 | 295.426 | 0 | 0 | 0 | 0 | 0 | 200 | 38000 | 200 | 709017.704 | 510.81 | 95.426
7623 | 11 | 0 | 1 | 0.19239 | 296.6689 | 0 | 0 | 0 | 0 | 0 | 200 | 38000 | 200 | 709217.704 | 510.81 | 96.6689
7624 | 11 | 0 | 0.72793 | 0.22473 | 219.4175 | 0 | 0 | 0 | 0 | 0 | 200 | 38000 | 200 | 709417.704 | 510.81 | 19.4175
7625 | 11 | 0 | 0.38633 | 0.1866 | 119.2032 | 0 | 0 | 0 | 0 | 0 | 119.2032 | 38000 | 119.2032 | 709536.9072 | 510.81 | 0
7626 | 11 | 0 | 0.082503 | 0.2327 | 33.3444 | 0 | 0 | 0 | 0 | 0 | 33.3444 | 38000 | 33.3444 | 709570.2516 | 510.81 | 0
7627 | 11 | 0 | 0 | 0.31614 | 12.9302 | 0 | 0 | 0 | 0 | 0 | 12.9302 | 38000 | 12.9302 | 709583.1818 | 510.81 | 0
7628 | 11 | 1 | 0 | 0.24979 | 10.2163 | 200 | 10.2163 | 180 | 190.2163 | 0 | 0 | 37800 | 190.2163 | 709773.3981 | 330.81 | 0
7629 | 11 | 1 | 0 | 0.21594 | 8.8319 | 200 | 8.8319 | 180 | 188.8319 | 0 | 0 | 37600 | 188.8319 | 709962.23 | 150.81 | 0
7630 | 11 | 0 | 0 | 0.20945 | 8.5665 | 0 | 0 | 0 | 0 | 8.5665 | 0 | 37600 | 0 | 709962.23 | 158.2354 | 0
7631 | 11 | 0 | 0 | 0.25015 | 10.2311 | 0 | 0 | 0 | 0 | 10.2311 | 0 | 37600 | 0 | 709962.23 | 167.1038 | 0
7632 | 11 | 0 | 0 | 0.17986 | 7.3562 | 0 | 0 | 0 | 0 | 7.3562 | 0 | 37600 | 0 | 709962.23 | 173.4801 | 0
7633 | 11 | 0 | 0 | 0.22536 | 9.2171 | 0 | 0 | 0 | 0 | 9.2171 | 0 | 37600 | 0 | 709962.23 | 181.4695 | 0
7634 | 11 | 0 | 0 | 0.14367 | 5.8759 | 0 | 0 | 0 | 0 | 5.8759 | 0 | 37600 | 0 | 709962.23 | 186.5628 | 0
7635 | 11 | 0 | 0 | 0.19039 | 7.7868 | 0 | 0 | 0 | 0 | 7.7868 | 0 | 37600 | 0 | 709962.23 | 193.3123 | 0
7636 | 11 | 0 | 0 | 0.20546 | 8.4034 | 0 | 0 | 0 | 0 | 8.4034 | 0 | 37600 | 0 | 709962.23 | 200.5964 | 0
7637 | 11 | 0 | 0 | 0.17702 | 7.24 | 0 | 0 | 0 | 0 | 7.24 | 0 | 37600 | 0 | 709962.23 | 206.8721 | 0
7638 | 11 | 0 | 0 | 0.24929 | 10.1958 | 0 | 0 | 0 | 0 | 10.1958 | 0 | 37600 | 0 | 709962.23 | 215.7098 | 0
7639 | 11 | 0 | 0 | 0.19501 | 7.9761 | 0 | 0 | 0 | 0 | 7.9761 | 0 | 37600 | 0 | 709962.23 | 222.6235 | 0
7640 | 11 | 1 | 0.079686 | 0.21883 | 31.9635 | 200 | 31.9635 | 168.0365 | 200 | 0 | 0 | 37400 | 200 | 710162.23 | 54.587 | 0
7641 | 11 | 1 | 0.37314 | 0.21803 | 116.679 | 200 | 116.679 | 54.587 | 171.266 | 0 | 0 | 37200 | 171.266 | 710333.496 | 0 | 0
7642 | 11 | 0 | 0.70307 | 0.3226 | 216.2421 | 0 | 0 | 0 | 0 | 180 | 36.2421 | 37200 | 36.2421 | 710369.7381 | 156.024 | 0
7643 | 11 | 0 | 0.99363 | 0.28679 | 298.6911 | 0 | 0 | 0 | 0 | 180 | 118.6911 | 37200 | 118.6911 | 710488.4292 | 312.048 | 0
7644 | 11 | 0 | 1 | 0.30169 | 301.139 | 0 | 0 | 0 | 0 | 180 | 121.139 | 37200 | 121.139 | 710609.5683 | 468.072 | 0
7645 | 11 | 0 | 1 | 0.30359 | 301.2167 | 0 | 0 | 0 | 0 | 49.3055 | 200 | 37200 | 200 | 710809.5683 | 510.81 | 51.9112
7646 | 11 | 0 | 1 | 0.30373 | 301.2224 | 0 | 0 | 0 | 0 | 0 | 200 | 37200 | 200 | 711009.5683 | 510.81 | 101.2224
7647 | 11 | 0 | 0.99363 | 0.27879 | 298.3641 | 0 | 0 | 0 | 0 | 0 | 200 | 37200 | 200 | 711209.5683 | 510.81 | 98.3641
7648 | 11 | 0 | 0.70307 | 0.31552 | 215.9526 | 0 | 0 | 0 | 0 | 0 | 200 | 37200 | 200 | 711409.5683 | 510.81 | 15.9526
7649 | 11 | 0 | 0.37314 | 0.26886 | 118.758 | 0 | 0 | 0 | 0 | 0 | 118.758 | 37200 | 118.758 | 711528.3262 | 510.81 | 0
7650 | 11 | 0 | 0.079686 | 0.17811 | 30.2981 | 0 | 0 | 0 | 0 | 0 | 30.2981 | 37200 | 30.2981 | 711558.6244 | 510.81 | 0
7651 | 11 | 0 | 0 | 0.18873 | 7.7189 | 0 | 0 | 0 | 0 | 0 | 7.7189 | 37200 | 7.7189 | 711566.3433 | 510.81 | 0
7652 | 11 | 1 | 0 | 0.27552 | 11.2687 | 200 | 11.2687 | 180 | 191.2687 | 0 | 0 | 37000 | 191.2687 | 711757.612 | 330.81 | 0
7653 | 11 | 1 | 0 | 0.2678 | 10.9531 | 200 | 10.9531 | 180 | 190.9531 | 0 | 0 | 36800 | 190.9531 | 711948.5651 | 150.81 | 0
7654 | 11 | 0 | 0 | 0.22008 | 9.0013 | 0 | 0 | 0 | 0 | 9.0013 | 0 | 36800 | 0 | 711948.5651 | 158.6123 | 0
7655 | 11 | 0 | 0 | 0.1183 | 4.8383 | 0 | 0 | 0 | 0 | 4.8383 | 0 | 36800 | 0 | 711948.5651 | 162.8061 | 0
7656 | 11 | 0 | 0 | 0.12462 | 5.0971 | 0 | 0 | 0 | 0 | 5.0971 | 0 | 36800 | 0 | 711948.5651 | 167.2243 | 0
7657 | 11 | 0 | 0 | 0.11572 | 4.7329 | 0 | 0 | 0 | 0 | 4.7329 | 0 | 36800 | 0 | 711948.5651 | 171.3267 | 0
7658 | 11 | 0 | 0 | 0.116 | 4.7444 | 0 | 0 | 0 | 0 | 4.7444 | 0 | 36800 | 0 | 711948.5651 | 175.4392 | 0
7659 | 11 | 0 | 0 | 0.10374 | 4.2428 | 0 | 0 | 0 | 0 | 4.2428 | 0 | 36800 | 0 | 711948.5651 | 179.1169 | 0
7660 | 11 | 0 | 0 | 0.11845 | 4.8447 | 0 | 0 | 0 | 0 | 4.8447 | 0 | 36800 | 0 | 711948.5651 | 183.3162 | 0
7661 | 11 | 0 | 0 | 0.11018 | 4.5065 | 0 | 0 | 0 | 0 | 4.5065 | 0 | 36800 | 0 | 711948.5651 | 187.2225 | 0
7662 | 11 | 0 | 0 | 0.15538 | 6.3552 | 0 | 0 | 0 | 0 | 6.3552 | 0 | 36800 | 0 | 711948.5651 | 192.7311 | 0
7663 | 11 | 0 | 0 | 0.11394 | 4.6601 | 0 | 0 | 0 | 0 | 4.6601 | 0 | 36800 | 0 | 711948.5651 | 196.7705 | 0
7664 | 11 | 1 | 0.07692 | 0.11462 | 26.9026 | 200 | 26.9026 | 173.0974 | 200 | 0 | 0 | 36600 | 200 | 712148.5651 | 23.6731 | 0
7665 | 11 | 1 | 0.36019 | 0.081798 | 107.3673 | 200 | 107.3673 | 23.6731 | 131.0404 | 0 | 0 | 36400 | 131.0404 | 712279.6055 | 0 | 0
7666 | 11 | 0 | 0.67867 | 0.09338 | 199.8203 | 0 | 0 | 0 | 0 | 180 | 19.8203 | 36400 | 19.8203 | 712299.4258 | 156.024 | 0
7667 | 11 | 0 | 0.95915 | 0.055987 | 279.2924 | 0 | 0 | 0 | 0 | 180 | 99.2924 | 36400 | 99.2924 | 712398.7182 | 312.048 | 0
7668 | 11 | 0 | 1 | 0.071744 | 291.7343 | 0 | 0 | 0 | 0 | 180 | 111.7343 | 36400 | 111.7343 | 712510.4525 | 468.072 | 0
7669 | 11 | 0 | 1 | 0.082538 | 292.1758 | 0 | 0 | 0 | 0 | 49.3055 | 200 | 36400 | 200 | 712710.4525 | 510.81 | 42.8703
7670 | 11 | 0 | 1 | 0.11026 | 293.3095 | 0 | 0 | 0 | 0 | 0 | 200 | 36400 | 200 | 712910.4525 | 510.81 | 93.3095
7671 | 11 | 0 | 0.95915 | 0.11971 | 281.8986 | 0 | 0 | 0 | 0 | 0 | 200 | 36400 | 200 | 713110.4525 | 510.81 | 81.8986
7672 | 11 | 0 | 0.67867 | 0.11259 | 200.606 | 0 | 0 | 0 | 0 | 0 | 200 | 36400 | 200 | 713310.4525 | 510.81 | 0.60598
7673 | 11 | 0 | 0.36019 | 0.10533 | 108.3298 | 0 | 0 | 0 | 0 | 0 | 108.3298 | 36400 | 108.3298 | 713418.7823 | 510.81 | 0
7674 | 11 | 0 | 0.07692 | 0.078135 | 25.4102 | 0 | 0 | 0 | 0 | 0 | 25.4102 | 36400 | 25.4102 | 713444.1925 | 510.81 | 0
7675 | 11 | 0 | 0 | 0.070785 | 2.8951 | 0 | 0 | 0 | 0 | 0 | 2.8951 | 36400 | 2.8951 | 713447.0876 | 510.81 | 0
7676 | 11 | 1 | 0 | 0.084012 | 3.4361 | 200 | 3.4361 | 180 | 183.4361 | 0 | 0 | 36200 | 183.4361 | 713630.5237 | 330.81 | 0
7677 | 11 | 1 | 0 | 0.10388 | 4.2487 | 200 | 4.2487 | 180 | 184.2487 | 0 | 0 | 36000 | 184.2487 | 713814.7724 | 150.81 | 0
7678 | 11 | 0 | 0 | 0.12608 | 5.1565 | 0 | 0 | 0 | 0 | 5.1565 | 0 | 36000 | 0 | 713814.7724 | 155.2797 | 0
7679 | 11 | 0 | 0 | 0.12846 | 5.2538 | 0 | 0 | 0 | 0 | 5.2538 | 0 | 36000 | 0 | 713814.7724 | 159.8337 | 0
7680 | 11 | 0 | 0 | 0.14583 | 5.9644 | 0 | 0 | 0 | 0 | 5.9644 | 0 | 36000 | 0 | 713814.7724 | 165.0036 | 0
7681 | 11 | 0 | 0 | 0.16123 | 6.5943 | 0 | 0 | 0 | 0 | 6.5943 | 0 | 36000 | 0 | 713814.7724 | 170.7196 | 0
7682 | 11 | 0 | 0 | 0.22917 | 9.3731 | 0 | 0 | 0 | 0 | 9.3731 | 0 | 36000 | 0 | 713814.7724 | 178.8443 | 0
7683 | 11 | 0 | 0 | 0.13899 | 5.6848 | 0 | 0 | 0 | 0 | 5.6848 | 0 | 36000 | 0 | 713814.7724 | 183.7719 | 0
7684 | 11 | 0 | 0 | 0.15146 | 6.1949 | 0 | 0 | 0 | 0 | 6.1949 | 0 | 36000 | 0 | 713814.7724 | 189.1416 | 0
7685 | 11 | 0 | 0 | 0.12377 | 5.062 | 0 | 0 | 0 | 0 | 5.062 | 0 | 36000 | 0 | 713814.7724 | 193.5294 | 0
7686 | 11 | 0 | 0 | 0.108 | 4.4171 | 0 | 0 | 0 | 0 | 4.4171 | 0 | 36000 | 0 | 713814.7724 | 197.3581 | 0
7687 | 11 | 0 | 0 | 0.081818 | 3.3464 | 0 | 0 | 0 | 0 | 3.3464 | 0 | 36000 | 0 | 713814.7724 | 200.2588 | 0
7688 | 11 | 1 | 0.079729 | 0.065359 | 25.6989 | 200 | 25.6989 | 174.3011 | 200 | 0 | 0 | 35800 | 200 | 714014.7724 | 25.9577 | 0
7689 | 11 | 1 | 0.37334 | 0.057156 | 110.1586 | 200 | 110.1586 | 25.9577 | 136.1162 | 0 | 0 | 35600 | 136.1162 | 714150.8886 | 0 | 0
7690 | 11 | 0 | 0.70346 | 0.07158 | 206.0869 | 0 | 0 | 0 | 0 | 180 | 26.0869 | 35600 | 26.0869 | 714176.9755 | 156.024 | 0
7691 | 11 | 0 | 0.99418 | 0.11869 | 291.9735 | 0 | 0 | 0 | 0 | 180 | 111.9735 | 35600 | 111.9735 | 714288.9489 | 312.048 | 0
7692 | 11 | 0 | 1 | 0.094961 | 292.6839 | 0 | 0 | 0 | 0 | 180 | 112.6839 | 35600 | 112.6839 | 714401.6328 | 468.072 | 0
7693 | 11 | 0 | 1 | 0.11217 | 293.3877 | 0 | 0 | 0 | 0 | 49.3055 | 200 | 35600 | 200 | 714601.6328 | 510.81 | 44.0822
7694 | 11 | 0 | 1 | 0.12974 | 294.1062 | 0 | 0 | 0 | 0 | 0 | 200 | 35600 | 200 | 714801.6328 | 510.81 | 94.1062
7695 | 11 | 0 | 0.99418 | 0.14223 | 292.936 | 0 | 0 | 0 | 0 | 0 | 200 | 35600 | 200 | 715001.6328 | 510.81 | 92.936
7696 | 11 | 0 | 0.70346 | 0.13659 | 208.7459 | 0 | 0 | 0 | 0 | 0 | 200 | 35600 | 200 | 715201.6328 | 510.81 | 8.7459
7697 | 11 | 0 | 0.37334 | 0.1123 | 112.414 | 0 | 0 | 0 | 0 | 0 | 112.414 | 35600 | 112.414 | 715314.0468 | 510.81 | 0
7698 | 11 | 0 | 0.079729 | 0.16536 | 29.7888 | 0 | 0 | 0 | 0 | 0 | 29.7888 | 35600 | 29.7888 | 715343.8356 | 510.81 | 0
7699 | 11 | 0 | 0 | 0.14965 | 6.1206 | 0 | 0 | 0 | 0 | 0 | 6.1206 | 35600 | 6.1206 | 715349.9562 | 510.81 | 0
7700 | 11 | 1 | 0 | 0.15629 | 6.3923 | 200 | 6.3923 | 180 | 186.3923 | 0 | 0 | 35400 | 186.3923 | 715536.3485 | 330.81 | 0
7701 | 11 | 1 | 0 | 0.11371 | 4.6509 | 200 | 4.6509 | 180 | 184.6509 | 0 | 0 | 35200 | 184.6509 | 715720.9994 | 150.81 | 0
7702 | 11 | 0 | 0 | 0.1106 | 4.5237 | 0 | 0 | 0 | 0 | 4.5237 | 0 | 35200 | 0 | 715720.9994 | 154.7311 | 0
7703 | 11 | 0 | 0 | 0.068325 | 2.7945 | 0 | 0 | 0 | 0 | 2.7945 | 0 | 35200 | 0 | 715720.9994 | 157.1534 | 0
7704 | 11 | 0 | 0 | 0.07811 | 3.1947 | 0 | 0 | 0 | 0 | 3.1947 | 0 | 35200 | 0 | 715720.9994 | 159.9226 | 0
7705 | 11 | 0 | 0 | 0.060519 | 2.4752 | 0 | 0 | 0 | 0 | 2.4752 | 0 | 35200 | 0 | 715720.9994 | 162.0681 | 0
7706 | 11 | 0 | 0 | 0.064877 | 2.6535 | 0 | 0 | 0 | 0 | 2.6535 | 0 | 35200 | 0 | 715720.9994 | 164.3681 | 0
7707 | 11 | 0 | 0 | 0.052849 | 2.1615 | 0 | 0 | 0 | 0 | 2.1615 | 0 | 35200 | 0 | 715720.9994 | 166.2417 | 0
7708 | 11 | 0 | 0 | 0.081366 | 3.3279 | 0 | 0 | 0 | 0 | 3.3279 | 0 | 35200 | 0 | 715720.9994 | 169.1263 | 0
7709 | 11 | 0 | 0 | 0.119 | 4.8669 | 0 | 0 | 0 | 0 | 4.8669 | 0 | 35200 | 0 | 715720.9994 | 173.345 | 0
7710 | 11 | 0 | 0 | 0.11221 | 4.5893 | 0 | 0 | 0 | 0 | 4.5893 | 0 | 35200 | 0 | 715720.9994 | 177.323 | 0
7711 | 11 | 0 | 0 | 0.11906 | 4.8694 | 0 | 0 | 0 | 0 | 4.8694 | 0 | 35200 | 0 | 715720.9994 | 181.5438 | 0
7712 | 11 | 1 | 0.084538 | 0.12765 | 29.6357 | 200 | 29.6357 | 170.3643 | 200 | 0 | 0 | 35000 | 200 | 715920.9994 | 11.1795 | 0
7713 | 11 | 1 | 0.39586 | 0.15882 | 120.8201 | 200 | 120.8201 | 11.1795 | 131.9996 | 0 | 0 | 34800 | 131.9996 | 716052.999 | 0 | 0
7714 | 11 | 0 | 0.74589 | 0.15588 | 221.7886 | 0 | 0 | 0 | 0 | 180 | 41.7886 | 34800 | 41.7886 | 716094.7877 | 156.024 | 0
7715 | 11 | 0 | 1 | 0.12659 | 293.9777 | 0 | 0 | 0 | 0 | 180 | 113.9777 | 34800 | 113.9777 | 716208.7653 | 312.048 | 0
7716 | 11 | 0 | 1 | 0.10096 | 292.9291 | 0 | 0 | 0 | 0 | 180 | 112.9291 | 34800 | 112.9291 | 716321.6945 | 468.072 | 0
7717 | 11 | 0 | 1 | 0.051866 | 290.9213 | 0 | 0 | 0 | 0 | 49.3055 | 200 | 34800 | 200 | 716521.6945 | 510.81 | 41.6158
7718 | 11 | 0 | 1 | 0.059767 | 291.2445 | 0 | 0 | 0 | 0 | 0 | 200 | 34800 | 200 | 716721.6945 | 510.81 | 91.2445
7719 | 11 | 0 | 1 | 0.057217 | 291.1402 | 0 | 0 | 0 | 0 | 0 | 200 | 34800 | 200 | 716921.6945 | 510.81 | 91.1402
7720 | 11 | 0 | 0.74589 | 0.045423 | 217.2711 | 0 | 0 | 0 | 0 | 0 | 200 | 34800 | 200 | 717121.6945 | 510.81 | 17.2711
7721 | 11 | 0 | 0.39586 | 0.03764 | 115.8638 | 0 | 0 | 0 | 0 | 0 | 115.8638 | 34800 | 115.8638 | 717237.5583 | 510.81 | 0
7722 | 11 | 0 | 0.084538 | 0.063351 | 27.0056 | 0 | 0 | 0 | 0 | 0 | 27.0056 | 34800 | 27.0056 | 717264.564 | 510.81 | 0
7723 | 11 | 0 | 0 | 0.081004 | 3.3131 | 0 | 0 | 0 | 0 | 0 | 3.3131 | 34800 | 3.3131 | 717267.877 | 510.81 | 0
7724 | 11 | 1 | 0 | 0.078749 | 3.2208 | 200 | 3.2208 | 180 | 183.2208 | 0 | 0 | 34600 | 183.2208 | 717451.0979 | 330.81 | 0
7725 | 11 | 1 | 0 | 0.073647 | 3.0122 | 200 | 3.0122 | 180 | 183.0122 | 0 | 0 | 34400 | 183.0122 | 717634.11 | 150.81 | 0
7726 | 11 | 0 | 0 | 0.076106 | 3.1127 | 0 | 0 | 0 | 0 | 3.1127 | 0 | 34400 | 0 | 717634.11 | 153.5081 | 0
7727 | 11 | 0 | 0 | 0.1188 | 4.859 | 0 | 0 | 0 | 0 | 4.859 | 0 | 34400 | 0 | 717634.11 | 157.7199 | 0
7728 | 11 | 0 | 0 | 0.11701 | 4.7856 | 0 | 0 | 0 | 0 | 4.7856 | 0 | 34400 | 0 | 717634.11 | 161.868 | 0
7729 | 11 | 0 | 0 | 0.12167 | 4.9763 | 0 | 0 | 0 | 0 | 4.9763 | 0 | 34400 | 0 | 717634.11 | 166.1815 | 0
7730 | 11 | 0 | 0 | 0.16322 | 6.6758 | 0 | 0 | 0 | 0 | 6.6758 | 0 | 34400 | 0 | 717634.11 | 171.9681 | 0
7731 | 11 | 0 | 0 | 0.1777 | 7.268 | 0 | 0 | 0 | 0 | 7.268 | 0 | 34400 | 0 | 717634.11 | 178.268 | 0
7732 | 11 | 0 | 0 | 0.23484 | 9.6049 | 0 | 0 | 0 | 0 | 9.6049 | 0 | 34400 | 0 | 717634.11 | 186.5935 | 0
7733 | 11 | 0 | 0 | 0.20287 | 8.2972 | 0 | 0 | 0 | 0 | 8.2972 | 0 | 34400 | 0 | 717634.11 | 193.7856 | 0
7734 | 11 | 0 | 0 | 0.1748 | 7.1492 | 0 | 0 | 0 | 0 | 7.1492 | 0 | 34400 | 0 | 717634.11 | 199.9825 | 0
7735 | 11 | 0 | 0 | 0.14096 | 5.7653 | 0 | 0 | 0 | 0 | 5.7653 | 0 | 34400 | 0 | 717634.11 | 204.9799 | 0
7736 | 11 | 1 | 0.074626 | 0.14987 | 27.6818 | 200 | 27.6818 | 172.3182 | 200 | 0 | 0 | 34200 | 200 | 717834.11 | 32.6617 | 0
7737 | 11 | 1 | 0.34944 | 0.18359 | 108.4277 | 200 | 108.4277 | 32.6617 | 141.0894 | 0 | 0 | 34000 | 141.0894 | 717975.1995 | 0 | 0
7738 | 11 | 0 | 0.65843 | 0.15026 | 196.3003 | 0 | 0 | 0 | 0 | 180 | 16.3003 | 34000 | 16.3003 | 717991.4998 | 156.024 | 0
7739 | 11 | 0 | 0.93054 | 0.18676 | 276.3785 | 0 | 0 | 0 | 0 | 180 | 96.3785 | 34000 | 96.3785 | 718087.8783 | 312.048 | 0
7740 | 11 | 0 | 1 | 0.22932 | 298.1793 | 0 | 0 | 0 | 0 | 180 | 118.1793 | 34000 | 118.1793 | 718206.0575 | 468.072 | 0
7741 | 11 | 0 | 1 | 0.14452 | 294.7109 | 0 | 0 | 0 | 0 | 49.3055 | 200 | 34000 | 200 | 718406.0575 | 510.81 | 45.4054
7742 | 11 | 0 | 1 | 0.14377 | 294.68 | 0 | 0 | 0 | 0 | 0 | 200 | 34000 | 200 | 718606.0575 | 510.81 | 94.68
7743 | 11 | 0 | 0.93054 | 0.10797 | 273.1557 | 0 | 0 | 0 | 0 | 0 | 200 | 34000 | 200 | 718806.0575 | 510.81 | 73.1557
7744 | 11 | 0 | 0.65843 | 0.078839 | 193.3791 | 0 | 0 | 0 | 0 | 0 | 193.3791 | 34000 | 193.3791 | 718999.4366 | 510.81 | 0
7745 | 11 | 0 | 0.34944 | 0.083676 | 104.3412 | 0 | 0 | 0 | 0 | 0 | 104.3412 | 34000 | 104.3412 | 719103.7778 | 510.81 | 0
7746 | 11 | 0 | 0.074626 | 0.077916 | 24.7388 | 0 | 0 | 0 | 0 | 0 | 24.7388 | 34000 | 24.7388 | 719128.5166 | 510.81 | 0
7747 | 11 | 0 | 0 | 0.06936 | 2.8368 | 0 | 0 | 0 | 0 | 0 | 2.8368 | 34000 | 2.8368 | 719131.3534 | 510.81 | 0
7748 | 11 | 1 | 0 | 0.084293 | 3.4476 | 200 | 3.4476 | 180 | 183.4476 | 0 | 0 | 33800 | 183.4476 | 719314.801 | 330.81 | 0
7749 | 11 | 1 | 0 | 0.10152 | 4.1522 | 200 | 4.1522 | 180 | 184.1522 | 0 | 0 | 33600 | 184.1522 | 719498.9533 | 150.81 | 0
7750 | 11 | 0 | 0 | 0.10973 | 4.4881 | 0 | 0 | 0 | 0 | 4.4881 | 0 | 33600 | 0 | 719498.9533 | 154.7003 | 0
7751 | 11 | 0 | 0 | 0.12587 | 5.148 | 0 | 0 | 0 | 0 | 5.148 | 0 | 33600 | 0 | 719498.9533 | 159.1626 | 0
7752 | 11 | 0 | 0 | 0.21626 | 8.8451 | 0 | 0 | 0 | 0 | 8.8451 | 0 | 33600 | 0 | 719498.9533 | 166.8295 | 0
7753 | 11 | 0 | 0 | 0.27181 | 11.1172 | 0 | 0 | 0 | 0 | 11.1172 | 0 | 33600 | 0 | 719498.9533 | 176.4659 | 0
7754 | 11 | 0 | 0 | 0.29927 | 12.2401 | 0 | 0 | 0 | 0 | 12.2401 | 0 | 33600 | 0 | 719498.9533 | 187.0756 | 0
7755 | 11 | 0 | 0 | 0.25682 | 10.5041 | 0 | 0 | 0 | 0 | 10.5041 | 0 | 33600 | 0 | 719498.9533 | 196.1806 | 0
7756 | 11 | 0 | 0 | 0.22804 | 9.327 | 0 | 0 | 0 | 0 | 9.327 | 0 | 33600 | 0 | 719498.9533 | 204.2652 | 0
7757 | 11 | 0 | 0 | 0.28909 | 11.8237 | 0 | 0 | 0 | 0 | 11.8237 | 0 | 33600 | 0 | 719498.9533 | 214.514 | 0
7758 | 11 | 0 | 0 | 0.2758 | 11.2802 | 0 | 0 | 0 | 0 | 11.2802 | 0 | 33600 | 0 | 719498.9533 | 224.2917 | 0
7759 | 11 | 0 | 0 | 0.39446 | 16.1335 | 0 | 0 | 0 | 0 | 16.1335 | 0 | 33600 | 0 | 719498.9533 | 238.2762 | 0
7760 | 11 | 1 | 0.088967 | 0.37222 | 40.9174 | 200 | 40.9174 | 159.0826 | 200 | 0 | 0 | 33400 | 200 | 719698.9533 | 79.1935 | 0
7761 | 11 | 1 | 0.4166 | 0.36249 | 135.1397 | 200 | 135.1397 | 64.8603 | 200 | 0 | 0 | 33200 | 200 | 719898.9533 | 14.3333 | 0
7762 | 11 | 0 | 0.78497 | 0.31209 | 239.463 | 0 | 0 | 0 | 0 | 180 | 59.463 | 33200 | 59.463 | 719958.4162 | 170.3573 | 0
7763 | 11 | 0 | 1 | 0.25101 | 299.0665 | 0 | 0 | 0 | 0 | 180 | 119.0665 | 33200 | 119.0665 | 720077.4827 | 326.3813 | 0
7764 | 11 | 0 | 1 | 0.28213 | 300.3392 | 0 | 0 | 0 | 0 | 180 | 120.3392 | 33200 | 120.3392 | 720197.8219 | 482.4053 | 0
7765 | 11 | 0 | 1 | 0.22699 | 298.0838 | 0 | 0 | 0 | 0 | 32.7697 | 200 | 33200 | 200 | 720397.8219 | 510.81 | 65.3141
7766 | 11 | 0 | 1 | 0.20599 | 297.2248 | 0 | 0 | 0 | 0 | 0 | 200 | 33200 | 200 | 720597.8219 | 510.81 | 97.2248
7767 | 11 | 0 | 1 | 0.19542 | 296.7928 | 0 | 0 | 0 | 0 | 0 | 200 | 33200 | 200 | 720797.8219 | 510.81 | 96.7928
7768 | 11 | 0 | 0.78497 | 0.15083 | 232.8673 | 0 | 0 | 0 | 0 | 0 | 200 | 33200 | 200 | 720997.8219 | 510.81 | 32.8673
7769 | 11 | 0 | 0.4166 | 0.15337 | 126.5865 | 0 | 0 | 0 | 0 | 0 | 126.5865 | 33200 | 126.5865 | 721124.4084 | 510.81 | 0
7770 | 11 | 0 | 0.088967 | 0.15311 | 31.9558 | 0 | 0 | 0 | 0 | 0 | 31.9558 | 33200 | 31.9558 | 721156.3642 | 510.81 | 0
7771 | 11 | 0 | 0 | 0.18105 | 7.4051 | 0 | 0 | 0 | 0 | 0 | 7.4051 | 33200 | 7.4051 | 721163.7693 | 510.81 | 0
7772 | 11 | 1 | 0 | 0.13675 | 5.5931 | 200 | 5.5931 | 180 | 185.5931 | 0 | 0 | 33000 | 185.5931 | 721349.3623 | 330.81 | 0
7773 | 11 | 1 | 0 | 0.23513 | 9.6169 | 200 | 9.6169 | 180 | 189.6169 | 0 | 0 | 32800 | 189.6169 | 721538.9792 | 150.81 | 0
7774 | 11 | 0 | 0 | 0.3037 | 12.4215 | 0 | 0 | 0 | 0 | 12.4215 | 0 | 32800 | 0 | 721538.9792 | 161.577 | 0
7775 | 11 | 0 | 0 | 0.36123 | 14.7742 | 0 | 0 | 0 | 0 | 14.7742 | 0 | 32800 | 0 | 721538.9792 | 174.3832 | 0
7776 | 11 | 0 | 0 | 0.36354 | 14.8689 | 0 | 0 | 0 | 0 | 14.8689 | 0 | 32800 | 0 | 721538.9792 | 187.2716 | 0
7777 | 11 | 0 | 0 | 0.44316 | 18.1253 | 0 | 0 | 0 | 0 | 18.1253 | 0 | 32800 | 0 | 721538.9792 | 202.9826 | 0
7778 | 11 | 0 | 0 | 0.32803 | 13.4163 | 0 | 0 | 0 | 0 | 13.4163 | 0 | 32800 | 0 | 721538.9792 | 214.6119 | 0
7779 | 11 | 0 | 0 | 0.3219 | 13.1659 | 0 | 0 | 0 | 0 | 13.1659 | 0 | 32800 | 0 | 721538.9792 | 226.0241 | 0
7780 | 11 | 0 | 0 | 0.38079 | 15.5743 | 0 | 0 | 0 | 0 | 15.5743 | 0 | 32800 | 0 | 721538.9792 | 239.5239 | 0
7781 | 11 | 0 | 0 | 0.56699 | 23.19 | 0 | 0 | 0 | 0 | 23.19 | 0 | 32800 | 0 | 721538.9792 | 259.625 | 0
7782 | 11 | 0 | 0 | 0.51404 | 21.0244 | 0 | 0 | 0 | 0 | 21.0244 | 0 | 32800 | 0 | 721538.9792 | 277.8489 | 0
7783 | 11 | 0 | 0 | 0.59437 | 24.3099 | 0 | 0 | 0 | 0 | 24.3099 | 0 | 32800 | 0 | 721538.9792 | 298.9207 | 0
7784 | 11 | 1 | 0.09047 | 0.39636 | 42.3387 | 200 | 42.3387 | 157.6613 | 200 | 0 | 0 | 32600 | 200 | 721738.9792 | 141.2594 | 0
7785 | 11 | 1 | 0.42363 | 0.40714 | 138.9979 | 200 | 138.9979 | 61.0021 | 200 | 0 | 0 | 32400 | 200 | 721938.9792 | 80.2573 | 0
7786 | 11 | 0 | 0.79823 | 0.39794 | 246.8036 | 0 | 0 | 0 | 0 | 180 | 66.8036 | 32400 | 66.8036 | 722005.7829 | 236.2813 | 0
7787 | 11 | 0 | 1 | 0.30191 | 301.1482 | 0 | 0 | 0 | 0 | 180 | 121.1482 | 32400 | 121.1482 | 722126.9311 | 392.3053 | 0
7788 | 11 | 0 | 1 | 0.30238 | 301.1673 | 0 | 0 | 0 | 0 | 136.7152 | 164.4522 | 32400 | 164.4522 | 722291.3833 | 510.81 | 0
7789 | 11 | 0 | 1 | 0.35509 | 303.3231 | 0 | 0 | 0 | 0 | 0 | 200 | 32400 | 200 | 722491.3833 | 510.81 | 103.3231
7790 | 11 | 0 | 1 | 0.25771 | 299.3401 | 0 | 0 | 0 | 0 | 0 | 200 | 32400 | 200 | 722691.3833 | 510.81 | 99.3401
7791 | 11 | 0 | 1 | 0.2604 | 299.4502 | 0 | 0 | 0 | 0 | 0 | 200 | 32400 | 200 | 722891.3833 | 510.81 | 99.4502
7792 | 11 | 0 | 0.79823 | 0.379 | 246.0286 | 0 | 0 | 0 | 0 | 0 | 200 | 32400 | 200 | 723091.3833 | 510.81 | 46.0286
7793 | 11 | 0 | 0.42363 | 0.44437 | 140.5205 | 0 | 0 | 0 | 0 | 0 | 140.5205 | 32400 | 140.5205 | 723231.9038 | 510.81 | 0
7794 | 11 | 0 | 0.09047 | 0.34953 | 40.4236 | 0 | 0 | 0 | 0 | 0 | 40.4236 | 32400 | 40.4236 | 723272.3273 | 510.81 | 0
7795 | 11 | 0 | 0 | 0.37745 | 15.4377 | 0 | 0 | 0 | 0 | 0 | 15.4377 | 32400 | 15.4377 | 723287.7651 | 510.81 | 0
7796 | 11 | 1 | 0 | 0.35125 | 14.3663 | 200 | 14.3663 | 180 | 194.3663 | 0 | 0 | 32200 | 194.3663 | 723482.1314 | 330.81 | 0
7797 | 11 | 1 | 0 | 0.30595 | 12.5136 | 200 | 12.5136 | 180 | 192.5136 | 0 | 0 | 32000 | 192.5136 | 723674.6449 | 150.81 | 0
7798 | 11 | 0 | 0 | 0.20952 | 8.5694 | 0 | 0 | 0 | 0 | 8.5694 | 0 | 32000 | 0 | 723674.6449 | 158.238 | 0
7799 | 11 | 0 | 0 | 0.24905 | 10.1863 | 0 | 0 | 0 | 0 | 10.1863 | 0 | 32000 | 0 | 723674.6449 | 167.0675 | 0
7800 | 11 | 0 | 0 | 0.22883 | 9.359 | 0 | 0 | 0 | 0 | 9.359 | 0 | 32000 | 0 | 723674.6449 | 175.1799 | 0
7801 | 11 | 0 | 0 | 0.18418 | 7.533 | 0 | 0 | 0 | 0 | 7.533 | 0 | 32000 | 0 | 723674.6449 | 181.7095 | 0
7802 | 11 | 0 | 0 | 0.14905 | 6.096 | 0 | 0 | 0 | 0 | 6.096 | 0 | 32000 | 0 | 723674.6449 | 186.9936 | 0
7803 | 11 | 0 | 0 | 0.11094 | 4.5374 | 0 | 0 | 0 | 0 | 4.5374 | 0 | 32000 | 0 | 723674.6449 | 190.9266 | 0
7804 | 11 | 0 | 0 | 0.11535 | 4.718 | 0 | 0 | 0 | 0 | 4.718 | 0 | 32000 | 0 | 723674.6449 | 195.0162 | 0
7805 | 11 | 0 | 0 | 0.13503 | 5.5226 | 0 | 0 | 0 | 0 | 5.5226 | 0 | 32000 | 0 | 723674.6449 | 199.8032 | 0
7806 | 11 | 0 | 0 | 0.13139 | 5.3738 | 0 | 0 | 0 | 0 | 5.3738 | 0 | 32000 | 0 | 723674.6449 | 204.4611 | 0
7807 | 11 | 0 | 0 | 0.13291 | 5.436 | 0 | 0 | 0 | 0 | 5.436 | 0 | 32000 | 0 | 723674.6449 | 209.1731 | 0
7808 | 11 | 1 | 0.078023 | 0.098993 | 26.5819 | 200 | 26.5819 | 173.4181 | 200 | 0 | 0 | 31800 | 200 | 723874.6449 | 35.7549 | 0
7809 | 11 | 1 | 0.36535 | 0.074882 | 108.5755 | 200 | 108.5755 | 35.7549 | 144.3304 | 0 | 0 | 31600 | 144.3304 | 724018.9753 | 0 | 0
7810 | 11 | 0 | 0.6884 | 0.10224 | 202.9919 | 0 | 0 | 0 | 0 | 180 | 22.9919 | 31600 | 22.9919 | 724041.9673 | 156.024 | 0
7811 | 11 | 0 | 0.9729 | 0.10227 | 285.1557 | 0 | 0 | 0 | 0 | 180 | 105.1557 | 31600 | 105.1557 | 724147.123 | 312.048 | 0
7812 | 11 | 0 | 1 | 0.12008 | 293.7111 | 0 | 0 | 0 | 0 | 180 | 113.7111 | 31600 | 113.7111 | 724260.8341 | 468.072 | 0
7813 | 11 | 0 | 1 | 0.13173 | 294.1876 | 0 | 0 | 0 | 0 | 49.3055 | 200 | 31600 | 200 | 724460.8341 | 510.81 | 44.8821
7814 | 11 | 0 | 1 | 0.12467 | 293.899 | 0 | 0 | 0 | 0 | 0 | 200 | 31600 | 200 | 724660.8341 | 510.81 | 93.899
7815 | 11 | 0 | 0.9729 | 0.11212 | 285.5585 | 0 | 0 | 0 | 0 | 0 | 200 | 31600 | 200 | 724860.8341 | 510.81 | 85.5585
7816 | 11 | 0 | 0.6884 | 0.14009 | 204.5401 | 0 | 0 | 0 | 0 | 0 | 200 | 31600 | 200 | 725060.8341 | 510.81 | 4.5401
7817 | 11 | 0 | 0.36535 | 0.18175 | 112.9465 | 0 | 0 | 0 | 0 | 0 | 112.9465 | 31600 | 112.9465 | 725173.7806 | 510.81 | 0
7818 | 11 | 0 | 0.078023 | 0.17366 | 29.6359 | 0 | 0 | 0 | 0 | 0 | 29.6359 | 31600 | 29.6359 | 725203.4165 | 510.81 | 0
7819 | 11 | 0 | 0 | 0.1615 | 6.6053 | 0 | 0 | 0 | 0 | 0 | 6.6053 | 31600 | 6.6053 | 725210.0217 | 510.81 | 0
7820 | 11 | 1 | 0 | 0.14739 | 6.0281 | 200 | 6.0281 | 180 | 186.0281 | 0 | 0 | 31400 | 186.0281 | 725396.0499 | 330.81 | 0
7821 | 11 | 1 | 0 | 0.13168 | 5.3856 | 200 | 5.3856 | 180 | 185.3856 | 0 | 0 | 31200 | 185.3856 | 725581.4354 | 150.81 | 0
7822 | 11 | 0 | 0 | 0.17505 | 7.1597 | 0 | 0 | 0 | 0 | 7.1597 | 0 | 31200 | 0 | 725581.4354 | 157.016 | 0
7823 | 11 | 0 | 0 | 0.16454 | 6.7296 | 0 | 0 | 0 | 0 | 6.7296 | 0 | 31200 | 0 | 725581.4354 | 162.8492 | 0
7824 | 11 | 0 | 0 | 0.17742 | 7.2566 | 0 | 0 | 0 | 0 | 7.2566 | 0 | 31200 | 0 | 725581.4354 | 169.1392 | 0
7825 | 11 | 0 | 0 | 0.15149 | 6.1959 | 0 | 0 | 0 | 0 | 6.1959 | 0 | 31200 | 0 | 725581.4354 | 174.5098 | 0
7826 | 11 | 0 | 0 | 0.25133 | 10.2796 | 0 | 0 | 0 | 0 | 10.2796 | 0 | 31200 | 0 | 725581.4354 | 183.4201 | 0
7827 | 11 | 0 | 0 | 0.23845 | 9.7525 | 0 | 0 | 0 | 0 | 9.7525 | 0 | 31200 | 0 | 725581.4354 | 191.8736 | 0
7828 | 11 | 0 | 0 | 0.19284 | 7.8872 | 0 | 0 | 0 | 0 | 7.8872 | 0 | 31200 | 0 | 725581.4354 | 198.7102 | 0
7829 | 11 | 0 | 0 | 0.1785 | 7.3005 | 0 | 0 | 0 | 0 | 7.3005 | 0 | 31200 | 0 | 725581.4354 | 205.0383 | 0
7830 | 11 | 0 | 0 | 0.18835 | 7.7037 | 0 | 0 | 0 | 0 | 7.7037 | 0 | 31200 | 0 | 725581.4354 | 211.7159 | 0
7831 | 11 | 0 | 0 | 0.14006 | 5.7282 | 0 | 0 | 0 | 0 | 5.7282 | 0 | 31200 | 0 | 725581.4354 | 216.6811 | 0
7832 | 11 | 1 | 0.08939 | 0.11192 | 30.3935 | 200 | 30.3935 | 169.6065 | 200 | 0 | 0 | 31000 | 200 | 725781.4354 | 47.0746 | 0
7833 | 11 | 1 | 0.41858 | 0.16655 | 127.6971 | 200 | 127.6971 | 47.0746 | 174.7717 | 0 | 0 | 30800 | 174.7717 | 725956.2071 | 0 | 0
7834 | 11 | 0 | 0.7887 | 0.17493 | 234.9299 | 0 | 0 | 0 | 0 | 180 | 54.9299 | 30800 | 54.9299 | 726011.137 | 156.024 | 0
7835 | 11 | 0 | 1 | 0.31505 | 301.6856 | 0 | 0 | 0 | 0 | 180 | 121.6856 | 30800 | 121.6856 | 726132.8226 | 312.048 | 0
7836 | 11 | 0 | 1 | 0.29203 | 300.7439 | 0 | 0 | 0 | 0 | 180 | 120.7439 | 30800 | 120.7439 | 726253.5666 | 468.072 | 0
7837 | 11 | 0 | 1 | 0.23746 | 298.5122 | 0 | 0 | 0 | 0 | 49.3055 | 200 | 30800 | 200 | 726453.5666 | 510.81 | 49.2067
7838 | 11 | 0 | 1 | 0.39697 | 305.0361 | 0 | 0 | 0 | 0 | 0 | 200 | 30800 | 200 | 726653.5666 | 510.81 | 105.0361
7839 | 11 | 0 | 1 | 0.19219 | 296.6604 | 0 | 0 | 0 | 0 | 0 | 200 | 30800 | 200 | 726853.5666 | 510.81 | 96.6604
7840 | 11 | 0 | 0.7887 | 0.1895 | 235.5256 | 0 | 0 | 0 | 0 | 0 | 200 | 30800 | 200 | 727053.5666 | 510.81 | 35.5256
7841 | 11 | 0 | 0.41858 | 0.12737 | 126.0946 | 0 | 0 | 0 | 0 | 0 | 126.0946 | 30800 | 126.0946 | 727179.6612 | 510.81 | 0
7842 | 11 | 0 | 0.08939 | 0.083235 | 29.2201 | 0 | 0 | 0 | 0 | 0 | 29.2201 | 30800 | 29.2201 | 727208.8813 | 510.81 | 0
7843 | 11 | 0 | 0 | 0.14922 | 6.1033 | 0 | 0 | 0 | 0 | 0 | 6.1033 | 30800 | 6.1033 | 727214.9846 | 510.81 | 0
7844 | 11 | 1 | 0 | 0.16301 | 6.6671 | 200 | 6.6671 | 180 | 186.6671 | 0 | 0 | 30600 | 186.6671 | 727401.6516 | 330.81 | 0
7845 | 11 | 1 | 0 | 0.21517 | 8.8003 | 200 | 8.8003 | 180 | 188.8003 | 0 | 0 | 30400 | 188.8003 | 727590.452 | 150.81 | 0
7846 | 11 | 0 | 0 | 0.29576 | 12.0967 | 0 | 0 | 0 | 0 | 12.0967 | 0 | 30400 | 0 | 727590.452 | 161.2954 | 0
7847 | 11 | 0 | 0 | 0.25492 | 10.4262 | 0 | 0 | 0 | 0 | 10.4262 | 0 | 30400 | 0 | 727590.452 | 170.3328 | 0
7848 | 11 | 0 | 0 | 0.28724 | 11.7481 | 0 | 0 | 0 | 0 | 11.7481 | 0 | 30400 | 0 | 727590.452 | 180.5161 | 0
7849 | 11 | 0 | 0 | 0.21699 | 8.8747 | 0 | 0 | 0 | 0 | 8.8747 | 0 | 30400 | 0 | 727590.452 | 188.2087 | 0
7850 | 11 | 0 | 0 | 0.17023 | 6.9625 | 0 | 0 | 0 | 0 | 6.9625 | 0 | 30400 | 0 | 727590.452 | 194.2438 | 0
7851 | 11 | 0 | 0 | 0.20445 | 8.3619 | 0 | 0 | 0 | 0 | 8.3619 | 0 | 30400 | 0 | 727590.452 | 201.4919 | 0
7852 | 11 | 0 | 0 | 0.21505 | 8.7955 | 0 | 0 | 0 | 0 | 8.7955 | 0 | 30400 | 0 | 727590.452 | 209.1158 | 0
7853 | 11 | 0 | 0 | 0.20909 | 8.5519 | 0 | 0 | 0 | 0 | 8.5519 | 0 | 30400 | 0 | 727590.452 | 216.5286 | 0
7854 | 11 | 0 | 0 | 0.22364 | 9.147 | 0 | 0 | 0 | 0 | 9.147 | 0 | 30400 | 0 | 727590.452 | 224.4572 | 0
7855 | 11 | 0 | 0 | 0.25392 | 10.3855 | 0 | 0 | 0 | 0 | 10.3855 | 0 | 30400 | 0 | 727590.452 | 233.4594 | 0
7856 | 11 | 1 | 0.080669 | 0.2226 | 32.4014 | 200 | 32.4014 | 167.5986 | 200 | 0 | 0 | 30200 | 200 | 727790.452 | 65.8607 | 0
7857 | 11 | 1 | 0.37774 | 0.22589 | 118.3304 | 200 | 118.3304 | 65.8607 | 184.1911 | 0 | 0 | 30000 | 184.1911 | 727974.6431 | 0 | 0
7858 | 11 | 0 | 0.71175 | 0.23365 | 215.109 | 0 | 0 | 0 | 0 | 180 | 35.109 | 30000 | 35.109 | 728009.7521 | 156.024 | 0
7859 | 11 | 0 | 1 | 0.19281 | 296.686 | 0 | 0 | 0 | 0 | 180 | 116.686 | 30000 | 116.686 | 728126.438 | 312.048 | 0
7860 | 11 | 0 | 1 | 0.13826 | 294.4547 | 0 | 0 | 0 | 0 | 180 | 114.4547 | 30000 | 114.4547 | 728240.8927 | 468.072 | 0
7861 | 11 | 0 | 1 | 0.11726 | 293.596 | 0 | 0 | 0 | 0 | 49.3055 | 200 | 30000 | 200 | 728440.8927 | 510.81 | 44.2905
7862 | 11 | 0 | 1 | 0.12686 | 293.9885 | 0 | 0 | 0 | 0 | 0 | 200 | 30000 | 200 | 728640.8927 | 510.81 | 93.9885
7863 | 11 | 0 | 1 | 0.11796 | 293.6246 | 0 | 0 | 0 | 0 | 0 | 200 | 30000 | 200 | 728840.8927 | 510.81 | 93.6246
7864 | 11 | 0 | 0.71175 | 0.1229 | 210.5793 | 0 | 0 | 0 | 0 | 0 | 200 | 30000 | 200 | 729040.8927 | 510.81 | 10.5793
7865 | 11 | 0 | 0.37774 | 0.086512 | 112.6297 | 0 | 0 | 0 | 0 | 0 | 112.6297 | 30000 | 112.6297 | 729153.5224 | 510.81 | 0
7866 | 11 | 0 | 0.080669 | 0.081773 | 26.6417 | 0 | 0 | 0 | 0 | 0 | 26.6417 | 30000 | 26.6417 | 729180.1641 | 510.81 | 0
7867 | 11 | 0 | 0 | 0.11924 | 4.8768 | 0 | 0 | 0 | 0 | 0 | 4.8768 | 30000 | 4.8768 | 729185.041 | 510.81 | 0
7868 | 11 | 1 | 0 | 0.11383 | 4.6555 | 200 | 4.6555 | 180 | 184.6555 | 0 | 0 | 29800 | 184.6555 | 729369.6965 | 330.81 | 0
7869 | 11 | 1 | 0 | 0.13834 | 5.658 | 200 | 5.658 | 180 | 185.658 | 0 | 0 | 29600 | 185.658 | 729555.3545 | 150.81 | 0
7870 | 11 | 0 | 0 | 0.17046 | 6.972 | 0 | 0 | 0 | 0 | 6.972 | 0 | 29600 | 0 | 729555.3545 | 156.8533 | 0
7871 | 11 | 0 | 0 | 0.19869 | 8.1265 | 0 | 0 | 0 | 0 | 8.1265 | 0 | 29600 | 0 | 729555.3545 | 163.8973 | 0
7872 | 11 | 0 | 0 | 0.13842 | 5.6614 | 0 | 0 | 0 | 0 | 5.6614 | 0 | 29600 | 0 | 729555.3545 | 168.8046 | 0
7873 | 11 | 0 | 0 | 0.21205 | 8.673 | 0 | 0 | 0 | 0 | 8.673 | 0 | 29600 | 0 | 729555.3545 | 176.3223 | 0
7874 | 11 | 0 | 0 | 0.25586 | 10.4647 | 0 | 0 | 0 | 0 | 10.4647 | 0 | 29600 | 0 | 729555.3545 | 185.3931 | 0
7875 | 11 | 0 | 0 | 0.28112 | 11.4979 | 0 | 0 | 0 | 0 | 11.4979 | 0 | 29600 | 0 | 729555.3545 | 195.3595 | 0
7876 | 11 | 0 | 0 | 0.3829 | 15.6606 | 0 | 0 | 0 | 0 | 15.6606 | 0 | 29600 | 0 | 729555.3545 | 208.9341 | 0
7877 | 11 | 0 | 0 | 0.3296 | 13.4805 | 0 | 0 | 0 | 0 | 13.4805 | 0 | 29600 | 0 | 729555.3545 | 220.6191 | 0
7878 | 11 | 0 | 0 | 0.27468 | 11.2344 | 0 | 0 | 0 | 0 | 11.2344 | 0 | 29600 | 0 | 729555.3545 | 230.357 | 0
7879 | 11 | 0 | 0 | 0.28227 | 11.5448 | 0 | 0 | 0 | 0 | 11.5448 | 0 | 29600 | 0 | 729555.3545 | 240.364 | 0
7880 | 11 | 1 | 0.084543 | 0.27848 | 35.8059 | 200 | 35.8059 | 164.1941 | 200 | 0 | 0 | 29400 | 200 | 729755.3545 | 76.1699 | 0
7881 | 11 | 1 | 0.39588 | 0.38659 | 130.1419 | 200 | 130.1419 | 69.8581 | 200 | 0 | 0 | 29200 | 200 | 729955.3545 | 6.3117 | 0
7882 | 11 | 0 | 0.74593 | 0.39913 | 231.7495 | 0 | 0 | 0 | 0 | 180 | 51.7495 | 29200 | 51.7495 | 730007.104 | 162.3357 | 0
7883 | 11 | 0 | 1 | 0.51731 | 309.9578 | 0 | 0 | 0 | 0 | 180 | 129.9578 | 29200 | 129.9578 | 730137.0617 | 318.3597 | 0
7884 | 11 | 0 | 1 | 0.55711 | 311.5858 | 0 | 0 | 0 | 0 | 180 | 131.5858 | 29200 | 131.5858 | 730268.6475 | 474.3837 | 0
7885 | 11 | 0 | 1 | 0.4227 | 306.0884 | 0 | 0 | 0 | 0 | 42.0238 | 200 | 29200 | 200 | 730468.6475 | 510.81 | 64.0646
7886 | 11 | 0 | 1 | 0.43794 | 306.7116 | 0 | 0 | 0 | 0 | 0 | 200 | 29200 | 200 | 730668.6475 | 510.81 | 106.7116
7887 | 11 | 0 | 1 | 0.49119 | 308.8896 | 0 | 0 | 0 | 0 | 0 | 200 | 29200 | 200 | 730868.6475 | 510.81 | 108.8896
7888 | 11 | 0 | 0.74593 | 0.83415 | 249.5414 | 0 | 0 | 0 | 0 | 0 | 200 | 29200 | 200 | 731068.6475 | 510.81 | 49.5414
7889 | 11 | 0 | 0.39588 | 0.73927 | 144.5665 | 0 | 0 | 0 | 0 | 0 | 144.5665 | 29200 | 144.5665 | 731213.2139 | 510.81 | 0
7890 | 11 | 0 | 0.084543 | 0.57343 | 47.8693 | 0 | 0 | 0 | 0 | 0 | 47.8693 | 29200 | 47.8693 | 731261.0833 | 510.81 | 0
7891 | 11 | 0 | 0 | 0.41433 | 16.9459 | 0 | 0 | 0 | 0 | 0 | 16.9459 | 29200 | 16.9459 | 731278.0292 | 510.81 | 0
7892 | 11 | 1 | 0 | 0.61709 | 25.2389 | 200 | 25.2389 | 174.7611 | 200 | 0 | 0 | 29000 | 200 | 731478.0292 | 336.0489 | 0
7893 | 11 | 1 | 0 | 0.69836 | 28.5629 | 200 | 28.5629 | 171.4371 | 200 | 0 | 0 | 28800 | 200 | 731678.0292 | 164.6118 | 0
7894 | 11 | 0 | 0 | 0.81792 | 33.453 | 0 | 0 | 0 | 0 | 33.453 | 0 | 28800 | 0 | 731678.0292 | 193.6089 | 0
7895 | 11 | 0 | 0 | 0.75282 | 30.7902 | 0 | 0 | 0 | 0 | 30.7902 | 0 | 28800 | 0 | 731678.0292 | 220.2978 | 0
7896 | 11 | 0 | 0 | 0.57032 | 23.326 | 0 | 0 | 0 | 0 | 23.326 | 0 | 28800 | 0 | 731678.0292 | 240.5168 | 0
7897 | 11 | 0 | 0 | 0.3921 | 16.0368 | 0 | 0 | 0 | 0 | 16.0368 | 0 | 28800 | 0 | 731678.0292 | 254.4175 | 0
7898 | 11 | 0 | 0 | 0.33183 | 13.5718 | 0 | 0 | 0 | 0 | 13.5718 | 0 | 28800 | 0 | 731678.0292 | 266.1815 | 0
7899 | 11 | 0 | 0 | 0.42467 | 17.369 | 0 | 0 | 0 | 0 | 17.369 | 0 | 28800 | 0 | 731678.0292 | 281.237 | 0
7900 | 11 | 0 | 0 | 0.40496 | 16.5629 | 0 | 0 | 0 | 0 | 16.5629 | 0 | 28800 | 0 | 731678.0292 | 295.5938 | 0
7901 | 11 | 0 | 0 | 0.39743 | 16.2551 | 0 | 0 | 0 | 0 | 16.2551 | 0 | 28800 | 0 | 731678.0292 | 309.6837 | 0
7902 | 11 | 0 | 0 | 0.60391 | 24.6999 | 0 | 0 | 0 | 0 | 24.6999 | 0 | 28800 | 0 | 731678.0292 | 331.0935 | 0
7903 | 11 | 0 | 0 | 0.399 | 16.3193 | 0 | 0 | 0 | 0 | 16.3193 | 0 | 28800 | 0 | 731678.0292 | 345.2391 | 0
7904 | 11 | 1 | 0.081403 | 0.39279 | 39.5742 | 200 | 39.5742 | 160.4258 | 200 | 0 | 0 | 28600 | 200 | 731878.0292 | 184.8133 | 0
7905 | 11 | 1 | 0.38118 | 0.72544 | 139.7542 | 200 | 139.7542 | 60.2458 | 200 | 0 | 0 | 28400 | 200 | 732078.0292 | 124.5675 | 0
7906 | 11 | 0 | 0.71822 | 0.89341 | 243.9634 | 0 | 0 | 0 | 0 | 180 | 63.9634 | 28400 | 63.9634 | 732141.9926 | 280.5915 | 0
7907 | 11 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 180 | 149.7 | 28400 | 149.7 | 732291.6926 | 436.6155 | 0
7908 | 11 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 85.5959 | 200 | 28400 | 200 | 732491.6926 | 510.81 | 44.1041
7909 | 11 | 0 | 1 | 0.92481 | 326.6246 | 0 | 0 | 0 | 0 | 0 | 200 | 28400 | 200 | 732691.6926 | 510.81 | 126.6246
7910 | 11 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 0 | 200 | 28400 | 200 | 732891.6926 | 510.81 | 129.7
7911 | 11 | 0 | 1 | 0.92998 | 326.836 | 0 | 0 | 0 | 0 | 0 | 200 | 28400 | 200 | 733091.6926 | 510.81 | 126.836
7912 | 11 | 0 | 0.71822 | 0.75656 | 238.3664 | 0 | 0 | 0 | 0 | 0 | 200 | 28400 | 200 | 733291.6926 | 510.81 | 38.3664
7913 | 11 | 0 | 0.38118 | 0.95104 | 148.9815 | 0 | 0 | 0 | 0 | 0 | 148.9815 | 28400 | 148.9815 | 733440.6741 | 510.81 | 0
7914 | 11 | 0 | 0.081403 | 0.8346 | 57.6444 | 0 | 0 | 0 | 0 | 0 | 57.6444 | 28400 | 57.6444 | 733498.3185 | 510.81 | 0
7915 | 11 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 0 | 40.9 | 28400 | 40.9 | 733539.2185 | 510.81 | 0
7916 | 11 | 1 | 0 | 0.82764 | 33.8505 | 200 | 33.8505 | 166.1495 | 200 | 0 | 0 | 28200 | 200 | 733739.2185 | 344.6605 | 0
7917 | 11 | 1 | 0 | 0.71353 | 29.1832 | 200 | 29.1832 | 170.8168 | 200 | 0 | 0 | 28000 | 200 | 733939.2185 | 173.8437 | 0
7918 | 11 | 0 | 0 | 0.73903 | 30.2265 | 0 | 0 | 0 | 0 | 30.2265 | 0 | 28000 | 0 | 733939.2185 | 200.044 | 0
7919 | 11 | 0 | 0 | 0.88116 | 36.0393 | 0 | 0 | 0 | 0 | 36.0393 | 0 | 28000 | 0 | 733939.2185 | 231.2829 | 0
7920 | 11 | 0 | 0 | 0.77252 | 31.5961 | 0 | 0 | 0 | 0 | 31.5961 | 0 | 28000 | 0 | 733939.2185 | 258.6704 | 0
7921 | 11 | 0 | 0 | 0.6146 | 25.1373 | 0 | 0 | 0 | 0 | 25.1373 | 0 | 28000 | 0 | 733939.2185 | 280.4595 | 0
7922 | 11 | 0 | 0 | 0.33731 | 13.7959 | 0 | 0 | 0 | 0 | 13.7959 | 0 | 28000 | 0 | 733939.2185 | 292.4178 | 0
7923 | 11 | 0 | 0 | 0.34222 | 13.9967 | 0 | 0 | 0 | 0 | 13.9967 | 0 | 28000 | 0 | 733939.2185 | 304.5502 | 0
7924 | 11 | 0 | 0 | 0.25976 | 10.624 | 0 | 0 | 0 | 0 | 10.624 | 0 | 28000 | 0 | 733939.2185 | 313.759 | 0
7925 | 11 | 0 | 0 | 0.21133 | 8.6434 | 0 | 0 | 0 | 0 | 8.6434 | 0 | 28000 | 0 | 733939.2185 | 321.2512 | 0
7926 | 11 | 0 | 0 | 0.19658 | 8.0402 | 0 | 0 | 0 | 0 | 8.0402 | 0 | 28000 | 0 | 733939.2185 | 328.2204 | 0
7927 | 11 | 0 | 0 | 0.17646 | 7.2172 | 0 | 0 | 0 | 0 | 7.2172 | 0 | 28000 | 0 | 733939.2185 | 334.4763 | 0
7928 | 11 | 1 | 0.075315 | 0.22324 | 30.8814 | 200 | 30.8814 | 169.1186 | 200 | 0 | 0 | 27800 | 200 | 734139.2185 | 165.3577 | 0
7929 | 11 | 1 | 0.35267 | 0.30252 | 114.2246 | 200 | 114.2246 | 85.7754 | 200 | 0 | 0 | 27600 | 200 | 734339.2185 | 79.5823 | 0
7930 | 11 | 0 | 0.66451 | 0.27127 | 203.007 | 0 | 0 | 0 | 0 | 180 | 23.007 | 27600 | 23.007 | 734362.2256 | 235.6063 | 0
7931 | 11 | 0 | 0.93914 | 0.3403 | 285.1417 | 0 | 0 | 0 | 0 | 180 | 105.1417 | 27600 | 105.1417 | 734467.3673 | 391.6303 | 0
7932 | 11 | 0 | 1 | 0.34029 | 302.7179 | 0 | 0 | 0 | 0 | 137.4939 | 165.2241 | 27600 | 165.2241 | 734632.5913 | 510.81 | 0
7933 | 11 | 0 | 1 | 0.38181 | 304.4161 | 0 | 0 | 0 | 0 | 0 | 200 | 27600 | 200 | 734832.5913 | 510.81 | 104.4161
7934 | 11 | 0 | 1 | 0.31687 | 301.76 | 0 | 0 | 0 | 0 | 0 | 200 | 27600 | 200 | 735032.5913 | 510.81 | 101.76
7935 | 11 | 0 | 0.93914 | 0.38035 | 286.7801 | 0 | 0 | 0 | 0 | 0 | 200 | 27600 | 200 | 735232.5913 | 510.81 | 86.7801
7936 | 11 | 0 | 0.66451 | 0.52644 | 213.4432 | 0 | 0 | 0 | 0 | 0 | 200 | 27600 | 200 | 735432.5913 | 510.81 | 13.4432
7937 | 11 | 0 | 0.35267 | 0.95042 | 140.7239 | 0 | 0 | 0 | 0 | 0 | 140.7239 | 27600 | 140.7239 | 735573.3153 | 510.81 | 0
7938 | 11 | 0 | 0.075315 | 0.72228 | 51.2923 | 0 | 0 | 0 | 0 | 0 | 51.2923 | 27600 | 51.2923 | 735624.6075 | 510.81 | 0
7939 | 11 | 0 | 0 | 0.68369 | 27.9631 | 0 | 0 | 0 | 0 | 0 | 27.9631 | 27600 | 27.9631 | 735652.5706 | 510.81 | 0
7940 | 11 | 1 | 0 | 0.79851 | 32.659 | 200 | 32.659 | 167.341 | 200 | 0 | 0 | 27400 | 200 | 735852.5706 | 343.469 | 0
7941 | 11 | 1 | 0 | 1 | 40.9 | 200 | 40.9 | 159.1 | 200 | 0 | 0 | 27200 | 200 | 736052.5706 | 184.369 | 0
7942 | 11 | 0 | 0 | 0.93685 | 38.3173 | 0 | 0 | 0 | 0 | 38.3173 | 0 | 27200 | 0 | 736052.5706 | 217.5825 | 0
7943 | 11 | 0 | 0 | 0.61064 | 24.9753 | 0 | 0 | 0 | 0 | 24.9753 | 0 | 27200 | 0 | 736052.5706 | 239.231 | 0
7944 | 11 | 0 | 0 | 0.53733 | 21.9767 | 0 | 0 | 0 | 0 | 21.9767 | 0 | 27200 | 0 | 736052.5706 | 258.2804 | 0
7945 | 11 | 0 | 0 | 0.51417 | 21.0297 | 0 | 0 | 0 | 0 | 21.0297 | 0 | 27200 | 0 | 736052.5706 | 276.509 | 0
7946 | 11 | 0 | 0 | 0.44608 | 18.2445 | 0 | 0 | 0 | 0 | 18.2445 | 0 | 27200 | 0 | 736052.5706 | 292.3233 | 0
7947 | 11 | 0 | 0 | 0.53127 | 21.7289 | 0 | 0 | 0 | 0 | 21.7289 | 0 | 27200 | 0 | 736052.5706 | 311.158 | 0
7948 | 11 | 0 | 0 | 0.47438 | 19.4021 | 0 | 0 | 0 | 0 | 19.4021 | 0 | 27200 | 0 | 736052.5706 | 327.9758 | 0
7949 | 11 | 0 | 0 | 0.52803 | 21.5963 | 0 | 0 | 0 | 0 | 21.5963 | 0 | 27200 | 0 | 736052.5706 | 346.6954 | 0
7950 | 11 | 0 | 0 | 0.31246 | 12.7796 | 0 | 0 | 0 | 0 | 12.7796 | 0 | 27200 | 0 | 736052.5706 | 357.7728 | 0
7951 | 11 | 0 | 0 | 0.30428 | 12.4451 | 0 | 0 | 0 | 0 | 12.4451 | 0 | 27200 | 0 | 736052.5706 | 368.5602 | 0
7952 | 11 | 1 | 0.085646 | 0.39074 | 40.7159 | 200 | 40.7159 | 159.2841 | 200 | 0 | 0 | 27000 | 200 | 736252.5706 | 209.2761 | 0
7953 | 11 | 1 | 0.40104 | 0.44018 | 133.825 | 200 | 133.825 | 66.175 | 200 | 0 | 0 | 26800 | 200 | 736452.5706 | 143.1011 | 0
7954 | 11 | 0 | 0.75566 | 0.50714 | 238.9763 | 0 | 0 | 0 | 0 | 180 | 58.9763 | 26800 | 58.9763 | 736511.5469 | 299.1251 | 0
7955 | 11 | 0 | 1 | 0.42575 | 306.2131 | 0 | 0 | 0 | 0 | 180 | 126.2131 | 26800 | 126.2131 | 736637.76 | 455.1491 | 0
7956 | 11 | 0 | 1 | 0.52484 | 310.2658 | 0 | 0 | 0 | 0 | 64.2142 | 200 | 26800 | 200 | 736837.76 | 510.81 | 46.0515
7957 | 11 | 0 | 1 | 0.62481 | 314.3546 | 0 | 0 | 0 | 0 | 0 | 200 | 26800 | 200 | 737037.76 | 510.81 | 114.3546
7958 | 11 | 0 | 1 | 0.48191 | 308.5101 | 0 | 0 | 0 | 0 | 0 | 200 | 26800 | 200 | 737237.76 | 510.81 | 108.5101
7959 | 11 | 0 | 1 | 0.44788 | 307.1182 | 0 | 0 | 0 | 0 | 0 | 200 | 26800 | 200 | 737437.76 | 510.81 | 107.1182
7960 | 11 | 0 | 0.75566 | 0.45609 | 236.8885 | 0 | 0 | 0 | 0 | 0 | 200 | 26800 | 200 | 737637.76 | 510.81 | 36.8885
7961 | 11 | 0 | 0.40104 | 0.60528 | 140.5773 | 0 | 0 | 0 | 0 | 0 | 140.5773 | 26800 | 140.5773 | 737778.3374 | 510.81 | 0
7962 | 11 | 0 | 0.085646 | 0.58173 | 48.5274 | 0 | 0 | 0 | 0 | 0 | 48.5274 | 26800 | 48.5274 | 737826.8648 | 510.81 | 0
7963 | 11 | 0 | 0 | 0.40565 | 16.5912 | 0 | 0 | 0 | 0 | 0 | 16.5912 | 26800 | 16.5912 | 737843.456 | 510.81 | 0
7964 | 11 | 1 | 0 | 0.36387 | 14.8823 | 200 | 14.8823 | 180 | 194.8823 | 0 | 0 | 26600 | 194.8823 | 738038.3384 | 330.81 | 0
7965 | 11 | 1 | 0 | 0.38257 | 15.6471 | 200 | 15.6471 | 180 | 195.6471 | 0 | 0 | 26400 | 195.6471 | 738233.9855 | 150.81 | 0
7966 | 11 | 0 | 0 | 0.38117 | 15.5899 | 0 | 0 | 0 | 0 | 15.5899 | 0 | 26400 | 0 | 738233.9855 | 164.3234 | 0
7967 | 11 | 0 | 0 | 0.28838 | 11.7947 | 0 | 0 | 0 | 0 | 11.7947 | 0 | 26400 | 0 | 738233.9855 | 174.547 | 0
7968 | 11 | 0 | 0 | 0.29692 | 12.1442 | 0 | 0 | 0 | 0 | 12.1442 | 0 | 26400 | 0 | 738233.9855 | 185.0736 | 0
7969 | 11 | 0 | 0 | 0.26038 | 10.6494 | 0 | 0 | 0 | 0 | 10.6494 | 0 | 26400 | 0 | 738233.9855 | 194.3045 | 0
7970 | 11 | 0 | 0 | 0.29128 | 11.9133 | 0 | 0 | 0 | 0 | 11.9133 | 0 | 26400 | 0 | 738233.9855 | 204.631 | 0
7971 | 11 | 0 | 0 | 0.32849 | 13.4353 | 0 | 0 | 0 | 0 | 13.4353 | 0 | 26400 | 0 | 738233.9855 | 216.2767 | 0
7972 | 11 | 0 | 0 | 0.3737 | 15.2844 | 0 | 0 | 0 | 0 | 15.2844 | 0 | 26400 | 0 | 738233.9855 | 229.5252 | 0
7973 | 11 | 0 | 0 | 0.35872 | 14.6715 | 0 | 0 | 0 | 0 | 14.6715 | 0 | 26400 | 0 | 738233.9855 | 242.2425 | 0
7974 | 11 | 0 | 0 | 0.38693 | 15.8254 | 0 | 0 | 0 | 0 | 15.8254 | 0 | 26400 | 0 | 738233.9855 | 255.96 | 0
7975 | 11 | 0 | 0 | 0.42045 | 17.1964 | 0 | 0 | 0 | 0 | 17.1964 | 0 | 26400 | 0 | 738233.9855 | 270.8658 | 0
7976 | 11 | 1 | 0.079438 | 0.27552 | 34.2105 | 200 | 34.2105 | 165.7895 | 200 | 0 | 0 | 26200 | 200 | 738433.9855 | 105.0763 | 0
7977 | 11 | 1 | 0.37198 | 0.24418 | 117.4141 | 200 | 117.4141 | 82.5859 | 200 | 0 | 0 | 26000 | 200 | 738633.9855 | 22.4904 | 0
7978 | 11 | 0 | 0.70089 | 0.39796 | 218.6942 | 0 | 0 | 0 | 0 | 180 | 38.6942 | 26000 | 38.6942 | 738672.6796 | 178.5144 | 0
7979 | 11 | 0 | 0.99055 | 0.44786 | 304.3881 | 0 | 0 | 0 | 0 | 180 | 124.3881 | 26000 | 124.3881 | 738797.0678 | 334.5384 | 0
7980 | 11 | 0 | 1 | 0.34321 | 302.8373 | 0 | 0 | 0 | 0 | 180 | 122.8373 | 26000 | 122.8373 | 738919.9051 | 490.5624 | 0
7981 | 11 | 0 | 1 | 0.32747 | 302.1934 | 0 | 0 | 0 | 0 | 23.359 | 200 | 26000 | 200 | 739119.9051 | 510.81 | 78.8344
7982 | 11 | 0 | 1 | 0.40009 | 305.1638 | 0 | 0 | 0 | 0 | 0 | 200 | 26000 | 200 | 739319.9051 | 510.81 | 105.1638
7983 | 11 | 0 | 0.99055 | 0.43609 | 303.9067 | 0 | 0 | 0 | 0 | 0 | 200 | 26000 | 200 | 739519.9051 | 510.81 | 103.9067
7984 | 11 | 0 | 0.70089 | 0.52532 | 223.9033 | 0 | 0 | 0 | 0 | 0 | 200 | 26000 | 200 | 739719.9051 | 510.81 | 23.9033
7985 | 11 | 0 | 0.37198 | 0.64825 | 133.9407 | 0 | 0 | 0 | 0 | 0 | 133.9407 | 26000 | 133.9407 | 739853.8458 | 510.81 | 0
7986 | 11 | 0 | 0.079438 | 0.69368 | 51.3133 | 0 | 0 | 0 | 0 | 0 | 51.3133 | 26000 | 51.3133 | 739905.1591 | 510.81 | 0
7987 | 11 | 0 | 0 | 0.72346 | 29.5894 | 0 | 0 | 0 | 0 | 0 | 29.5894 | 26000 | 29.5894 | 739934.7485 | 510.81 | 0
7988 | 11 | 1 | 0 | 0.94767 | 38.7597 | 200 | 38.7597 | 161.2403 | 200 | 0 | 0 | 25800 | 200 | 740134.7485 | 349.5697 | 0
7989 | 11 | 1 | 0 | 0.91091 | 37.2562 | 200 | 37.2562 | 162.7438 | 200 | 0 | 0 | 25600 | 200 | 740334.7485 | 186.8259 | 0
7990 | 11 | 0 | 0 | 0.71098 | 29.079 | 0 | 0 | 0 | 0 | 29.079 | 0 | 25600 | 0 | 740334.7485 | 212.0316 | 0
7991 | 11 | 0 | 0 | 0.47498 | 19.4266 | 0 | 0 | 0 | 0 | 19.4266 | 0 | 25600 | 0 | 740334.7485 | 228.8705 | 0
7992 | 11 | 0 | 0 | 0.41691 | 17.0516 | 0 | 0 | 0 | 0 | 17.0516 | 0 | 25600 | 0 | 740334.7485 | 243.6508 | 0
7993 | 11 | 0 | 0 | 0.27419 | 11.2143 | 0 | 0 | 0 | 0 | 11.2143 | 0 | 25600 | 0 | 740334.7485 | 253.3714 | 0
7994 | 11 | 0 | 0 | 0.24978 | 10.216 | 0 | 0 | 0 | 0 | 10.216 | 0 | 25600 | 0 | 740334.7485 | 262.2266 | 0
7995 | 11 | 0 | 0 | 0.2071 | 8.4702 | 0 | 0 | 0 | 0 | 8.4702 | 0 | 25600 | 0 | 740334.7485 | 269.5686 | 0
7996 | 11 | 0 | 0 | 0.17124 | 7.0038 | 0 | 0 | 0 | 0 | 7.0038 | 0 | 25600 | 0 | 740334.7485 | 275.6395 | 0
7997 | 11 | 0 | 0 | 0.21799 | 8.9158 | 0 | 0 | 0 | 0 | 8.9158 | 0 | 25600 | 0 | 740334.7485 | 283.3677 | 0
7998 | 11 | 0 | 0 | 0.19793 | 8.0953 | 0 | 0 | 0 | 0 | 8.0953 | 0 | 25600 | 0 | 740334.7485 | 290.3847 | 0
7999 | 11 | 0 | 0 | 0.28499 | 11.6562 | 0 | 0 | 0 | 0 | 11.6562 | 0 | 25600 | 0 | 740334.7485 | 300.4882 | 0
8000 | 11 | 1 | 0.080415 | 0.29842 | 35.4293 | 200 | 35.4293 | 164.5707 | 200 | 0 | 0 | 25400 | 200 | 740534.7485 | 135.9175 | 0
8001 | 11 | 1 | 0.37655 | 0.3781 | 124.2116 | 200 | 124.2116 | 75.7884 | 200 | 0 | 0 | 25200 | 200 | 740734.7485 | 60.1291 | 0
8002 | 11 | 0 | 0.70951 | 0.53673 | 226.8576 | 0 | 0 | 0 | 0 | 180 | 46.8576 | 25200 | 46.8576 | 740781.6061 | 216.1531 | 0
8003 | 11 | 0 | 1 | 0.40714 | 305.4519 | 0 | 0 | 0 | 0 | 180 | 125.4519 | 25200 | 125.4519 | 740907.0579 | 372.1771 | 0
8004 | 11 | 0 | 1 | 0.30179 | 301.1433 | 0 | 0 | 0 | 0 | 159.9365 | 141.2068 | 25200 | 141.2068 | 741048.2647 | 510.81 | 0
8005 | 11 | 0 | 1 | 0.26949 | 299.8223 | 0 | 0 | 0 | 0 | 0 | 200 | 25200 | 200 | 741248.2647 | 510.81 | 99.8223
8006 | 11 | 0 | 1 | 0.20914 | 297.3538 | 0 | 0 | 0 | 0 | 0 | 200 | 25200 | 200 | 741448.2647 | 510.81 | 97.3538
8007 | 11 | 0 | 1 | 0.17266 | 295.8619 | 0 | 0 | 0 | 0 | 0 | 200 | 25200 | 200 | 741648.2647 | 510.81 | 95.8619
8008 | 11 | 0 | 0.70951 | 0.17935 | 212.2408 | 0 | 0 | 0 | 0 | 0 | 200 | 25200 | 200 | 741848.2647 | 510.81 | 12.2408
8009 | 11 | 0 | 0.37655 | 0.093434 | 112.5688 | 0 | 0 | 0 | 0 | 0 | 112.5688 | 25200 | 112.5688 | 741960.8335 | 510.81 | 0
8010 | 11 | 0 | 0.080415 | 0.12114 | 28.1786 | 0 | 0 | 0 | 0 | 0 | 28.1786 | 25200 | 28.1786 | 741989.0122 | 510.81 | 0
8011 | 11 | 0 | 0 | 0.13118 | 5.3652 | 0 | 0 | 0 | 0 | 0 | 5.3652 | 25200 | 5.3652 | 741994.3774 | 510.81 | 0
8012 | 11 | 1 | 0 | 0.10447 | 4.2726 | 200 | 4.2726 | 180 | 184.2726 | 0 | 0 | 25000 | 184.2726 | 742178.65 | 330.81 | 0
8013 | 11 | 1 | 0 | 0.09855 | 4.0307 | 200 | 4.0307 | 180 | 184.0307 | 0 | 0 | 24800 | 184.0307 | 742362.6807 | 150.81 | 0
8014 | 11 | 0 | 0 | 0.092543 | 3.785 | 0 | 0 | 0 | 0 | 3.785 | 0 | 24800 | 0 | 742362.6807 | 154.0908 | 0
8015 | 11 | 0 | 0 | 0.10212 | 4.1766 | 0 | 0 | 0 | 0 | 4.1766 | 0 | 24800 | 0 | 742362.6807 | 157.7111 | 0
8016 | 11 | 0 | 0 | 0.10452 | 4.2748 | 0 | 0 | 0 | 0 | 4.2748 | 0 | 24800 | 0 | 742362.6807 | 161.4165 | 0
8017 | 12 | 0 | 0 | 0.10812 | 4.4223 | 0 | 0 | 0 | 0 | 4.4223 | 0 | 24800 | 0 | 742362.6807 | 165.2498 | 0
8018 | 12 | 0 | 0 | 0.17362 | 7.1011 | 0 | 0 | 0 | 0 | 7.1011 | 0 | 24800 | 0 | 742362.6807 | 171.405 | 0
8019 | 12 | 0 | 0 | 0.27554 | 11.2695 | 0 | 0 | 0 | 0 | 11.2695 | 0 | 24800 | 0 | 742362.6807 | 181.1734 | 0
8020 | 12 | 0 | 0 | 0.36761 | 15.0353 | 0 | 0 | 0 | 0 | 15.0353 | 0 | 24800 | 0 | 742362.6807 | 194.206 | 0
8021 | 12 | 0 | 0 | 0.36156 | 14.7877 | 0 | 0 | 0 | 0 | 14.7877 | 0 | 24800 | 0 | 742362.6807 | 207.024 | 0
8022 | 12 | 0 | 0 | 0.27886 | 11.4055 | 0 | 0 | 0 | 0 | 11.4055 | 0 | 24800 | 0 | 742362.6807 | 216.9103 | 0
8023 | 12 | 0 | 0 | 0.26223 | 10.725 | 0 | 0 | 0 | 0 | 10.725 | 0 | 24800 | 0 | 742362.6807 | 226.2067 | 0
8024 | 12 | 1 | 0.046221 | 0.20281 | 21.6436 | 200 | 21.6436 | 178.3564 | 200 | 0 | 0 | 24600 | 200 | 742562.6807 | 47.8504 | 0
8025 | 12 | 1 | 0.32415 | 0.30634 | 106.1438 | 200 | 106.1438 | 47.8504 | 153.9942 | 0 | 0 | 24400 | 153.9942 | 742716.6749 | 0 | 0
8026 | 12 | 0 | 0.65118 | 0.40914 | 204.7953 | 0 | 0 | 0 | 0 | 180 | 24.7953 | 24400 | 24.7953 | 742741.4702 | 156.024 | 0
8027 | 12 | 0 | 0.94373 | 0.49508 | 292.797 | 0 | 0 | 0 | 0 | 180 | 112.797 | 24400 | 112.797 | 742854.2672 | 312.048 | 0
8028 | 12 | 0 | 1 | 0.42732 | 306.2774 | 0 | 0 | 0 | 0 | 180 | 126.2774 | 24400 | 126.2774 | 742980.5446 | 468.072 | 0
8029 | 12 | 0 | 1 | 0.39658 | 305.02 | 0 | 0 | 0 | 0 | 49.3055 | 200 | 24400 | 200 | 743180.5446 | 510.81 | 55.7145
8030 | 12 | 0 | 1 | 0.80742 | 321.8234 | 0 | 0 | 0 | 0 | 0 | 200 | 24400 | 200 | 743380.5446 | 510.81 | 121.8234
8031 | 12 | 0 | 0.94373 | 0.66383 | 299.6989 | 0 | 0 | 0 | 0 | 0 | 200 | 24400 | 200 | 743580.5446 | 510.81 | 99.6989
8032 | 12 | 0 | 0.65118 | 0.55327 | 210.6902 | 0 | 0 | 0 | 0 | 0 | 200 | 24400 | 200 | 743780.5446 | 510.81 | 10.6902
8033 | 12 | 0 | 0.32415 | 0.36196 | 108.4187 | 0 | 0 | 0 | 0 | 0 | 108.4187 | 24400 | 108.4187 | 743888.9634 | 510.81 | 0
8034 | 12 | 0 | 0.046221 | 0.53119 | 35.0742 | 0 | 0 | 0 | 0 | 0 | 35.0742 | 24400 | 35.0742 | 743924.0376 | 510.81 | 0
8035 | 12 | 0 | 0 | 0.6255 | 25.5831 | 0 | 0 | 0 | 0 | 0 | 25.5831 | 24400 | 25.5831 | 743949.6207 | 510.81 | 0
8036 | 12 | 1 | 0 | 0.47489 | 19.4228 | 200 | 19.4228 | 180 | 199.4228 | 0 | 0 | 24200 | 199.4228 | 744149.0435 | 330.81 | 0
8037 | 12 | 1 | 0 | 0.44359 | 18.1428 | 200 | 18.1428 | 180 | 198.1428 | 0 | 0 | 24000 | 198.1428 | 744347.1863 | 150.81 | 0
8038 | 12 | 0 | 0 | 0.3339 | 13.6564 | 0 | 0 | 0 | 0 | 13.6564 | 0 | 24000 | 0 | 744347.1863 | 162.6474 | 0
8039 | 12 | 0 | 0 | 0.30335 | 12.407 | 0 | 0 | 0 | 0 | 12.407 | 0 | 24000 | 0 | 744347.1863 | 173.4018 | 0
8040 | 12 | 0 | 0 | 0.36627 | 14.9804 | 0 | 0 | 0 | 0 | 14.9804 | 0 | 24000 | 0 | 744347.1863 | 186.3868 | 0
8041 | 12 | 0 | 0 | 0.33234 | 13.5927 | 0 | 0 | 0 | 0 | 13.5927 | 0 | 24000 | 0 | 744347.1863 | 198.1689 | 0
8042 | 12 | 0 | 0 | 0.35507 | 14.5223 | 0 | 0 | 0 | 0 | 14.5223 | 0 | 24000 | 0 | 744347.1863 | 210.7568 | 0
8043 | 12 | 0 | 0 | 0.62008 | 25.3613 | 0 | 0 | 0 | 0 | 25.3613 | 0 | 24000 | 0 | 744347.1863 | 232.74 | 0
8044 | 12 | 0 | 0 | 0.55381 | 22.6507 | 0 | 0 | 0 | 0 | 22.6507 | 0 | 24000 | 0 | 744347.1863 | 252.3736 | 0
8045 | 12 | 0 | 0 | 0.62796 | 25.6834 | 0 | 0 | 0 | 0 | 25.6834 | 0 | 24000 | 0 | 744347.1863 | 274.636 | 0
8046 | 12 | 0 | 0 | 0.55566 | 22.7266 | 0 | 0 | 0 | 0 | 22.7266 | 0 | 24000 | 0 | 744347.1863 | 294.3354 | 0
8047 | 12 | 0 | 0 | 0.49215 | 20.129 | 0 | 0 | 0 | 0 | 20.129 | 0 | 24000 | 0 | 744347.1863 | 311.7833 | 0
8048 | 12 | 1 | 0.04587 | 0.45681 | 31.9309 | 200 | 31.9309 | 168.0691 | 200 | 0 | 0 | 23800 | 200 | 744547.1863 | 143.7142 | 0
8049 | 12 | 1 | 0.32168 | 0.37415 | 108.2049 | 200 | 108.2049 | 91.7951 | 200 | 0 | 0 | 23600 | 200 | 744747.1863 | 51.919 | 0
8050 | 12 | 0 | 0.64623 | 0.28614 | 198.3339 | 0 | 0 | 0 | 0 | 180 | 18.3339 | 23600 | 18.3339 | 744765.5203 | 207.943 | 0
8051 | 12 | 0 | 0.93655 | 0.23887 | 280.2453 | 0 | 0 | 0 | 0 | 180 | 100.2453 | 23600 | 100.2453 | 744865.7655 | 363.967 | 0
8052 | 12 | 0 | 1 | 0.17024 | 295.7629 | 0 | 0 | 0 | 0 | 169.4081 | 126.3547 | 23600 | 126.3547 | 744992.1202 | 510.81 | 0
8053 | 12 | 0 | 1 | 0.14102 | 294.5678 | 0 | 0 | 0 | 0 | 0 | 200 | 23600 | 200 | 745192.1202 | 510.81 | 94.5678
8054 | 12 | 0 | 1 | 0.20226 | 297.0725 | 0 | 0 | 0 | 0 | 0 | 200 | 23600 | 200 | 745392.1202 | 510.81 | 97.0725
8055 | 12 | 0 | 0.93655 | 0.24173 | 280.362 | 0 | 0 | 0 | 0 | 0 | 200 | 23600 | 200 | 745592.1202 | 510.81 | 80.362
8056 | 12 | 0 | 0.64623 | 0.26649 | 197.5304 | 0 | 0 | 0 | 0 | 0 | 197.5304 | 23600 | 197.5304 | 745789.6506 | 510.81 | 0
8057 | 12 | 0 | 0.32168 | 0.20672 | 101.3574 | 0 | 0 | 0 | 0 | 0 | 101.3574 | 23600 | 101.3574 | 745891.008 | 510.81 | 0
8058 | 12 | 0 | 0.04587 | 0.23452 | 22.8393 | 0 | 0 | 0 | 0 | 0 | 22.8393 | 23600 | 22.8393 | 745913.8473 | 510.81 | 0
8059 | 12 | 0 | 0 | 0.19852 | 8.1194 | 0 | 0 | 0 | 0 | 0 | 8.1194 | 23600 | 8.1194 | 745921.9667 | 510.81 | 0
8060 | 12 | 1 | 0 | 0.17336 | 7.0905 | 200 | 7.0905 | 180 | 187.0905 | 0 | 0 | 23400 | 187.0905 | 746109.0572 | 330.81 | 0
8061 | 12 | 1 | 0 | 0.15531 | 6.3521 | 200 | 6.3521 | 180 | 186.3521 | 0 | 0 | 23200 | 186.3521 | 746295.4094 | 150.81 | 0
8062 | 12 | 0 | 0 | 0.19073 | 7.801 | 0 | 0 | 0 | 0 | 7.801 | 0 | 23200 | 0 | 746295.4094 | 157.5719 | 0
8063 | 12 | 0 | 0 | 0.23094 | 9.4454 | 0 | 0 | 0 | 0 | 9.4454 | 0 | 23200 | 0 | 746295.4094 | 165.7592 | 0
8064 | 12 | 0 | 0 | 0.24037 | 9.8312 | 0 | 0 | 0 | 0 | 9.8312 | 0 | 23200 | 0 | 746295.4094 | 174.2809 | 0
8065 | 12 | 0 | 0 | 0.32022 | 13.0969 | 0 | 0 | 0 | 0 | 13.0969 | 0 | 23200 | 0 | 746295.4094 | 185.6333 | 0
8066 | 12 | 0 | 0 | 0.25904 | 10.5949 | 0 | 0 | 0 | 0 | 10.5949 | 0 | 23200 | 0 | 746295.4094 | 194.8169 | 0
8067 | 12 | 0 | 0 | 0.2197 | 8.9856 | 0 | 0 | 0 | 0 | 8.9856 | 0 | 23200 | 0 | 746295.4094 | 202.6056 | 0
8068 | 12 | 0 | 0 | 0.21638 | 8.8499 | 0 | 0 | 0 | 0 | 8.8499 | 0 | 23200 | 0 | 746295.4094 | 210.2767 | 0
8069 | 12 | 0 | 0 | 0.34862 | 14.2587 | 0 | 0 | 0 | 0 | 14.2587 | 0 | 23200 | 0 | 746295.4094 | 222.6362 | 0
8070 | 12 | 0 | 0 | 0.26349 | 10.7766 | 0 | 0 | 0 | 0 | 10.7766 | 0 | 23200 | 0 | 746295.4094 | 231.9773 | 0
8071 | 12 | 0 | 0 | 0.28576 | 11.6877 | 0 | 0 | 0 | 0 | 11.6877 | 0 | 23200 | 0 | 746295.4094 | 242.1082 | 0
8072 | 12 | 1 | 0.052687 | 0.22095 | 24.2529 | 200 | 24.2529 | 175.7471 | 200 | 0 | 0 | 23000 | 200 | 746495.4094 | 66.3611 | 0
8073 | 12 | 1 | 0.3695 | 0.21518 | 115.511 | 200 | 115.511 | 66.3611 | 181.8721 | 0 | 0 | 22800 | 181.8721 | 746677.2815 | 0 | 0
8074 | 12 | 0 | 0.74228 | 0.18388 | 221.8901 | 0 | 0 | 0 | 0 | 180 | 41.8901 | 22800 | 41.8901 | 746719.1716 | 156.024 | 0
8075 | 12 | 0 | 1 | 0.12089 | 293.7444 | 0 | 0 | 0 | 0 | 180 | 113.7444 | 22800 | 113.7444 | 746832.916 | 312.048 | 0
8076 | 12 | 0 | 1 | 0.11865 | 293.6526 | 0 | 0 | 0 | 0 | 180 | 113.6526 | 22800 | 113.6526 | 746946.5686 | 468.072 | 0
8077 | 12 | 0 | 1 | 0.088932 | 292.4373 | 0 | 0 | 0 | 0 | 49.3055 | 200 | 22800 | 200 | 747146.5686 | 510.81 | 43.1318
8078 | 12 | 0 | 1 | 0.060189 | 291.2617 | 0 | 0 | 0 | 0 | 0 | 200 | 22800 | 200 | 747346.5686 | 510.81 | 91.2617
8079 | 12 | 0 | 1 | 0.037121 | 290.3182 | 0 | 0 | 0 | 0 | 0 | 200 | 22800 | 200 | 747546.5686 | 510.81 | 90.3182
8080 | 12 | 0 | 0.74228 | 0.051778 | 216.487 | 0 | 0 | 0 | 0 | 0 | 200 | 22800 | 200 | 747746.5686 | 510.81 | 16.487
8081 | 12 | 0 | 0.3695 | 0.058187 | 109.09 | 0 | 0 | 0 | 0 | 0 | 109.09 | 22800 | 109.09 | 747855.6586 | 510.81 | 0
8082 | 12 | 0 | 0.052687 | 0.042494 | 16.954 | 0 | 0 | 0 | 0 | 0 | 16.954 | 22800 | 16.954 | 747872.6126 | 510.81 | 0
8083 | 12 | 0 | 0 | 0.041382 | 1.6925 | 0 | 0 | 0 | 0 | 0 | 1.6925 | 22800 | 1.6925 | 747874.3051 | 510.81 | 0
8084 | 12 | 1 | 0 | 0.039579 | 1.6188 | 200 | 1.6188 | 180 | 181.6188 | 0 | 0 | 22600 | 181.6188 | 748055.9239 | 330.81 | 0
8085 | 12 | 1 | 0 | 0.040427 | 1.6535 | 200 | 1.6535 | 180 | 181.6535 | 0 | 0 | 22400 | 181.6535 | 748237.5774 | 150.81 | 0
8086 | 12 | 0 | 0 | 0.077214 | 3.1581 | 0 | 0 | 0 | 0 | 3.1581 | 0 | 22400 | 0 | 748237.5774 | 153.5474 | 0
8087 | 12 | 0 | 0 | 0.079211 | 3.2397 | 0 | 0 | 0 | 0 | 3.2397 | 0 | 22400 | 0 | 748237.5774 | 156.3556 | 0
8088 | 12 | 0 | 0 | 0.079011 | 3.2315 | 0 | 0 | 0 | 0 | 3.2315 | 0 | 22400 | 0 | 748237.5774 | 159.1567 | 0
8089 | 12 | 0 | 0 | 0.055462 | 2.2684 | 0 | 0 | 0 | 0 | 2.2684 | 0 | 22400 | 0 | 748237.5774 | 161.123 | 0
8090 | 12 | 0 | 0 | 0.056795 | 2.3229 | 0 | 0 | 0 | 0 | 2.3229 | 0 | 22400 | 0 | 748237.5774 | 163.1365 | 0
8091 | 12 | 0 | 0 | 0.13936 | 5.6999 | 0 | 0 | 0 | 0 | 5.6999 | 0 | 22400 | 0 | 748237.5774 | 168.0772 | 0
8092 | 12 | 0 | 0 | 0.17901 | 7.3215 | 0 | 0 | 0 | 0 | 7.3215 | 0 | 22400 | 0 | 748237.5774 | 174.4234 | 0
8093 | 12 | 0 | 0 | 0.22101 | 9.0393 | 0 | 0 | 0 | 0 | 9.0393 | 0 | 22400 | 0 | 748237.5774 | 182.2587 | 0
8094 | 12 | 0 | 0 | 0.19087 | 7.8067 | 0 | 0 | 0 | 0 | 7.8067 | 0 | 22400 | 0 | 748237.5774 | 189.0256 | 0
8095 | 12 | 0 | 0 | 0.19895 | 8.1369 | 0 | 0 | 0 | 0 | 8.1369 | 0 | 22400 | 0 | 748237.5774 | 196.0786 | 0
8096 | 12 | 1 | 0.043916 | 0.14721 | 18.7037 | 200 | 18.7037 | 180 | 198.7037 | 0 | 0 | 22200 | 198.7037 | 748436.2811 | 16.0786 | 0
8097 | 12 | 1 | 0.30798 | 0.097999 | 92.9534 | 200 | 92.9534 | 16.0786 | 109.032 | 0 | 0 | 22000 | 109.032 | 748545.3131 | 0 | 0
8098 | 12 | 0 | 0.6187 | 0.14236 | 184.504 | 0 | 0 | 0 | 0 | 180 | 4.504 | 22000 | 4.504 | 748549.817 | 156.024 | 0
8099 | 12 | 0 | 0.89666 | 0.159 | 265.4576 | 0 | 0 | 0 | 0 | 180 | 85.4576 | 22000 | 85.4576 | 748635.2746 | 312.048 | 0
8100 | 12 | 0 | 1 | 0.18891 | 296.5266 | 0 | 0 | 0 | 0 | 180 | 116.5266 | 22000 | 116.5266 | 748751.8012 | 468.072 | 0
8101 | 12 | 0 | 1 | 0.40046 | 305.1787 | 0 | 0 | 0 | 0 | 49.3055 | 200 | 22000 | 200 | 748951.8012 | 510.81 | 55.8732
8102 | 12 | 0 | 1 | 0.56664 | 311.9756 | 0 | 0 | 0 | 0 | 0 | 200 | 22000 | 200 | 749151.8012 | 510.81 | 111.9756
8103 | 12 | 0 | 0.89666 | 0.41453 | 275.9088 | 0 | 0 | 0 | 0 | 0 | 200 | 22000 | 200 | 749351.8012 | 510.81 | 75.9088
8104 | 12 | 0 | 0.6187 | 0.41156 | 195.5141 | 0 | 0 | 0 | 0 | 0 | 56.1988 | 22000 | 56.1988 | 749408 | 510.81 | 139.3153
8105 | 12 | 0 | 0.30798 | 0.42929 | 106.5033 | 0 | 0 | 0 | 0 | 0 | 0 | 22000 | 0 | 749408 | 510.81 | 106.5033
8106 | 12 | 0 | 0.043916 | 0.65011 | 39.2726 | 0 | 0 | 0 | 0 | 0 | 0 | 22000 | 0 | 749408 | 510.81 | 39.2726
8107 | 12 | 0 | 0 | 0.71345 | 29.1801 | 0 | 0 | 0 | 0 | 0 | 0 | 22000 | 0 | 749408 | 510.81 | 29.1801
8108 | 12 | 1 | 0 | 0.7097 | 29.0266 | 200 | 29.0266 | 170.9734 | 200 | 0 | 0 | 21800 | 200 | 749608 | 339.8366 | 0
8109 | 12 | 1 | 0 | 0.47518 | 19.4349 | 200 | 19.4349 | 180 | 199.4349 | 0 | 0 | 21600 | 199.4349 | 749807.4349 | 159.8366 | 0
8110 | 12 | 0 | 0 | 0.47969 | 19.6194 | 0 | 0 | 0 | 0 | 19.6194 | 0 | 21600 | 0 | 749807.4349 | 176.8427 | 0
8111 | 12 | 0 | 0 | 0.72788 | 29.7704 | 0 | 0 | 0 | 0 | 29.7704 | 0 | 21600 | 0 | 749807.4349 | 202.6476 | 0
8112 | 12 | 0 | 0 | 0.61298 | 25.0707 | 0 | 0 | 0 | 0 | 25.0707 | 0 | 21600 | 0 | 749807.4349 | 224.3789 | 0
8113 | 12 | 0 | 0 | 0.60541 | 24.7611 | 0 | 0 | 0 | 0 | 24.7611 | 0 | 21600 | 0 | 749807.4349 | 245.8418 | 0
8114 | 12 | 0 | 0 | 0.54761 | 22.3972 | 0 | 0 | 0 | 0 | 22.3972 | 0 | 21600 | 0 | 749807.4349 | 265.2558 | 0
8115 | 12 | 0 | 0 | 0.42383 | 17.3348 | 0 | 0 | 0 | 0 | 17.3348 | 0 | 21600 | 0 | 749807.4349 | 280.2816 | 0
8116 | 12 | 0 | 0 | 0.30275 | 12.3824 | 0 | 0 | 0 | 0 | 12.3824 | 0 | 21600 | 0 | 749807.4349 | 291.0147 | 0
8117 | 12 | 0 | 0 | 0.22623 | 9.2528 | 0 | 0 | 0 | 0 | 9.2528 | 0 | 21600 | 0 | 749807.4349 | 299.035 | 0
8118 | 12 | 0 | 0 | 0.14078 | 5.7581 | 0 | 0 | 0 | 0 | 5.7581 | 0 | 21600 | 0 | 749807.4349 | 304.026 | 0
8119 | 12 | 0 | 0 | 0.18836 | 7.7038 | 0 | 0 | 0 | 0 | 7.7038 | 0 | 21600 | 0 | 749807.4349 | 310.7037 | 0
8120 | 12 | 1 | 0.050166 | 0.15634 | 20.8822 | 200 | 20.8822 | 179.1178 | 200 | 0 | 0 | 21400 | 200 | 750007.4349 | 131.5859 | 0
8121 | 12 | 1 | 0.35182 | 0.19762 | 109.6871 | 200 | 109.6871 | 90.3129 | 200 | 0 | 0 | 21200 | 200 | 750207.4349 | 41.273 | 0
8122 | 12 | 0 | 0.70676 | 0.27474 | 215.3491 | 0 | 0 | 0 | 0 | 180 | 0.56514 | 21200 | 0.56514 | 750208 | 197.297 | 34.784
8123 | 12 | 0 | 1 | 0.3864 | 304.6038 | 0 | 0 | 0 | 0 | 180 | 0 | 21200 | 0 | 750208 | 353.321 | 124.6038
8124 | 12 | 0 | 1 | 0.28042 | 300.2691 | 0 | 0 | 0 | 0 | 180 | 0 | 21200 | 0 | 750208 | 509.345 | 120.2691
8125 | 12 | 0 | 1 | 0.33379 | 302.4521 | 0 | 0 | 0 | 0 | 1.6901 | 0 | 21200 | 0 | 750208 | 510.81 | 300.762
8126 | 12 | 0 | 1 | 0.33728 | 302.5947 | 0 | 0 | 0 | 0 | 0 | 0 | 21200 | 0 | 750208 | 510.81 | 302.5947
8127 | 12 | 0 | 1 | 0.3456 | 302.9349 | 0 | 0 | 0 | 0 | 0 | 0 | 21200 | 0 | 750208 | 510.81 | 302.9349
8128 | 12 | 0 | 0.70676 | 0.21587 | 212.9415 | 0 | 0 | 0 | 0 | 0 | 0 | 21200 | 0 | 750208 | 510.81 | 212.9415
8129 | 12 | 0 | 0.35182 | 0.1349 | 107.122 | 0 | 0 | 0 | 0 | 0 | 0 | 21200 | 0 | 750208 | 510.81 | 107.122
8130 | 12 | 0 | 0.050166 | 0.15705 | 20.9112 | 0 | 0 | 0 | 0 | 0 | 0 | 21200 | 0 | 750208 | 510.81 | 20.9112
8131 | 12 | 0 | 0 | 0.10889 | 4.4537 | 0 | 0 | 0 | 0 | 0 | 0 | 21200 | 0 | 750208 | 510.81 | 4.4537
8132 | 12 | 1 | 0 | 0.16374 | 6.6971 | 200 | 6.6971 | 180 | 186.6971 | 0 | 0 | 21000 | 186.6971 | 750394.6971 | 330.81 | 0
8133 | 12 | 1 | 0 | 0.17705 | 7.2415 | 200 | 7.2415 | 180 | 187.2415 | 0 | 0 | 20800 | 187.2415 | 750581.9386 | 150.81 | 0
8134 | 12 | 0 | 0 | 0.17177 | 7.0254 | 0 | 0 | 0 | 0 | 7.0254 | 0 | 20800 | 0 | 750581.9386 | 156.8996 | 0
8135 | 12 | 0 | 0 | 0.13762 | 5.6289 | 0 | 0 | 0 | 0 | 5.6289 | 0 | 20800 | 0 | 750581.9386 | 161.7787 | 0
8136 | 12 | 0 | 0 | 0.1215 | 4.9692 | 0 | 0 | 0 | 0 | 4.9692 | 0 | 20800 | 0 | 750581.9386 | 166.086 | 0
8137 | 12 | 0 | 0 | 0.1857 | 7.595 | 0 | 0 | 0 | 0 | 7.595 | 0 | 20800 | 0 | 750581.9386 | 172.6694 | 0
8138 | 12 | 0 | 0 | 0.12948 | 5.2959 | 0 | 0 | 0 | 0 | 5.2959 | 0 | 20800 | 0 | 750581.9386 | 177.2599 | 0
8139 | 12 | 0 | 0 | 0.097459 | 3.9861 | 0 | 0 | 0 | 0 | 3.9861 | 0 | 20800 | 0 | 750581.9386 | 180.715 | 0
8140 | 12 | 0 | 0 | 0.099931 | 4.0872 | 0 | 0 | 0 | 0 | 4.0872 | 0 | 20800 | 0 | 750581.9386 | 184.2578 | 0
8141 | 12 | 0 | 0 | 0.10036 | 4.1048 | 0 | 0 | 0 | 0 | 4.1048 | 0 | 20800 | 0 | 750581.9386 | 187.8159 | 0
8142 | 12 | 0 | 0 | 0.10454 | 4.2756 | 0 | 0 | 0 | 0 | 4.2756 | 0 | 20800 | 0 | 750581.9386 | 191.522 | 0
8143 | 12 | 0 | 0 | 0.14291 | 5.8451 | 0 | 0 | 0 | 0 | 5.8451 | 0 | 20800 | 0 | 750581.9386 | 196.5885 | 0
8144 | 12 | 1 | 0.050731 | 0.13877 | 20.3268 | 200 | 20.3268 | 179.6732 | 200 | 0 | 0 | 20600 | 200 | 750781.9386 | 16.9153 | 0
8145 | 12 | 1 | 0.35578 | 0.21883 | 111.6983 | 200 | 111.6983 | 16.9153 | 128.6136 | 0 | 0 | 20400 | 128.6136 | 750910.5522 | 0 | 0
8146 | 12 | 0 | 0.71472 | 0.27882 | 217.8138 | 0 | 0 | 0 | 0 | 180 | 37.8138 | 20400 | 37.8138 | 750948.3661 | 156.024 | 0
8147 | 12 | 0 | 1 | 0.34178 | 302.7788 | 0 | 0 | 0 | 0 | 180 | 59.6339 | 20400 | 59.6339 | 751008 | 312.048 | 63.1449
8148 | 12 | 0 | 1 | 0.34701 | 302.9925 | 0 | 0 | 0 | 0 | 180 | 0 | 20400 | 0 | 751008 | 468.072 | 122.9925
8149 | 12 | 0 | 1 | 0.39833 | 305.0918 | 0 | 0 | 0 | 0 | 49.3055 | 0 | 20400 | 0 | 751008 | 510.81 | 255.7863
8150 | 12 | 0 | 1 | 0.33815 | 302.6302 | 0 | 0 | 0 | 0 | 0 | 0 | 20400 | 0 | 751008 | 510.81 | 302.6302
8151 | 12 | 0 | 1 | 0.40749 | 305.4663 | 0 | 0 | 0 | 0 | 0 | 0 | 20400 | 0 | 751008 | 510.81 | 305.4663
8152 | 12 | 0 | 0.71472 | 0.38166 | 222.0201 | 0 | 0 | 0 | 0 | 0 | 0 | 20400 | 0 | 751008 | 510.81 | 222.0201
8153 | 12 | 0 | 0.35578 | 0.32369 | 115.9868 | 0 | 0 | 0 | 0 | 0 | 0 | 20400 | 0 | 751008 | 510.81 | 115.9868
8154 | 12 | 0 | 0.050731 | 0.22217 | 23.7377 | 0 | 0 | 0 | 0 | 0 | 0 | 20400 | 0 | 751008 | 510.81 | 23.7377
8155 | 12 | 0 | 0 | 0.18797 | 7.6881 | 0 | 0 | 0 | 0 | 0 | 0 | 20400 | 0 | 751008 | 510.81 | 7.6881
8156 | 12 | 1 | 0 | 0.17095 | 6.9917 | 200 | 6.9917 | 180 | 186.9917 | 0 | 0 | 20200 | 186.9917 | 751194.9917 | 330.81 | 0
8157 | 12 | 1 | 0 | 0.15632 | 6.3934 | 200 | 6.3934 | 180 | 186.3934 | 0 | 0 | 20000 | 186.3934 | 751381.385 | 150.81 | 0
8158 | 12 | 0 | 0 | 0.15253 | 6.2386 | 0 | 0 | 0 | 0 | 6.2386 | 0 | 20000 | 0 | 751381.385 | 156.2177 | 0
8159 | 12 | 0 | 0 | 0.12978 | 5.3081 | 0 | 0 | 0 | 0 | 5.3081 | 0 | 20000 | 0 | 751381.385 | 160.8187 | 0
8160 | 12 | 0 | 0 | 0.093842 | 3.8381 | 0 | 0 | 0 | 0 | 3.8381 | 0 | 20000 | 0 | 751381.385 | 164.1456 | 0
8161 | 12 | 0 | 0 | 0.15798 | 6.4614 | 0 | 0 | 0 | 0 | 6.4614 | 0 | 20000 | 0 | 751381.385 | 169.7464 | 0
8162 | 12 | 0 | 0 | 0.13533 | 5.5351 | 0 | 0 | 0 | 0 | 5.5351 | 0 | 20000 | 0 | 751381.385 | 174.5442 | 0
8163 | 12 | 0 | 0 | 0.18574 | 7.5968 | 0 | 0 | 0 | 0 | 7.5968 | 0 | 20000 | 0 | 751381.385 | 181.1291 | 0
8164 | 12 | 0 | 0 | 0.16685 | 6.8243 | 0 | 0 | 0 | 0 | 6.8243 | 0 | 20000 | 0 | 751381.385 | 187.0444 | 0
8165 | 12 | 0 | 0 | 0.16956 | 6.9349 | 0 | 0 | 0 | 0 | 6.9349 | 0 | 20000 | 0 | 751381.385 | 193.0556 | 0
8166 | 12 | 0 | 0 | 0.15238 | 6.2323 | 0 | 0 | 0 | 0 | 6.2323 | 0 | 20000 | 0 | 751381.385 | 198.4577 | 0
8167 | 12 | 0 | 0 | 0.16544 | 6.7665 | 0 | 0 | 0 | 0 | 6.7665 | 0 | 20000 | 0 | 751381.385 | 204.323 | 0
8168 | 12 | 1 | 0.045907 | 0.19265 | 21.1374 | 200 | 21.1374 | 178.8626 | 200 | 0 | 0 | 19800 | 200 | 751581.385 | 25.4603 | 0
8169 | 12 | 1 | 0.32194 | 0.25842 | 103.5468 | 200 | 103.5468 | 25.4603 | 129.0072 | 0 | 0 | 19600 | 129.0072 | 751710.3922 | 0 | 0
8170 | 12 | 0 | 0.64675 | 0.26551 | 197.641 | 0 | 0 | 0 | 0 | 180 | 17.641 | 19600 | 17.641 | 751728.0331 | 156.024 | 0
8171 | 12 | 0 | 0.93731 | 0.24173 | 280.5806 | 0 | 0 | 0 | 0 | 180 | 79.9669 | 19600 | 79.9669 | 751808 | 312.048 | 20.6138
8172 | 12 | 0 | 1 | 0.25988 | 299.4293 | 0 | 0 | 0 | 0 | 180 | 0 | 19600 | 0 | 751808 | 468.072 | 119.4293
8173 | 12 | 0 | 1 | 0.4151 | 305.7776 | 0 | 0 | 0 | 0 | 49.3055 | 0 | 19600 | 0 | 751808 | 510.81 | 256.4721
8174 | 12 | 0 | 1 | 0.56711 | 311.9949 | 0 | 0 | 0 | 0 | 0 | 0 | 19600 | 0 | 751808 | 510.81 | 311.9949
8175 | 12 | 0 | 0.93731 | 0.57573 | 294.2412 | 0 | 0 | 0 | 0 | 0 | 0 | 19600 | 0 | 751808 | 510.81 | 294.2412
8176 | 12 | 0 | 0.64675 | 0.35113 | 201.1427 | 0 | 0 | 0 | 0 | 0 | 0 | 19600 | 0 | 751808 | 510.81 | 201.1427
8177 | 12 | 0 | 0.32194 | 0.27735 | 104.3208 | 0 | 0 | 0 | 0 | 0 | 0 | 19600 | 0 | 751808 | 510.81 | 104.3208
8178 | 12 | 0 | 0.045907 | 0.39444 | 29.3905 | 0 | 0 | 0 | 0 | 0 | 0 | 19600 | 0 | 751808 | 510.81 | 29.3905
8179 | 12 | 0 | 0 | 0.33747 | 13.8024 | 0 | 0 | 0 | 0 | 0 | 0 | 19600 | 0 | 751808 | 510.81 | 13.8024
8180 | 12 | 1 | 0 | 0.30957 | 12.6614 | 200 | 12.6614 | 180 | 192.6614 | 0 | 0 | 19400 | 192.6614 | 752000.6614 | 330.81 | 0
8181 | 12 | 1 | 0 | 0.33373 | 13.6497 | 200 | 13.6497 | 180 | 193.6497 | 0 | 0 | 19200 | 193.6497 | 752194.3111 | 150.81 | 0
8182 | 12 | 0 | 0 | 0.29387 | 12.0194 | 0 | 0 | 0 | 0 | 12.0194 | 0 | 19200 | 0 | 752194.3111 | 161.2285 | 0
8183 | 12 | 0 | 0 | 0.33093 | 13.5351 | 0 | 0 | 0 | 0 | 13.5351 | 0 | 19200 | 0 | 752194.3111 | 172.9607 | 0
8184 | 12 | 0 | 0 | 0.3257 | 13.3213 | 0 | 0 | 0 | 0 | 13.3213 | 0 | 19200 | 0 | 752194.3111 | 184.5075 | 0
8185 | 12 | 0 | 0 | 0.2092 | 8.5564 | 0 | 0 | 0 | 0 | 8.5564 | 0 | 19200 | 0 | 752194.3111 | 191.9242 | 0
8186 | 12 | 0 | 0 | 0.37895 | 15.4991 | 0 | 0 | 0 | 0 | 15.4991 | 0 | 19200 | 0 | 752194.3111 | 205.3588 | 0
8187 | 12 | 0 | 0 | 0.32344 | 13.2287 | 0 | 0 | 0 | 0 | 13.2287 | 0 | 19200 | 0 | 752194.3111 | 216.8255 | 0
8188 | 12 | 0 | 0 | 0.21498 | 8.7928 | 0 | 0 | 0 | 0 | 8.7928 | 0 | 19200 | 0 | 752194.3111 | 224.4471 | 0
8189 | 12 | 0 | 0 | 0.18682 | 7.6411 | 0 | 0 | 0 | 0 | 7.6411 | 0 | 19200 | 0 | 752194.3111 | 231.0703 | 0
8190 | 12 | 0 | 0 | 0.14442 | 5.9067 | 0 | 0 | 0 | 0 | 5.9067 | 0 | 19200 | 0 | 752194.3111 | 236.1903 | 0
8191 | 12 | 0 | 0 | 0.1549 | 6.3352 | 0 | 0 | 0 | 0 | 6.3352 | 0 | 19200 | 0 | 752194.3111 | 241.6817 | 0
8192 | 12 | 1 | 0.045825 | 0.10919 | 17.7002 | 200 | 17.7002 | 180 | 197.7002 | 0 | 0 | 19000 | 197.7002 | 752392.0113 | 61.6817 | 0
8193 | 12 | 1 | 0.32137 | 0.087411 | 96.3879 | 200 | 96.3879 | 61.6817 | 158.0696 | 0 | 0 | 18800 | 158.0696 | 752550.0808 | 0 | 0
8194 | 12 | 0 | 0.64561 | 0.17403 | 193.569 | 0 | 0 | 0 | 0 | 180 | 13.569 | 18800 | 13.569 | 752563.6499 | 156.024 | 0
8195 | 12 | 0 | 0.93565 | 0.18471 | 277.7695 | 0 | 0 | 0 | 0 | 180 | 44.3501 | 18800 | 44.3501 | 752608 | 312.048 | 53.4193
8196 | 12 | 0 | 1 | 0.18592 | 296.404 | 0 | 0 | 0 | 0 | 180 | 0 | 18800 | 0 | 752608 | 468.072 | 116.404
8197 | 12 | 0 | 1 | 0.29211 | 300.7471 | 0 | 0 | 0 | 0 | 49.3055 | 0 | 18800 | 0 | 752608 | 510.81 | 251.4416
8198 | 12 | 0 | 1 | 0.26746 | 299.7391 | 0 | 0 | 0 | 0 | 0 | 0 | 18800 | 0 | 752608 | 510.81 | 299.7391
8199 | 12 | 0 | 0.93565 | 0.29531 | 282.2932 | 0 | 0 | 0 | 0 | 0 | 0 | 18800 | 0 | 752608 | 510.81 | 282.2932
8200 | 12 | 0 | 0.64561 | 0.35502 | 200.9716 | 0 | 0 | 0 | 0 | 0 | 0 | 18800 | 0 | 752608 | 510.81 | 200.9716
8201 | 12 | 0 | 0.32137 | 0.38793 | 108.6791 | 0 | 0 | 0 | 0 | 0 | 0 | 18800 | 0 | 752608 | 510.81 | 108.6791
8202 | 12 | 0 | 0.045825 | 0.28545 | 24.9092 | 0 | 0 | 0 | 0 | 0 | 0 | 18800 | 0 | 752608 | 510.81 | 24.9092
8203 | 12 | 0 | 0 | 0.32822 | 13.4243 | 0 | 0 | 0 | 0 | 0 | 0 | 18800 | 0 | 752608 | 510.81 | 13.4243
8204 | 12 | 1 | 0 | 0.29451 | 12.0455 | 200 | 12.0455 | 180 | 192.0455 | 0 | 0 | 18600 | 192.0455 | 752800.0455 | 330.81 | 0
8205 | 12 | 1 | 0 | 0.27159 | 11.108 | 200 | 11.108 | 180 | 191.108 | 0 | 0 | 18400 | 191.108 | 752991.1535 | 150.81 | 0
8206 | 12 | 0 | 0 | 0.23897 | 9.7739 | 0 | 0 | 0 | 0 | 9.7739 | 0 | 18400 | 0 | 752991.1535 | 159.282 | 0
8207 | 12 | 0 | 0 | 0.25882 | 10.5857 | 0 | 0 | 0 | 0 | 10.5857 | 0 | 18400 | 0 | 752991.1535 | 168.4577 | 0
8208 | 12 | 0 | 0 | 0.24757 | 10.1258 | 0 | 0 | 0 | 0 | 10.1258 | 0 | 18400 | 0 | 752991.1535 | 177.2347 | 0
8209 | 12 | 0 | 0 | 0.3461 | 14.1554 | 0 | 0 | 0 | 0 | 14.1554 | 0 | 18400 | 0 | 752991.1535 | 189.5047 | 0
8210 | 12 | 0 | 0 | 0.28683 | 11.7315 | 0 | 0 | 0 | 0 | 11.7315 | 0 | 18400 | 0 | 752991.1535 | 199.6735 | 0
8211 | 12 | 0 | 0 | 0.30991 | 12.6752 | 0 | 0 | 0 | 0 | 12.6752 | 0 | 18400 | 0 | 752991.1535 | 210.6604 | 0
8212 | 12 | 0 | 0 | 0.28942 | 11.8372 | 0 | 0 | 0 | 0 | 11.8372 | 0 | 18400 | 0 | 752991.1535 | 220.9208 | 0
8213 | 12 | 0 | 0 | 0.2464 | 10.0777 | 0 | 0 | 0 | 0 | 10.0777 | 0 | 18400 | 0 | 752991.1535 | 229.6562 | 0
8214 | 12 | 0 | 0 | 0.20887 | 8.5429 | 0 | 0 | 0 | 0 | 8.5429 | 0 | 18400 | 0 | 752991.1535 | 237.0612 | 0
8215 | 12 | 0 | 0 | 0.29366 | 12.0108 | 0 | 0 | 0 | 0 | 12.0108 | 0 | 18400 | 0 | 752991.1535 | 247.4722 | 0
8216 | 12 | 1 | 0.047731 | 0.30663 | 26.3258 | 200 | 26.3258 | 173.6742 | 200 | 0 | 0 | 18200 | 200 | 753191.1535 | 73.798 | 0
8217 | 12 | 1 | 0.33474 | 0.3628 | 111.5106 | 200 | 111.5106 | 73.798 | 185.3086 | 0 | 0 | 18000 | 185.3086 | 753376.4622 | 0 | 0
8218 | 12 | 0 | 0.67245 | 0.34914 | 208.4838 | 0 | 0 | 0 | 0 | 180 | 28.4838 | 18000 | 28.4838 | 753404.946 | 156.024 | 0
8219 | 12 | 0 | 0.97455 | 0.43039 | 299.0531 | 0 | 0 | 0 | 0 | 180 | 3.054 | 18000 | 3.054 | 753408 | 312.048 | 115.9991
8220 | 12 | 0 | 1 | 0.38648 | 304.6072 | 0 | 0 | 0 | 0 | 180 | 0 | 18000 | 0 | 753408 | 468.072 | 124.6072
8221 | 12 | 0 | 1 | 0.33035 | 302.3115 | 0 | 0 | 0 | 0 | 49.3055 | 0 | 18000 | 0 | 753408 | 510.81 | 253.006
8222 | 12 | 0 | 1 | 0.18403 | 296.3269 | 0 | 0 | 0 | 0 | 0 | 0 | 18000 | 0 | 753408 | 510.81 | 296.3269
8223 | 12 | 0 | 0.97455 | 0.16395 | 288.1559 | 0 | 0 | 0 | 0 | 0 | 0 | 18000 | 0 | 753408 | 510.81 | 288.1559
8224 | 12 | 0 | 0.67245 | 0.13363 | 199.6692 | 0 | 0 | 0 | 0 | 0 | 0 | 18000 | 0 | 753408 | 510.81 | 199.6692
8225 | 12 | 0 | 0.33474 | 0.099322 | 100.7343 | 0 | 0 | 0 | 0 | 0 | 0 | 18000 | 0 | 753408 | 510.81 | 100.7343
8226 | 12 | 0 | 0.047731 | 0.12485 | 18.8911 | 0 | 0 | 0 | 0 | 0 | 0 | 18000 | 0 | 753408 | 510.81 | 18.8911
8227 | 12 | 0 | 0 | 0.23793 | 9.7314 | 0 | 0 | 0 | 0 | 0 | 0 | 18000 | 0 | 753408 | 510.81 | 9.7314
8228 | 12 | 1 | 0 | 0.23583 | 9.6454 | 200 | 9.6454 | 180 | 189.6454 | 0 | 0 | 17800 | 189.6454 | 753597.6454 | 330.81 | 0
8229 | 12 | 1 | 0 | 0.15071 | 6.1641 | 200 | 6.1641 | 180 | 186.1641 | 0 | 0 | 17600 | 186.1641 | 753783.8095 | 150.81 | 0
8230 | 12 | 0 | 0 | 0.16502 | 6.7495 | 0 | 0 | 0 | 0 | 6.7495 | 0 | 17600 | 0 | 753783.8095 | 156.6605 | 0
8231 | 12 | 0 | 0 | 0.14781 | 6.0454 | 0 | 0 | 0 | 0 | 6.0454 | 0 | 17600 | 0 | 753783.8095 | 161.9006 | 0
8232 | 12 | 0 | 0 | 0.17539 | 7.1734 | 0 | 0 | 0 | 0 | 7.1734 | 0 | 17600 | 0 | 753783.8095 | 168.1185 | 0
8233 | 12 | 0 | 0 | 0.18799 | 7.6889 | 0 | 0 | 0 | 0 | 7.6889 | 0 | 17600 | 0 | 753783.8095 | 174.7832 | 0
8234 | 12 | 0 | 0 | 0.21183 | 8.6639 | 0 | 0 | 0 | 0 | 8.6639 | 0 | 17600 | 0 | 753783.8095 | 182.293 | 0
8235 | 12 | 0 | 0 | 0.29506 | 12.0677 | 0 | 0 | 0 | 0 | 12.0677 | 0 | 17600 | 0 | 753783.8095 | 192.7534 | 0
8236 | 12 | 0 | 0 | 0.39056 | 15.974 | 0 | 0 | 0 | 0 | 15.974 | 0 | 17600 | 0 | 753783.8095 | 206.5997 | 0
8237 | 12 | 0 | 0 | 0.38299 | 15.6643 | 0 | 0 | 0 | 0 | 15.6643 | 0 | 17600 | 0 | 753783.8095 | 220.1775 | 0
8238 | 12 | 0 | 0 | 0.39497 | 16.1544 | 0 | 0 | 0 | 0 | 16.1544 | 0 | 17600 | 0 | 753783.8095 | 234.1802 | 0
8239 | 12 | 0 | 0 | 0.41457 | 16.9557 | 0 | 0 | 0 | 0 | 16.9557 | 0 | 17600 | 0 | 753783.8095 | 248.8774 | 0
8240 | 12 | 1 | 0.048026 | 0.35256 | 28.2897 | 200 | 28.2897 | 171.7103 | 200 | 0 | 0 | 17400 | 200 | 753983.8095 | 77.1671 | 0
8241 | 12 | 1 | 0.33681 | 0.28347 | 108.8646 | 200 | 108.8646 | 77.1671 | 186.0317 | 0 | 0 | 17200 | 186.0317 | 754169.8412 | 0 | 0
8242 | 12 | 0 | 0.67661 | 0.27444 | 206.6305 | 0 | 0 | 0 | 0 | 180 | 26.6305 | 17200 | 26.6305 | 754196.4717 | 156.024 | 0
8243 | 12 | 0 | 0.98058 | 0.25878 | 293.7767 | 0 | 0 | 0 | 0 | 180 | 11.5283 | 17200 | 11.5283 | 754208 | 312.048 | 102.2484
8244 | 12 | 0 | 1 | 0.27037 | 299.8579 | 0 | 0 | 0 | 0 | 180 | 0 | 17200 | 0 | 754208 | 468.072 | 119.8579
8245 | 12 | 0 | 1 | 0.6327 | 314.6774 | 0 | 0 | 0 | 0 | 49.3055 | 0 | 17200 | 0 | 754208 | 510.81 | 265.3719
8246 | 12 | 0 | 1 | 0.60279 | 313.4542 | 0 | 0 | 0 | 0 | 0 | 0 | 17200 | 0 | 754208 | 510.81 | 313.4542
8247 | 12 | 0 | 0.98058 | 0.66494 | 310.3886 | 0 | 0 | 0 | 0 | 0 | 0 | 17200 | 0 | 754208 | 510.81 | 310.3886
8248 | 12 | 0 | 0.67661 | 0.6999 | 224.0316 | 0 | 0 | 0 | 0 | 0 | 0 | 17200 | 0 | 754208 | 510.81 | 224.0316
8249 | 12 | 0 | 0.33681 | 0.8893 | 133.6427 | 0 | 0 | 0 | 0 | 0 | 0 | 17200 | 0 | 754208 | 510.81 | 133.6427
8250 | 12 | 0 | 0.048026 | 1 | 54.7699 | 0 | 0 | 0 | 0 | 0 | 0 | 17200 | 0 | 754208 | 510.81 | 54.7699
8251 | 12 | 0 | 0 | 0.72169 | 29.517 | 0 | 0 | 0 | 0 | 0 | 0 | 17200 | 0 | 754208 | 510.81 | 29.517
8252 | 12 | 1 | 0 | 0.86507 | 35.3812 | 200 | 35.3812 | 164.6188 | 200 | 0 | 0 | 17000 | 200 | 754408 | 346.1912 | 0
8253 | 12 | 1 | 0 | 0.79988 | 32.715 | 200 | 32.715 | 167.285 | 200 | 0 | 0 | 16800 | 200 | 754608 | 178.9062 | 0
8254 | 12 | 0 | 0 | 0.61372 | 25.1013 | 0 | 0 | 0 | 0 | 25.1013 | 0 | 16800 | 0 | 754608 | 200.664 | 0
8255 | 12 | 0 | 0 | 0.52079 | 21.3003 | 0 | 0 | 0 | 0 | 21.3003 | 0 | 16800 | 0 | 754608 | 219.1271 | 0
8256 | 12 | 0 | 0 | 0.5239 | 21.4275 | 0 | 0 | 0 | 0 | 21.4275 | 0 | 16800 | 0 | 754608 | 237.7005 | 0
8257 | 12 | 0 | 0 | 0.45771 | 18.7203 | 0 | 0 | 0 | 0 | 18.7203 | 0 | 16800 | 0 | 754608 | 253.9272 | 0
8258 | 12 | 0 | 0 | 0.42064 | 17.2041 | 0 | 0 | 0 | 0 | 17.2041 | 0 | 16800 | 0 | 754608 | 268.8397 | 0
8259 | 12 | 0 | 0 | 0.35998 | 14.7231 | 0 | 0 | 0 | 0 | 14.7231 | 0 | 16800 | 0 | 754608 | 281.6017 | 0
8260 | 12 | 0 | 0 | 0.29099 | 11.9015 | 0 | 0 | 0 | 0 | 11.9015 | 0 | 16800 | 0 | 754608 | 291.9179 | 0
8261 | 12 | 0 | 0 | 0.38135 | 15.5971 | 0 | 0 | 0 | 0 | 15.5971 | 0 | 16800 | 0 | 754608 | 305.4374 | 0
8262 | 12 | 0 | 0 | 0.35632 | 14.5734 | 0 | 0 | 0 | 0 | 14.5734 | 0 | 16800 | 0 | 754608 | 318.0696 | 0
8263 | 12 | 0 | 0 | 0.27888 | 11.4061 | 0 | 0 | 0 | 0 | 11.4061 | 0 | 16800 | 0 | 754608 | 327.9565 | 0
8264 | 12 | 1 | 0.053323 | 0.34736 | 29.6065 | 200 | 29.6065 | 170.3935 | 200 | 0 | 0 | 16600 | 200 | 754808 | 157.563 | 0
8265 | 12 | 1 | 0.37395 | 0.39314 | 124.0773 | 200 | 124.0773 | 75.9227 | 200 | 0 | 0 | 16400 | 200 | 755008 | 81.6403 | 0
8266 | 12 | 0 | 0.75123 | 0.2784 | 228.3429 | 0 | 0 | 0 | 0 | 180 | 0 | 16400 | 0 | 755008 | 237.6643 | 48.3429
8267 | 12 | 0 | 1 | 0.29637 | 300.9215 | 0 | 0 | 0 | 0 | 180 | 0 | 16400 | 0 | 755008 | 393.6883 | 120.9215
8268 | 12 | 0 | 1 | 0.24444 | 298.7976 | 0 | 0 | 0 | 0 | 135.1196 | 0 | 16400 | 0 | 755008 | 510.81 | 163.678
8269 | 12 | 0 | 1 | 0.25873 | 299.382 | 0 | 0 | 0 | 0 | 0 | 0 | 16400 | 0 | 755008 | 510.81 | 299.382
8270 | 12 | 0 | 1 | 0.17243 | 295.8525 | 0 | 0 | 0 | 0 | 0 | 0 | 16400 | 0 | 755008 | 510.81 | 295.8525
8271 | 12 | 0 | 1 | 0.20614 | 297.2312 | 0 | 0 | 0 | 0 | 0 | 0 | 16400 | 0 | 755008 | 510.81 | 297.2312
8272 | 12 | 0 | 0.75123 | 0.22225 | 226.0463 | 0 | 0 | 0 | 0 | 0 | 0 | 16400 | 0 | 755008 | 510.81 | 226.0463
8273 | 12 | 0 | 0.37395 | 0.17847 | 115.2973 | 0 | 0 | 0 | 0 | 0 | 0 | 16400 | 0 | 755008 | 510.81 | 115.2973
8274 | 12 | 0 | 0.053323 | 0.27866 | 26.7968 | 0 | 0 | 0 | 0 | 0 | 0 | 16400 | 0 | 755008 | 510.81 | 26.7968
8275 | 12 | 0 | 0 | 0.19079 | 7.8031 | 0 | 0 | 0 | 0 | 0 | 0 | 16400 | 0 | 755008 | 510.81 | 7.8031
8276 | 12 | 1 | 0 | 0.16546 | 6.7672 | 200 | 6.7672 | 180 | 186.7672 | 0 | 0 | 16200 | 186.7672 | 755194.7672 | 330.81 | 0
8277 | 12 | 1 | 0 | 0.16489 | 6.7439 | 200 | 6.7439 | 180 | 186.7439 | 0 | 0 | 16000 | 186.7439 | 755381.5111 | 150.81 | 0
8278 | 12 | 0 | 0 | 0.10684 | 4.3697 | 0 | 0 | 0 | 0 | 4.3697 | 0 | 16000 | 0 | 755381.5111 | 154.5977 | 0
8279 | 12 | 0 | 0 | 0.13465 | 5.5073 | 0 | 0 | 0 | 0 | 5.5073 | 0 | 16000 | 0 | 755381.5111 | 159.3714 | 0
8280 | 12 | 0 | 0 | 0.11676 | 4.7753 | 0 | 0 | 0 | 0 | 4.7753 | 0 | 16000 | 0 | 755381.5111 | 163.5107 | 0
8281 | 12 | 0 | 0 | 0.11806 | 4.8286 | 0 | 0 | 0 | 0 | 4.8286 | 0 | 16000 | 0 | 755381.5111 | 167.6961 | 0
8282 | 12 | 0 | 0 | 0.12648 | 5.173 | 0 | 0 | 0 | 0 | 5.173 | 0 | 16000 | 0 | 755381.5111 | 172.1801 | 0
8283 | 12 | 0 | 0 | 0.085273 | 3.4877 | 0 | 0 | 0 | 0 | 3.4877 | 0 | 16000 | 0 | 755381.5111 | 175.2032 | 0
8284 | 12 | 0 | 0 | 0.089636 | 3.6661 | 0 | 0 | 0 | 0 | 3.6661 | 0 | 16000 | 0 | 755381.5111 | 178.381 | 0
8285 | 12 | 0 | 0 | 0.060879 | 2.49 | 0 | 0 | 0 | 0 | 2.49 | 0 | 16000 | 0 | 755381.5111 | 180.5393 | 0
8286 | 12 | 0 | 0 | 0.074928 | 3.0646 | 0 | 0 | 0 | 0 | 3.0646 | 0 | 16000 | 0 | 755381.5111 | 183.1956 | 0
8287 | 12 | 0 | 0 | 0.07583 | 3.1014 | 0 | 0 | 0 | 0 | 3.1014 | 0 | 16000 | 0 | 755381.5111 | 185.884 | 0
8288 | 12 | 1 | 0.042696 | 0.084935 | 15.8044 | 200 | 15.8044 | 180 | 195.8044 | 0 | 0 | 15800 | 195.8044 | 755577.3155 | 5.884 | 0
8289 | 12 | 1 | 0.29942 | 0.1106 | 90.9973 | 200 | 90.9973 | 5.884 | 96.8813 | 0 | 0 | 15600 | 96.8813 | 755674.1968 | 0 | 0
8290 | 12 | 0 | 0.60151 | 0.10569 | 178.0391 | 0 | 0 | 0 | 0 | 178.0391 | 0 | 15600 | 0 | 755674.1968 | 154.3243 | 0
8291 | 12 | 0 | 0.87174 | 0.11001 | 256.2584 | 0 | 0 | 0 | 0 | 180 | 76.2584 | 15600 | 76.2584 | 755750.4552 | 310.3483 | 0
8292 | 12 | 0 | 1 | 0.11573 | 293.5334 | 0 | 0 | 0 | 0 | 180 | 57.5448 | 15600 | 57.5448 | 755808 | 466.3723 | 55.9886
8293 | 12 | 0 | 1 | 0.10705 | 293.1784 | 0 | 0 | 0 | 0 | 51.2664 | 0 | 15600 | 0 | 755808 | 510.81 | 241.912
8294 | 12 | 0 | 1 | 0.10255 | 292.9942 | 0 | 0 | 0 | 0 | 0 | 0 | 15600 | 0 | 755808 | 510.81 | 292.9942
8295 | 12 | 0 | 0.87174 | 0.1132 | 256.389 | 0 | 0 | 0 | 0 | 0 | 0 | 15600 | 0 | 755808 | 510.81 | 256.389
8296 | 12 | 0 | 0.60151 | 0.08147 | 177.0485 | 0 | 0 | 0 | 0 | 0 | 0 | 15600 | 0 | 755808 | 510.81 | 177.0485
8297 | 12 | 0 | 0.29942 | 0.087855 | 90.0669 | 0 | 0 | 0 | 0 | 0 | 0 | 15600 | 0 | 755808 | 510.81 | 90.0669
8298 | 12 | 0 | 0.042696 | 0.10719 | 16.7148 | 0 | 0 | 0 | 0 | 0 | 0 | 15600 | 0 | 755808 | 510.81 | 16.7148
8299 | 12 | 0 | 0 | 0.089646 | 3.6665 | 0 | 0 | 0 | 0 | 0 | 0 | 15600 | 0 | 755808 | 510.81 | 3.6665
8300 | 12 | 1 | 0 | 0.10116 | 4.1376 | 200 | 4.1376 | 180 | 184.1376 | 0 | 0 | 15400 | 184.1376 | 755992.1376 | 330.81 | 0
8301 | 12 | 1 | 0 | 0.1174 | 4.8018 | 200 | 4.8018 | 180 | 184.8018 | 0 | 0 | 15200 | 184.8018 | 756176.9394 | 150.81 | 0
8302 | 12 | 0 | 0 | 0.14753 | 6.0339 | 0 | 0 | 0 | 0 | 6.0339 | 0 | 15200 | 0 | 756176.9394 | 156.0402 | 0
8303 | 12 | 0 | 0 | 0.17711 | 7.244 | 0 | 0 | 0 | 0 | 7.244 | 0 | 15200 | 0 | 756176.9394 | 162.3193 | 0
8304 | 12 | 0 | 0 | 0.11488 | 4.6986 | 0 | 0 | 0 | 0 | 4.6986 | 0 | 15200 | 0 | 756176.9394 | 166.3921 | 0
8305 | 12 | 0 | 0 | 0.14881 | 6.0864 | 0 | 0 | 0 | 0 | 6.0864 | 0 | 15200 | 0 | 756176.9394 | 171.6678 | 0
8306 | 12 | 0 | 0 | 0.17406 | 7.1192 | 0 | 0 | 0 | 0 | 7.1192 | 0 | 15200 | 0 | 756176.9394 | 177.8387 | 0
8307 | 12 | 0 | 0 | 0.14033 | 5.7395 | 0 | 0 | 0 | 0 | 5.7395 | 0 | 15200 | 0 | 756176.9394 | 182.8137 | 0
8308 | 12 | 0 | 0 | 0.094103 | 3.8488 | 0 | 0 | 0 | 0 | 3.8488 | 0 | 15200 | 0 | 756176.9394 | 186.1499 | 0
8309 | 12 | 0 | 0 | 0.15564 | 6.3656 | 0 | 0 | 0 | 0 | 6.3656 | 0 | 15200 | 0 | 756176.9394 | 191.6676 | 0
8310 | 12 | 0 | 0 | 0.27099 | 11.0836 | 0 | 0 | 0 | 0 | 11.0836 | 0 | 15200 | 0 | 756176.9394 | 201.2749 | 0
8311 | 12 | 0 | 0 | 0.24612 | 10.0663 | 0 | 0 | 0 | 0 | 10.0663 | 0 | 15200 | 0 | 756176.9394 | 210.0003 | 0
8312 | 12 | 1 | 0.045857 | 0.25766 | 23.7818 | 200 | 23.7818 | 176.2182 | 200 | 0 | 0 | 15000 | 200 | 756376.9394 | 33.7821 | 0
8313 | 12 | 1 | 0.3216 | 0.21785 | 101.7876 | 200 | 101.7876 | 33.7821 | 135.5696 | 0 | 0 | 14800 | 135.5696 | 756512.509 | 0 | 0
8314 | 12 | 0 | 0.64606 | 0.17342 | 193.6741 | 0 | 0 | 0 | 0 | 180 | 13.6741 | 14800 | 13.6741 | 756526.1831 | 156.024 | 0
8315 | 12 | 0 | 0.9363 | 0.2715 | 281.5074 | 0 | 0 | 0 | 0 | 180 | 81.8169 | 14800 | 81.8169 | 756608 | 312.048 | 19.6905
8316 | 12 | 0 | 1 | 0.2417 | 298.6856 | 0 | 0 | 0 | 0 | 180 | 0 | 14800 | 0 | 756608 | 468.072 | 118.6856
8317 | 12 | 0 | 1 | 0.33731 | 302.5959 | 0 | 0 | 0 | 0 | 49.3055 | 0 | 14800 | 0 | 756608 | 510.81 | 253.2904
8318 | 12 | 0 | 1 | 0.40331 | 305.2955 | 0 | 0 | 0 | 0 | 0 | 0 | 14800 | 0 | 756608 | 510.81 | 305.2955
8319 | 12 | 0 | 0.9363 | 0.57709 | 294.0061 | 0 | 0 | 0 | 0 | 0 | 0 | 14800 | 0 | 756608 | 510.81 | 294.0061
8320 | 12 | 0 | 0.64606 | 0.51981 | 207.8413 | 0 | 0 | 0 | 0 | 0 | 0 | 14800 | 0 | 756608 | 510.81 | 207.8413
8321 | 12 | 0 | 0.3216 | 0.51119 | 113.7851 | 0 | 0 | 0 | 0 | 0 | 0 | 14800 | 0 | 756608 | 510.81 | 113.7851
8322 | 12 | 0 | 0.045857 | 0.81613 | 46.6231 | 0 | 0 | 0 | 0 | 0 | 0 | 14800 | 0 | 756608 | 510.81 | 46.6231
8323 | 12 | 0 | 0 | 0.76071 | 31.1131 | 0 | 0 | 0 | 0 | 0 | 0 | 14800 | 0 | 756608 | 510.81 | 31.1131
8324 | 12 | 1 | 0 | 0.59941 | 24.5159 | 200 | 24.5159 | 175.4841 | 200 | 0 | 0 | 14600 | 200 | 756808 | 335.3259 | 0
8325 | 12 | 1 | 0 | 0.68162 | 27.8784 | 200 | 27.8784 | 172.1216 | 200 | 0 | 0 | 14400 | 200 | 757008 | 163.2043 | 0
8326 | 12 | 0 | 0 | 0.74984 | 30.6687 | 0 | 0 | 0 | 0 | 30.6687 | 0 | 14400 | 0 | 757008 | 189.7879 | 0
8327 | 12 | 0 | 0 | 0.77555 | 31.72 | 0 | 0 | 0 | 0 | 31.72 | 0 | 14400 | 0 | 757008 | 217.2828 | 0
8328 | 12 | 0 | 0 | 0.42604 | 17.425 | 0 | 0 | 0 | 0 | 17.425 | 0 | 14400 | 0 | 757008 | 232.3868 | 0
8329 | 12 | 0 | 0 | 0.42908 | 17.5494 | 0 | 0 | 0 | 0 | 17.5494 | 0 | 14400 | 0 | 757008 | 247.5986 | 0
8330 | 12 | 0 | 0 | 0.39483 | 16.1484 | 0 | 0 | 0 | 0 | 16.1484 | 0 | 14400 | 0 | 757008 | 261.596 | 0
8331 | 12 | 0 | 0 | 0.34449 | 14.0896 | 0 | 0 | 0 | 0 | 14.0896 | 0 | 14400 | 0 | 757008 | 273.8089 | 0
8332 | 12 | 0 | 0 | 0.34937 | 14.2891 | 0 | 0 | 0 | 0 | 14.2891 | 0 | 14400 | 0 | 757008 | 286.1947 | 0
8333 | 12 | 0 | 0 | 0.27686 | 11.3237 | 0 | 0 | 0 | 0 | 11.3237 | 0 | 14400 | 0 | 757008 | 296.01 | 0
8334 | 12 | 0 | 0 | 0.30465 | 12.4602 | 0 | 0 | 0 | 0 | 12.4602 | 0 | 14400 | 0 | 757008 | 306.8106 | 0
8335 | 12 | 0 | 0 | 0.41764 | 17.0816 | 0 | 0 | 0 | 0 | 17.0816 | 0 | 14400 | 0 | 757008 | 321.6169 | 0
8336 | 12 | 1 | 0.04871 | 0.27582 | 25.3486 | 200 | 25.3486 | 174.6514 | 200 | 0 | 0 | 14200 | 200 | 757208 | 146.9655 | 0
8337 | 12 | 1 | 0.3416 | 0.30334 | 111.0611 | 200 | 111.0611 | 88.9389 | 200 | 0 | 0 | 14000 | 200 | 757408 | 58.0265 | 0
8338 | 12 | 0 | 0.68624 | 0.31456 | 211.0521 | 0 | 0 | 0 | 0 | 180 | 0 | 14000 | 0 | 757408 | 214.0505 | 31.0521
8339 | 12 | 0 | 0.99454 | 0.26554 | 298.083 | 0 | 0 | 0 | 0 | 180 | 0 | 14000 | 0 | 757408 | 370.0745 | 118.083
8340 | 12 | 0 | 1 | 0.27645 | 300.1066 | 0 | 0 | 0 | 0 | 162.3621 | 0 | 14000 | 0 | 757408 | 510.81 | 137.7445
8341 | 12 | 0 | 1 | 0.17665 | 296.0248 | 0 | 0 | 0 | 0 | 0 | 0 | 14000 | 0 | 757408 | 510.81 | 296.0248
8342 | 12 | 0 | 1 | 0.1508 | 294.9675 | 0 | 0 | 0 | 0 | 0 | 0 | 14000 | 0 | 757408 | 510.81 | 294.9675
8343 | 12 | 0 | 0.99454 | 0.1506 | 293.3817 | 0 | 0 | 0 | 0 | 0 | 0 | 14000 | 0 | 757408 | 510.81 | 293.3817
8344 | 12 | 0 | 0.68624 | 0.15271 | 204.4322 | 0 | 0 | 0 | 0 | 0 | 0 | 14000 | 0 | 757408 | 510.81 | 204.4322
8345 | 12 | 0 | 0.3416 | 0.22017 | 107.6598 | 0 | 0 | 0 | 0 | 0 | 0 | 14000 | 0 | 757408 | 510.81 | 107.6598
8346 | 12 | 0 | 0.04871 | 0.30385 | 26.4947 | 0 | 0 | 0 | 0 | 0 | 0 | 14000 | 0 | 757408 | 510.81 | 26.4947
8347 | 12 | 0 | 0 | 0.38056 | 15.5647 | 0 | 0 | 0 | 0 | 0 | 0 | 14000 | 0 | 757408 | 510.81 | 15.5647
8348 | 12 | 1 | 0 | 0.42245 | 17.278 | 200 | 17.278 | 180 | 197.278 | 0 | 0 | 13800 | 197.278 | 757605.278 | 330.81 | 0
8349 | 12 | 1 | 0 | 0.47537 | 19.4427 | 200 | 19.4427 | 180 | 199.4427 | 0 | 0 | 13600 | 199.4427 | 757804.7208 | 150.81 | 0
8350 | 12 | 0 | 0 | 0.42181 | 17.2519 | 0 | 0 | 0 | 0 | 17.2519 | 0 | 13600 | 0 | 757804.7208 | 165.7639 | 0
8351 | 12 | 0 | 0 | 0.43644 | 17.8505 | 0 | 0 | 0 | 0 | 17.8505 | 0 | 13600 | 0 | 757804.7208 | 181.2367 | 0
8352 | 12 | 0 | 0 | 0.26958 | 11.0258 | 0 | 0 | 0 | 0 | 11.0258 | 0 | 13600 | 0 | 757804.7208 | 190.7939 | 0
8353 | 12 | 0 | 0 | 0.4782 | 19.5583 | 0 | 0 | 0 | 0 | 19.5583 | 0 | 13600 | 0 | 757804.7208 | 207.747 | 0
8354 | 12 | 0 | 0 | 0.27291 | 11.1619 | 0 | 0 | 0 | 0 | 11.1619 | 0 | 13600 | 0 | 757804.7208 | 217.4221 | 0
8355 | 12 | 0 | 0 | 0.34728 | 14.2039 | 0 | 0 | 0 | 0 | 14.2039 | 0 | 13600 | 0 | 757804.7208 | 229.7341 | 0
8356 | 12 | 0 | 0 | 0.38258 | 15.6477 | 0 | 0 | 0 | 0 | 15.6477 | 0 | 13600 | 0 | 757804.7208 | 243.2975 | 0
8357 | 12 | 0 | 0 | 0.29423 | 12.034 | 0 | 0 | 0 | 0 | 12.034 | 0 | 13600 | 0 | 757804.7208 | 253.7286 | 0
8358 | 12 | 0 | 0 | 0.2766 | 11.3131 | 0 | 0 | 0 | 0 | 11.3131 | 0 | 13600 | 0 | 757804.7208 | 263.5348 | 0
8359 | 12 | 0 | 0 | 0.34945 | 14.2926 | 0 | 0 | 0 | 0 | 14.2926 | 0 | 13600 | 0 | 757804.7208 | 275.9236 | 0
8360 | 12 | 1 | 0.035954 | 0.33494 | 24.0827 | 200 | 24.0827 | 175.9173 | 200 | 0 | 0 | 13400 | 200 | 758004.7208 | 100.0063 | 0
8361 | 12 | 1 | 0.25215 | 0.3126 | 85.606 | 200 | 85.606 | 100.0063 | 185.6123 | 0 | 0 | 13200 | 185.6123 | 758190.333 | 0 | 0
8362 | 12 | 0 | 0.50654 | 0.28313 | 157.8687 | 0 | 0 | 0 | 0 | 157.8687 | 0 | 13200 | 0 | 758190.333 | 136.8406 | 0
8363 | 12 | 0 | 0.73411 | 0.2377 | 221.7313 | 0 | 0 | 0 | 0 | 180 | 17.667 | 13200 | 17.667 | 758208 | 292.8646 | 24.0643
8364 | 12 | 0 | 0.88979 | 0.2703 | 268.0258 | 0 | 0 | 0 | 0 | 180 | 0 | 13200 | 0 | 758208 | 448.8886 | 88.0258
8365 | 12 | 0 | 0.94498 | 0.17066 | 279.8901 | 0 | 0 | 0 | 0 | 71.4368 | 0 | 13200 | 0 | 758208 | 510.81 | 208.4533
8366 | 12 | 0 | 0.88979 | 0.12461 | 262.0674 | 0 | 0 | 0 | 0 | 0 | 0 | 13200 | 0 | 758208 | 510.81 | 262.0674
8367 | 12 | 0 | 0.73411 | 0.13573 | 217.5611 | 0 | 0 | 0 | 0 | 0 | 0 | 13200 | 0 | 758208 | 510.81 | 217.5611
8368 | 12 | 0 | 0.50654 | 0.1208 | 151.2294 | 0 | 0 | 0 | 0 | 0 | 0 | 13200 | 0 | 758208 | 510.81 | 151.2294
8369 | 12 | 0 | 0.25215 | 0.13318 | 78.2679 | 0 | 0 | 0 | 0 | 0 | 0 | 13200 | 0 | 758208 | 510.81 | 78.2679
8370 | 12 | 0 | 0.035954 | 0.12188 | 15.3686 | 0 | 0 | 0 | 0 | 0 | 0 | 13200 | 0 | 758208 | 510.81 | 15.3686
8371 | 12 | 0 | 0 | 0.12355 | 5.0533 | 0 | 0 | 0 | 0 | 0 | 0 | 13200 | 0 | 758208 | 510.81 | 5.0533
8372 | 12 | 1 | 0 | 0.17989 | 7.3575 | 200 | 7.3575 | 180 | 187.3575 | 0 | 0 | 13000 | 187.3575 | 758395.3575 | 330.81 | 0
8373 | 12 | 1 | 0 | 0.18206 | 7.4463 | 200 | 7.4463 | 180 | 187.4463 | 0 | 0 | 12800 | 187.4463 | 758582.8038 | 150.81 | 0
8374 | 12 | 0 | 0 | 0.16115 | 6.591 | 0 | 0 | 0 | 0 | 6.591 | 0 | 12800 | 0 | 758582.8038 | 156.5231 | 0
8375 | 12 | 0 | 0 | 0.18587 | 7.602 | 0 | 0 | 0 | 0 | 7.602 | 0 | 12800 | 0 | 758582.8038 | 163.1125 | 0
8376 | 12 | 0 | 0 | 0.35585 | 14.5542 | 0 | 0 | 0 | 0 | 14.5542 | 0 | 12800 | 0 | 758582.8038 | 175.7281 | 0
8377 | 12 | 0 | 0 | 0.32906 | 13.4584 | 0 | 0 | 0 | 0 | 13.4584 | 0 | 12800 | 0 | 758582.8038 | 187.3938 | 0
8378 | 12 | 0 | 0 | 0.44323 | 18.128 | 0 | 0 | 0 | 0 | 18.128 | 0 | 12800 | 0 | 758582.8038 | 203.1072 | 0
8379 | 12 | 0 | 0 | 0.51898 | 21.2264 | 0 | 0 | 0 | 0 | 21.2264 | 0 | 12800 | 0 | 758582.8038 | 221.5063 | 0
8380 | 12 | 0 | 0 | 0.32062 | 13.1133 | 0 | 0 | 0 | 0 | 13.1133 | 0 | 12800 | 0 | 758582.8038 | 232.8729 | 0
8381 | 12 | 0 | 0 | 0.37084 | 15.1672 | 0 | 0 | 0 | 0 | 15.1672 | 0 | 12800 | 0 | 758582.8038 | 246.0199 | 0
8382 | 12 | 0 | 0 | 0.38383 | 15.6984 | 0 | 0 | 0 | 0 | 15.6984 | 0 | 12800 | 0 | 758582.8038 | 259.6273 | 0
8383 | 12 | 0 | 0 | 0.46538 | 19.0341 | 0 | 0 | 0 | 0 | 19.0341 | 0 | 12800 | 0 | 758582.8038 | 276.126 | 0
8384 | 12 | 1 | 0.050678 | 0.49771 | 34.9923 | 200 | 34.9923 | 165.0077 | 200 | 0 | 0 | 12600 | 200 | 758782.8038 | 111.1183 | 0
8385 | 12 | 1 | 0.35541 | 0.49104 | 122.7247 | 200 | 122.7247 | 77.2753 | 200 | 0 | 0 | 12400 | 200 | 758982.8038 | 33.843 | 0
8386 | 12 | 0 | 0.71397 | 0.38274 | 221.8492 | 0 | 0 | 0 | 0 | 180 | 25.1962 | 12400 | 25.1962 | 759008 | 189.867 | 16.653
8387 | 12 | 0 | 1 | 0.46584 | 307.8527 | 0 | 0 | 0 | 0 | 180 | 0 | 12400 | 0 | 759008 | 345.891 | 127.8527
8388 | 12 | 0 | 1 | 0.44065 | 306.8227 | 0 | 0 | 0 | 0 | 180 | 0 | 12400 | 0 | 759008 | 501.915 | 126.8227
8389 | 12 | 0 | 1 | 0.54676 | 311.1624 | 0 | 0 | 0 | 0 | 10.2619 | 0 | 12400 | 0 | 759008 | 510.81 | 300.9005
8390 | 12 | 0 | 1 | 0.61266 | 313.8579 | 0 | 0 | 0 | 0 | 0 | 0 | 12400 | 0 | 759008 | 510.81 | 313.8579
8391 | 12 | 0 | 1 | 0.64682 | 315.2549 | 0 | 0 | 0 | 0 | 0 | 0 | 12400 | 0 | 759008 | 510.81 | 315.2549
8392 | 12 | 0 | 0.71397 | 0.57652 | 229.7749 | 0 | 0 | 0 | 0 | 0 | 0 | 12400 | 0 | 759008 | 510.81 | 229.7749
8393 | 12 | 0 | 0.35541 | 0.3267 | 116.0033 | 0 | 0 | 0 | 0 | 0 | 0 | 12400 | 0 | 759008 | 510.81 | 116.0033
8394 | 12 | 0 | 0.050678 | 0.30601 | 27.1518 | 0 | 0 | 0 | 0 | 0 | 0 | 12400 | 0 | 759008 | 510.81 | 27.1518
8395 | 12 | 0 | 0 | 0.28684 | 11.7319 | 0 | 0 | 0 | 0 | 0 | 0 | 12400 | 0 | 759008 | 510.81 | 11.7319
8396 | 12 | 1 | 0 | 0.41072 | 16.7984 | 200 | 16.7984 | 180 | 196.7984 | 0 | 0 | 12200 | 196.7984 | 759204.7984 | 330.81 | 0
8397 | 12 | 1 | 0 | 0.51972 | 21.2566 | 200 | 21.2566 | 178.7434 | 200 | 0 | 0 | 12000 | 200 | 759404.7984 | 152.0666 | 0
8398 | 12 | 0 | 0 | 0.35861 | 14.6671 | 0 | 0 | 0 | 0 | 14.6671 | 0 | 12000 | 0 | 759404.7984 | 164.7801 | 0
8399 | 12 | 0 | 0 | 0.43261 | 17.6938 | 0 | 0 | 0 | 0 | 17.6938 | 0 | 12000 | 0 | 759404.7984 | 180.1171 | 0
8400 | 12 | 0 | 0 | 0.45038 | 18.4207 | 0 | 0 | 0 | 0 | 18.4207 | 0 | 12000 | 0 | 759404.7984 | 196.0841 | 0
8401 | 12 | 0 | 0 | 0.6182 | 25.2843 | 0 | 0 | 0 | 0 | 25.2843 | 0 | 12000 | 0 | 759404.7984 | 218.0005 | 0
8402 | 12 | 0 | 0 | 0.3841 | 15.7096 | 0 | 0 | 0 | 0 | 15.7096 | 0 | 12000 | 0 | 759404.7984 | 231.6176 | 0
8403 | 12 | 0 | 0 | 0.38717 | 15.8352 | 0 | 0 | 0 | 0 | 15.8352 | 0 | 12000 | 0 | 759404.7984 | 245.3436 | 0
8404 | 12 | 0 | 0 | 0.56245 | 23.0042 | 0 | 0 | 0 | 0 | 23.0042 | 0 | 12000 | 0 | 759404.7984 | 265.2836 | 0
8405 | 12 | 0 | 0 | 0.7583 | 31.0145 | 0 | 0 | 0 | 0 | 31.0145 | 0 | 12000 | 0 | 759404.7984 | 292.167 | 0
8406 | 12 | 0 | 0 | 0.74627 | 30.5226 | 0 | 0 | 0 | 0 | 30.5226 | 0 | 12000 | 0 | 759404.7984 | 318.624 | 0
8407 | 12 | 0 | 0 | 0.68721 | 28.1068 | 0 | 0 | 0 | 0 | 28.1068 | 0 | 12000 | 0 | 759404.7984 | 342.987 | 0
8408 | 12 | 1 | 0.048306 | 0.58671 | 37.9474 | 200 | 37.9474 | 162.0526 | 200 | 0 | 0 | 11800 | 200 | 759604.7984 | 180.9343 | 0
8409 | 12 | 1 | 0.33877 | 0.9486 | 136.6348 | 200 | 136.6348 | 63.3652 | 200 | 0 | 0 | 11600 | 200 | 759804.7984 | 117.5691 | 0
8410 | 12 | 0 | 0.68056 | 0.69359 | 224.912 | 0 | 0 | 0 | 0 | 180 | 3.2016 | 11600 | 3.2016 | 759808 | 273.5931 | 41.7104
8411 | 12 | 0 | 0.9863 | 0.8041 | 317.7299 | 0 | 0 | 0 | 0 | 180 | 0 | 11600 | 0 | 759808 | 429.6171 | 137.7299
8412 | 12 | 0 | 1 | 0.8645 | 324.1582 | 0 | 0 | 0 | 0 | 93.6697 | 0 | 11600 | 0 | 759808 | 510.81 | 230.4885
8413 | 12 | 0 | 1 | 0.86191 | 324.052 | 0 | 0 | 0 | 0 | 0 | 0 | 11600 | 0 | 759808 | 510.81 | 324.052
8414 | 12 | 0 | 1 | 1 | 329.7 | 0 | 0 | 0 | 0 | 0 | 0 | 11600 | 0 | 759808 | 510.81 | 329.7
8415 | 12 | 0 | 0.9863 | 0.85506 | 319.8142 | 0 | 0 | 0 | 0 | 0 | 0 | 11600 | 0 | 759808 | 510.81 | 319.8142
8416 | 12 | 0 | 0.68056 | 0.84236 | 230.997 | 0 | 0 | 0 | 0 | 0 | 0 | 11600 | 0 | 759808 | 510.81 | 230.997
8417 | 12 | 0 | 0.33877 | 0.94192 | 136.3617 | 0 | 0 | 0 | 0 | 0 | 0 | 11600 | 0 | 759808 | 510.81 | 136.3617
8418 | 12 | 0 | 0.048306 | 0.72948 | 43.7867 | 0 | 0 | 0 | 0 | 0 | 0 | 11600 | 0 | 759808 | 510.81 | 43.7867
8419 | 12 | 0 | 0 | 0.70486 | 28.8286 | 0 | 0 | 0 | 0 | 0 | 0 | 11600 | 0 | 759808 | 510.81 | 28.8286
8420 | 12 | 1 | 0 | 0.95558 | 39.0833 | 200 | 39.0833 | 160.9167 | 200 | 0 | 0 | 11400 | 200 | 760008 | 349.8933 | 0
8421 | 12 | 1 | 0 | 1 | 40.9 | 200 | 40.9 | 159.1 | 200 | 0 | 0 | 11200 | 200 | 760208 | 190.7933 | 0
8422 | 12 | 0 | 0 | 1 | 40.9 | 0 | 0 | 0 | 0 | 40.9 | 0 | 11200 | 0 | 760208 | 226.2454 | 0
8423 | 12 | 0 | 0 | 0.68462 | 28.0011 | 0 | 0 | 0 | 0 | 28.0011 | 0 | 11200 | 0 | 760208 | 250.5168 | 0
8424 | 12 | 0 | 0 | 0.8819 | 36.0698 | 0 | 0 | 0 | 0 | 36.0698 | 0 | 11200 | 0 | 760208 | 281.782 | 0
8425 | 12 | 0 | 0 | 0.65883 | 26.946 | 0 | 0 | 0 | 0 | 26.946 | 0 | 11200 | 0 | 760208 | 305.1388 | 0
8426 | 12 | 0 | 0 | 0.61424 | 25.1223 | 0 | 0 | 0 | 0 | 25.1223 | 0 | 11200 | 0 | 760208 | 326.9148 | 0
8427 | 12 | 0 | 0 | 0.29859 | 12.2125 | 0 | 0 | 0 | 0 | 12.2125 | 0 | 11200 | 0 | 760208 | 337.5006 | 0
8428 | 12 | 0 | 0 | 0.5572 | 22.7894 | 0 | 0 | 0 | 0 | 22.7894 | 0 | 11200 | 0 | 760208 | 357.2544 | 0
8429 | 12 | 0 | 0 | 0.53127 | 21.7289 | 0 | 0 | 0 | 0 | 21.7289 | 0 | 11200 | 0 | 760208 | 376.0891 | 0
8430 | 12 | 0 | 0 | 0.22859 | 9.3492 | 0 | 0 | 0 | 0 | 9.3492 | 0 | 11200 | 0 | 760208 | 384.193 | 0
8431 | 12 | 0 | 0 | 0.25724 | 10.5211 | 0 | 0 | 0 | 0 | 10.5211 | 0 | 11200 | 0 | 760208 | 393.3127 | 0
8432 | 12 | 1 | 0.047079 | 0.35067 | 27.9389 | 200 | 27.9389 | 172.0611 | 200 | 0 | 0 | 11000 | 200 | 760408 | 221.2516 | 0
8433 | 12 | 1 | 0.33017 | 0.38844 | 111.2398 | 200 | 111.2398 | 88.7602 | 200 | 0 | 0 | 10800 | 200 | 760608 | 132.4913 | 0
8434 | 12 | 0 | 0.66327 | 0.25157 | 201.8421 | 0 | 0 | 0 | 0 | 180 | 0 | 10800 | 0 | 760608 | 288.5153 | 21.8421
8435 | 12 | 0 | 0.96125 | 0.22179 | 286.6794 | 0 | 0 | 0 | 0 | 180 | 0 | 10800 | 0 | 760608 | 444.5393 | 106.6794
8436 | 12 | 0 | 1 | 0.21743 | 297.6929 | 0 | 0 | 0 | 0 | 76.4544 | 0 | 10800 | 0 | 760608 | 510.81 | 221.2385
8437 | 12 | 0 | 1 | 0.22224 | 297.8898 | 0 | 0 | 0 | 0 | 0 | 0 | 10800 | 0 | 760608 | 510.81 | 297.8898
8438 | 12 | 0 | 1 | 0.23962 | 298.6003 | 0 | 0 | 0 | 0 | 0 | 0 | 10800 | 0 | 760608 | 510.81 | 298.6003
8439 | 12 | 0 | 0.96125 | 0.2255 | 286.8312 | 0 | 0 | 0 | 0 | 0 | 0 | 10800 | 0 | 760608 | 510.81 | 286.8312
8440 | 12 | 0 | 0.66327 | 0.26996 | 202.5944 | 0 | 0 | 0 | 0 | 0 | 0 | 10800 | 0 | 760608 | 510.81 | 202.5944
8441 | 12 | 0 | 0.33017 | 0.29217 | 107.3024 | 0 | 0 | 0 | 0 | 0 | 0 | 10800 | 0 | 760608 | 510.81 | 107.3024
8442 | 12 | 0 | 0.047079 | 0.34341 | 27.642 | 0 | 0 | 0 | 0 | 0 | 0 | 10800 | 0 | 760608 | 510.81 | 27.642
8443 | 12 | 0 | 0 | 0.32438 | 13.267 | 0 | 0 | 0 | 0 | 0 | 0 | 10800 | 0 | 760608 | 510.81 | 13.267
8444 | 12 | 1 | 0 | 0.49476 | 20.2358 | 200 | 20.2358 | 179.7642 | 200 | 0 | 0 | 10600 | 200 | 760808 | 331.0458 | 0
8445 | 12 | 1 | 0 | 0.71731 | 29.338 | 200 | 29.338 | 170.662 | 200 | 0 | 0 | 10400 | 200 | 761008 | 160.3837 | 0
8446 | 12 | 0 | 0 | 0.77326 | 31.6263 | 0 | 0 | 0 | 0 | 31.6263 | 0 | 10400 | 0 | 761008 | 187.7974 | 0
8447 | 12 | 0 | 0 | 0.93383 | 38.1936 | 0 | 0 | 0 | 0 | 38.1936 | 0 | 10400 | 0 | 761008 | 220.9036 | 0
8448 | 12 | 0 | 0 | 0.61146 | 25.0088 | 0 | 0 | 0 | 0 | 25.0088 | 0 | 10400 | 0 | 761008 | 242.5812 | 0
8449 | 12 | 0 | 0 | 0.80353 | 32.8645 | 0 | 0 | 0 | 0 | 32.8645 | 0 | 10400 | 0 | 761008 | 271.0682 | 0
8450 | 12 | 0 | 0 | 0.72158 | 29.5127 | 0 | 0 | 0 | 0 | 29.5127 | 0 | 10400 | 0 | 761008 | 296.6498 | 0
8451 | 12 | 0 | 0 | 0.45314 | 18.5334 | 0 | 0 | 0 | 0 | 18.5334 | 0 | 10400 | 0 | 761008 | 312.7145 | 0
8452 | 12 | 0 | 0 | 0.57394 | 23.4743 | 0 | 0 | 0 | 0 | 23.4743 | 0 | 10400 | 0 | 761008 | 333.0621 | 0
8453 | 12 | 0 | 0 | 0.41225 | 16.8611 | 0 | 0 | 0 | 0 | 16.8611 | 0 | 10400 | 0 | 761008 | 347.6772 | 0
8454 | 12 | 0 | 0 | 0.49851 | 20.3891 | 0 | 0 | 0 | 0 | 20.3891 | 0 | 10400 | 0 | 761008 | 365.3505 | 0
8455 | 12 | 0 | 0 | 0.5175 | 21.1655 | 0 | 0 | 0 | 0 | 21.1655 | 0 | 10400 | 0 | 761008 | 383.6968 | 0
8456 | 12 | 1 | 0.04072 | 0.48864 | 31.7453 | 200 | 31.7453 | 168.2547 | 200 | 0 | 0 | 10200 | 200 | 761208 | 215.4421 | 0
8457 | 12 | 1 | 0.28557 | 0.62917 | 108.2058 | 200 | 108.2058 | 91.7942 | 200 | 0 | 0 | 10000 | 200 | 761408 | 123.6479 | 0
8458 | 12 | 0 | 0.57368 | 0.49966 | 186.1154 | 0 | 0 | 0 | 0 | 180 | 0 | 10000 | 0 | 761408 | 279.6719 | 6.1154
8459 | 12 | 0 | 0.83141 | 0.37782 | 255.5641 | 0 | 0 | 0 | 0 | 180 | 0 | 10000 | 0 | 761408 | 435.6959 | 75.5641
8460 | 12 | 0 | 1 | 0.29809 | 300.9919 | 0 | 0 | 0 | 0 | 86.6567 | 0 | 10000 | 0 | 761408 | 510.81 | 214.3352
8461 | 12 | 0 | 1 | 0.306 | 301.3153 | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 0 | 761408 | 510.81 | 301.3153
8462 | 12 | 0 | 1 | 0.31799 | 301.8057 | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 0 | 761408 | 510.81 | 301.8057
8463 | 12 | 0 | 0.83141 | 0.19975 | 248.2808 | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 0 | 761408 | 510.81 | 248.2808
8464 | 12 | 0 | 0.57368 | 0.24738 | 175.7974 | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 0 | 761408 | 510.81 | 175.7974
8465 | 12 | 0 | 0.28557 | 0.3007 | 94.7717 | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 0 | 761408 | 510.81 | 94.7717
8466 | 12 | 0 | 0.04072 | 0.31901 | 24.8074 | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 0 | 761408 | 510.81 | 24.8074
8467 | 12 | 0 | 0 | 0.41926 | 17.1476 | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 0 | 761408 | 510.81 | 17.1476
8468 | 12 | 1 | 0 | 0.34808 | 14.2367 | 200 | 14.2367 | 180 | 194.2367 | 0 | 0 | 9800 | 194.2367 | 761602.2367 | 330.81 | 0
8469 | 12 | 1 | 0 | 0.16925 | 6.9225 | 200 | 6.9225 | 180 | 186.9225 | 0 | 0 | 9600 | 186.9225 | 761789.1592 | 150.81 | 0
8470 | 12 | 0 | 0 | 0.14568 | 5.9581 | 0 | 0 | 0 | 0 | 5.9581 | 0 | 9600 | 0 | 761789.1592 | 155.9745 | 0
8471 | 12 | 0 | 0 | 0.16419 | 6.7155 | 0 | 0 | 0 | 0 | 6.7155 | 0 | 9600 | 0 | 761789.1592 | 161.7955 | 0
8472 | 12 | 0 | 0 | 0.15491 | 6.3359 | 0 | 0 | 0 | 0 | 6.3359 | 0 | 9600 | 0 | 761789.1592 | 167.2875 | 0
8473 | 12 | 0 | 0 | 0.183 | 7.4845 | 0 | 0 | 0 | 0 | 7.4845 | 0 | 9600 | 0 | 761789.1592 | 173.7751 | 0
8474 | 12 | 0 | 0 | 0.22849 | 9.3451 | 0 | 0 | 0 | 0 | 9.3451 | 0 | 9600 | 0 | 761789.1592 | 181.8755 | 0
8475 | 12 | 0 | 0 | 0.21172 | 8.6593 | 0 | 0 | 0 | 0 | 8.6593 | 0 | 9600 | 0 | 761789.1592 | 189.3814 | 0
8476 | 12 | 0 | 0 | 0.18586 | 7.6016 | 0 | 0 | 0 | 0 | 7.6016 | 0 | 9600 | 0 | 761789.1592 | 195.9705 | 0
8477 | 12 | 0 | 0 | 0.24449 | 9.9995 | 0 | 0 | 0 | 0 | 9.9995 | 0 | 9600 | 0 | 761789.1592 | 204.6381 | 0
8478 | 12 | 0 | 0 | 0.38452 | 15.727 | 0 | 0 | 0 | 0 | 15.727 | 0 | 9600 | 0 | 761789.1592 | 218.2702 | 0
8479 | 12 | 0 | 0 | 0.45467 | 18.5959 | 0 | 0 | 0 | 0 | 18.5959 | 0 | 9600 | 0 | 761789.1592 | 234.3891 | 0
8480 | 12 | 1 | 0.057668 | 0.40034 | 33.0283 | 200 | 33.0283 | 166.9717 | 200 | 0 | 0 | 9400 | 200 | 761989.1592 | 67.4175 | 0
8481 | 12 | 1 | 0.40443 | 0.36922 | 131.9003 | 200 | 131.9003 | 67.4175 | 199.3178 | 0 | 0 | 9200 | 199.3178 | 762188.4769 | 0 | 0
8482 | 12 | 0 | 0.81246 | 0.34794 | 248.8676 | 0 | 0 | 0 | 0 | 180 | 19.5231 | 9200 | 19.5231 | 762208 | 156.024 | 49.3446
8483 | 12 | 0 | 1 | 0.4272 | 306.2725 | 0 | 0 | 0 | 0 | 180 | 0 | 9200 | 0 | 762208 | 312.048 | 126.2725
8484 | 12 | 0 | 1 | 0.4453 | 307.0126 | 0 | 0 | 0 | 0 | 180 | 0 | 9200 | 0 | 762208 | 468.072 | 127.0126
8485 | 12 | 0 | 1 | 0.31848 | 301.8259 | 0 | 0 | 0 | 0 | 49.3055 | 0 | 9200 | 0 | 762208 | 510.81 | 252.5204
8486 | 12 | 0 | 1 | 0.38539 | 304.5626 | 0 | 0 | 0 | 0 | 0 | 0 | 9200 | 0 | 762208 | 510.81 | 304.5626
8487 | 12 | 0 | 1 | 0.34553 | 302.9324 | 0 | 0 | 0 | 0 | 0 | 0 | 9200 | 0 | 762208 | 510.81 | 302.9324
8488 | 12 | 0 | 0.81246 | 0.34372 | 248.6951 | 0 | 0 | 0 | 0 | 0 | 0 | 9200 | 0 | 762208 | 510.81 | 248.6951
8489 | 12 | 0 | 0.40443 | 0.28979 | 128.6516 | 0 | 0 | 0 | 0 | 0 | 0 | 9200 | 0 | 762208 | 510.81 | 128.6516
8490 | 12 | 0 | 0.057668 | 0.33632 | 30.4099 | 0 | 0 | 0 | 0 | 0 | 0 | 9200 | 0 | 762208 | 510.81 | 30.4099
8491 | 12 | 0 | 0 | 0.24726 | 10.1129 | 0 | 0 | 0 | 0 | 0 | 0 | 9200 | 0 | 762208 | 510.81 | 10.1129
8492 | 12 | 1 | 0 | 0.25164 | 10.2921 | 200 | 10.2921 | 180 | 190.2921 | 0 | 0 | 9000 | 190.2921 | 762398.2921 | 330.81 | 0
8493 | 12 | 1 | 0 | 0.19244 | 7.8708 | 200 | 7.8708 | 180 | 187.8708 | 0 | 0 | 8800 | 187.8708 | 762586.1629 | 150.81 | 0
8494 | 12 | 0 | 0 | 0.21525 | 8.8038 | 0 | 0 | 0 | 0 | 8.8038 | 0 | 8800 | 0 | 762586.1629 | 158.4412 | 0
8495 | 12 | 0 | 0 | 0.21427 | 8.7637 | 0 | 0 | 0 | 0 | 8.7637 | 0 | 8800 | 0 | 762586.1629 | 166.0376 | 0
8496 | 12 | 0 | 0 | 0.20926 | 8.5589 | 0 | 0 | 0 | 0 | 8.5589 | 0 | 8800 | 0 | 762586.1629 | 173.4564 | 0
8497 | 12 | 0 | 0 | 0.21857 | 8.9396 | 0 | 0 | 0 | 0 | 8.9396 | 0 | 8800 | 0 | 762586.1629 | 181.2053 | 0
8498 | 12 | 0 | 0 | 0.1824 | 7.46 | 0 | 0 | 0 | 0 | 7.46 | 0 | 8800 | 0 | 762586.1629 | 187.6716 | 0
8499 | 12 | 0 | 0 | 0.078375 | 3.2055 | 0 | 0 | 0 | 0 | 3.2055 | 0 | 8800 | 0 | 762586.1629 | 190.4502 | 0
8500 | 12 | 0 | 0 | 0.066924 | 2.7372 | 0 | 0 | 0 | 0 | 2.7372 | 0 | 8800 | 0 | 762586.1629 | 192.8228 | 0
8501 | 12 | 0 | 0 | 0.12698 | 5.1936 | 0 | 0 | 0 | 0 | 5.1936 | 0 | 8800 | 0 | 762586.1629 | 197.3246 | 0
8502 | 12 | 0 | 0 | 0.091422 | 3.7392 | 0 | 0 | 0 | 0 | 3.7392 | 0 | 8800 | 0 | 762586.1629 | 200.5657 | 0
8503 | 12 | 0 | 0 | 0.067932 | 2.7784 | 0 | 0 | 0 | 0 | 2.7784 | 0 | 8800 | 0 | 762586.1629 | 202.9741 | 0
8504 | 12 | 1 | 0.046812 | 0.12818 | 18.7618 | 200 | 18.7618 | 180 | 198.7618 | 0 | 0 | 8600 | 198.7618 | 762784.9247 | 22.9741 | 0
8505 | 12 | 1 | 0.32829 | 0.1343 | 100.3027 | 200 | 100.3027 | 22.9741 | 123.2768 | 0 | 0 | 8400 | 123.2768 | 762908.2015 | 0 | 0
8506 | 12 | 0 | 0.6595 | 0.1432 | 196.3199 | 0 | 0 | 0 | 0 | 180 | 16.3199 | 8400 | 16.3199 | 762924.5214 | 156.024 | 0
8507 | 12 | 0 | 0.95578 | 0.16142 | 282.6311 | 0 | 0 | 0 | 0 | 180 | 83.4786 | 8400 | 83.4786 | 763008 | 312.048 | 19.1525
8508 | 12 | 0 | 1 | 0.24778 | 298.9341 | 0 | 0 | 0 | 0 | 180 | 0 | 8400 | 0 | 763008 | 468.072 | 118.9341
8509 | 12 | 0 | 1 | 0.18262 | 296.2691 | 0 | 0 | 0 | 0 | 49.3055 | 0 | 8400 | 0 | 763008 | 510.81 | 246.9636
8510 | 12 | 0 | 1 | 0.30285 | 301.1865 | 0 | 0 | 0 | 0 | 0 | 0 | 8400 | 0 | 763008 | 510.81 | 301.1865
8511 | 12 | 0 | 0.95578 | 0.31099 | 288.7485 | 0 | 0 | 0 | 0 | 0 | 0 | 8400 | 0 | 763008 | 510.81 | 288.7485
8512 | 12 | 0 | 0.6595 | 0.32765 | 203.8639 | 0 | 0 | 0 | 0 | 0 | 0 | 8400 | 0 | 763008 | 510.81 | 203.8639
8513 | 12 | 0 | 0.32829 | 0.22529 | 104.0241 | 0 | 0 | 0 | 0 | 0 | 0 | 8400 | 0 | 763008 | 510.81 | 104.0241
8514 | 12 | 0 | 0.046812 | 0.18465 | 21.0716 | 0 | 0 | 0 | 0 | 0 | 0 | 8400 | 0 | 763008 | 510.81 | 21.0716
8515 | 12 | 0 | 0 | 0.1731 | 7.08 | 0 | 0 | 0 | 0 | 0 | 0 | 8400 | 0 | 763008 | 510.81 | 7.08
8516 | 12 | 1 | 0 | 0.24108 | 9.8602 | 200 | 9.8602 | 180 | 189.8602 | 0 | 0 | 8200 | 189.8602 | 763197.8602 | 330.81 | 0
8517 | 12 | 1 | 0 | 0.21609 | 8.838 | 200 | 8.838 | 180 | 188.838 | 0 | 0 | 8000 | 188.838 | 763386.6982 | 150.81 | 0
8518 | 12 | 0 | 0 | 0.16078 | 6.576 | 0 | 0 | 0 | 0 | 6.576 | 0 | 8000 | 0 | 763386.6982 | 156.5101 | 0
8519 | 12 | 0 | 0 | 0.14054 | 5.748 | 0 | 0 | 0 | 0 | 5.748 | 0 | 8000 | 0 | 763386.6982 | 161.4924 | 0
8520 | 12 | 0 | 0 | 0.12649 | 5.1734 | 0 | 0 | 0 | 0 | 5.1734 | 0 | 8000 | 0 | 763386.6982 | 165.9767 | 0
8521 | 12 | 0 | 0 | 0.16467 | 6.7348 | 0 | 0 | 0 | 0 | 6.7348 | 0 | 8000 | 0 | 763386.6982 | 171.8145 | 0
8522 | 12 | 0 | 0 | 0.1312 | 5.366 | 0 | 0 | 0 | 0 | 5.366 | 0 | 8000 | 0 | 763386.6982 | 176.4657 | 0
8523 | 12 | 0 | 0 | 0.11621 | 4.7529 | 0 | 0 | 0 | 0 | 4.7529 | 0 | 8000 | 0 | 763386.6982 | 180.5855 | 0
8524 | 12 | 0 | 0 | 0.19475 | 7.9651 | 0 | 0 | 0 | 0 | 7.9651 | 0 | 8000 | 0 | 763386.6982 | 187.4897 | 0
8525 | 12 | 0 | 0 | 0.1459 | 5.9673 | 0 | 0 | 0 | 0 | 5.9673 | 0 | 8000 | 0 | 763386.6982 | 192.6621 | 0
8526 | 12 | 0 | 0 | 0.1816 | 7.4273 | 0 | 0 | 0 | 0 | 7.4273 | 0 | 8000 | 0 | 763386.6982 | 199.1001 | 0
8527 | 12 | 0 | 0 | 0.15878 | 6.494 | 0 | 0 | 0 | 0 | 6.494 | 0 | 8000 | 0 | 763386.6982 | 204.7291 | 0
8528 | 12 | 1 | 0.047949 | 0.26334 | 24.6183 | 200 | 24.6183 | 175.3817 | 200 | 0 | 0 | 7800 | 200 | 763586.6982 | 29.3474 | 0
8529 | 12 | 1 | 0.33626 | 0.24992 | 107.3344 | 200 | 107.3344 | 29.3474 | 136.6819 | 0 | 0 | 7600 | 136.6819 | 763723.3801 | 0 | 0
8530 | 12 | 0 | 0.67552 | 0.19502 | 203.0657 | 0 | 0 | 0 | 0 | 180 | 23.0657 | 7600 | 23.0657 | 763746.4458 | 156.024 | 0
8531 | 12 | 0 | 0.97899 | 0.17064 | 289.7126 | 0 | 0 | 0 | 0 | 180 | 61.5542 | 7600 | 61.5542 | 763808 | 312.048 | 48.1584
8532 | 12 | 0 | 1 | 0.36373 | 303.6764 | 0 | 0 | 0 | 0 | 180 | 0 | 7600 | 0 | 763808 | 468.072 | 123.6764
8533 | 12 | 0 | 1 | 0.39725 | 305.0477 | 0 | 0 | 0 | 0 | 49.3055 | 0 | 7600 | 0 | 763808 | 510.81 | 255.7422
8534 | 12 | 0 | 1 | 0.23947 | 298.5945 | 0 | 0 | 0 | 0 | 0 | 0 | 7600 | 0 | 763808 | 510.81 | 298.5945
8535 | 12 | 0 | 0.97899 | 0.23378 | 292.2951 | 0 | 0 | 0 | 0 | 0 | 0 | 7600 | 0 | 763808 | 510.81 | 292.2951
8536 | 12 | 0 | 0.67552 | 0.21718 | 203.9718 | 0 | 0 | 0 | 0 | 0 | 0 | 7600 | 0 | 763808 | 510.81 | 203.9718
8537 | 12 | 0 | 0.33626 | 0.20654 | 105.5603 | 0 | 0 | 0 | 0 | 0 | 0 | 7600 | 0 | 763808 | 510.81 | 105.5603
8538 | 12 | 0 | 0.047949 | 0.12955 | 19.1462 | 0 | 0 | 0 | 0 | 0 | 0 | 7600 | 0 | 763808 | 510.81 | 19.1462
8539 | 12 | 0 | 0 | 0.12008 | 4.9115 | 0 | 0 | 0 | 0 | 0 | 0 | 7600 | 0 | 763808 | 510.81 | 4.9115
8540 | 12 | 1 | 0 | 0.073291 | 2.9976 | 200 | 2.9976 | 180 | 182.9976 | 0 | 0 | 7400 | 182.9976 | 763990.9976 | 330.81 | 0
8541 | 12 | 1 | 0 | 0.083103 | 3.3989 | 200 | 3.3989 | 180 | 183.3989 | 0 | 0 | 7200 | 183.3989 | 764174.3965 | 150.81 | 0
8542 | 12 | 0 | 0 | 0.059217 | 2.422 | 0 | 0 | 0 | 0 | 2.422 | 0 | 7200 | 0 | 764174.3965 | 152.9094 | 0
8543 | 12 | 0 | 0 | 0.051552 | 2.1085 | 0 | 0 | 0 | 0 | 2.1085 | 0 | 7200 | 0 | 764174.3965 | 154.737 | 0
8544 | 12 | 0 | 0 | 0.046521 | 1.9027 | 0 | 0 | 0 | 0 | 1.9027 | 0 | 7200 | 0 | 764174.3965 | 156.3863 | 0
8545 | 12 | 0 | 0 | 0.038508 | 1.575 | 0 | 0 | 0 | 0 | 1.575 | 0 | 7200 | 0 | 764174.3965 | 157.7515 | 0
8546 | 12 | 0 | 0 | 0.034105 | 1.3949 | 0 | 0 | 0 | 0 | 1.3949 | 0 | 7200 | 0 | 764174.3965 | 158.9605 | 0
8547 | 12 | 0 | 0 | 0.048888 | 1.9995 | 0 | 0 | 0 | 0 | 1.9995 | 0 | 7200 | 0 | 764174.3965 | 160.6937 | 0
8548 | 12 | 0 | 0 | 0.04047 | 1.6552 | 0 | 0 | 0 | 0 | 1.6552 | 0 | 7200 | 0 | 764174.3965 | 162.1285 | 0
8549 | 12 | 0 | 0 | 0.042614 | 1.7429 | 0 | 0 | 0 | 0 | 1.7429 | 0 | 7200 | 0 | 764174.3965 | 163.6392 | 0
8550 | 12 | 0 | 0 | 0.050977 | 2.085 | 0 | 0 | 0 | 0 | 2.085 | 0 | 7200 | 0 | 764174.3965 | 165.4465 | 0
8551 | 12 | 0 | 0 | 0.067275 | 2.7515 | 0 | 0 | 0 | 0 | 2.7515 | 0 | 7200 | 0 | 764174.3965 | 167.8315 | 0
8552 | 12 | 1 | 0.047182 | 0.092138 | 17.3946 | 200 | 17.3946 | 167.8315 | 185.2261 | 0 | 0 | 7000 | 185.2261 | 764359.6226 | 0 | 0
8553 | 12 | 1 | 0.33089 | 0.14724 | 101.5836 | 200 | 101.5836 | 0 | 101.5836 | 0 | 0 | 6800 | 101.5836 | 764461.2062 | 0 | 0
8554 | 12 | 0 | 0.66473 | 0.14584 | 197.9373 | 0 | 0 | 0 | 0 | 180 | 17.9373 | 6800 | 17.9373 | 764479.1435 | 156.024 | 0
8555 | 12 | 0 | 0.96335 | 0.14588 | 284.183 | 0 | 0 | 0 | 0 | 180 | 104.183 | 6800 | 104.183 | 764583.3264 | 312.048 | 0
8556 | 12 | 0 | 1 | 0.1401 | 294.53 | 0 | 0 | 0 | 0 | 180 | 24.6736 | 6800 | 24.6736 | 764608 | 468.072 | 89.8564
8557 | 12 | 0 | 1 | 0.1725 | 295.8552 | 0 | 0 | 0 | 0 | 49.3055 | 0 | 6800 | 0 | 764608 | 510.81 | 246.5497
8558 | 12 | 0 | 1 | 0.20875 | 297.3381 | 0 | 0 | 0 | 0 | 0 | 0 | 6800 | 0 | 764608 | 510.81 | 297.3381
8559 | 12 | 0 | 0.96335 | 0.25559 | 288.6702 | 0 | 0 | 0 | 0 | 0 | 0 | 6800 | 0 | 764608 | 510.81 | 288.6702
8560 | 12 | 0 | 0.66473 | 0.24551 | 202.014 | 0 | 0 | 0 | 0 | 0 | 0 | 6800 | 0 | 764608 | 510.81 | 202.014
8561 | 12 | 0 | 0.33089 | 0.20984 | 104.1437 | 0 | 0 | 0 | 0 | 0 | 0 | 6800 | 0 | 764608 | 510.81 | 104.1437
8562 | 12 | 0 | 0.047182 | 0.16108 | 20.2142 | 0 | 0 | 0 | 0 | 0 | 0 | 6800 | 0 | 764608 | 510.81 | 20.2142
8563 | 12 | 0 | 0 | 0.21926 | 8.9679 | 0 | 0 | 0 | 0 | 0 | 0 | 6800 | 0 | 764608 | 510.81 | 8.9679
8564 | 12 | 1 | 0 | 0.19875 | 8.1288 | 200 | 8.1288 | 180 | 188.1288 | 0 | 0 | 6600 | 188.1288 | 764796.1288 | 330.81 | 0
8565 | 12 | 1 | 0 | 0.20371 | 8.3317 | 200 | 8.3317 | 180 | 188.3317 | 0 | 0 | 6400 | 188.3317 | 764984.4605 | 150.81 | 0
8566 | 12 | 0 | 0 | 0.11255 | 4.6034 | 0 | 0 | 0 | 0 | 4.6034 | 0 | 6400 | 0 | 764984.4605 | 154.8002 | 0
8567 | 12 | 0 | 0 | 0.10601 | 4.3358 | 0 | 0 | 0 | 0 | 4.3358 | 0 | 6400 | 0 | 764984.4605 | 158.5585 | 0
8568 | 12 | 0 | 0 | 0.088403 | 3.6157 | 0 | 0 | 0 | 0 | 3.6157 | 0 | 6400 | 0 | 764984.4605 | 161.6926 | 0
8569 | 12 | 0 | 0 | 0.080097 | 3.276 | 0 | 0 | 0 | 0 | 3.276 | 0 | 6400 | 0 | 764984.4605 | 164.5322 | 0
8570 | 12 | 0 | 0 | 0.12343 | 5.0484 | 0 | 0 | 0 | 0 | 5.0484 | 0 | 6400 | 0 | 764984.4605 | 168.9081 | 0
8571 | 12 | 0 | 0 | 0.13991 | 5.7223 | 0 | 0 | 0 | 0 | 5.7223 | 0 | 6400 | 0 | 764984.4605 | 173.8682 | 0
8572 | 12 | 0 | 0 | 0.15924 | 6.513 | 0 | 0 | 0 | 0 | 6.513 | 0 | 6400 | 0 | 764984.4605 | 179.5136 | 0
8573 | 12 | 0 | 0 | 0.11034 | 4.5127 | 0 | 0 | 0 | 0 | 4.5127 | 0 | 6400 | 0 | 764984.4605 | 183.4252 | 0
8574 | 12 | 0 | 0 | 0.12722 | 5.2033 | 0 | 0 | 0 | 0 | 5.2033 | 0 | 6400 | 0 | 764984.4605 | 187.9354 | 0
8575 | 12 | 0 | 0 | 0.11559 | 4.7277 | 0 | 0 | 0 | 0 | 4.7277 | 0 | 6400 | 0 | 764984.4605 | 192.0334 | 0
8576 | 12 | 1 | 0.047298 | 0.10937 | 18.1328 | 200 | 18.1328 | 180 | 198.1328 | 0 | 0 | 6200 | 198.1328 | 765182.5933 | 12.0334 | 0
8577 | 12 | 1 | 0.3317 | 0.089773 | 99.4667 | 200 | 99.4667 | 12.0334 | 111.5001 | 0 | 0 | 6000 | 111.5001 | 765294.0934 | 0 | 0
8578 | 12 | 0 | 0.66635 | 0.11242 | 197.0401 | 0 | 0 | 0 | 0 | 180 | 17.0401 | 6000 | 17.0401 | 765311.1334 | 156.024 | 0
8579 | 12 | 0 | 0.96571 | 0.14352 | 284.7665 | 0 | 0 | 0 | 0 | 180 | 96.8666 | 6000 | 96.8666 | 765408 | 312.048 | 7.9
8580 | 12 | 0 | 1 | 0.1448 | 294.7225 | 0 | 0 | 0 | 0 | 180 | 0 | 6000 | 0 | 765408 | 468.072 | 114.7225
8581 | 12 | 0 | 1 | 0.21417 | 297.5596 | 0 | 0 | 0 | 0 | 49.3055 | 0 | 6000 | 0 | 765408 | 510.81 | 248.2541
8582 | 12 | 0 | 1 | 0.27356 | 299.9884 | 0 | 0 | 0 | 0 | 0 | 0 | 6000 | 0 | 765408 | 510.81 | 299.9884
8583 | 12 | 0 | 0.96571 | 0.21671 | 287.7601 | 0 | 0 | 0 | 0 | 0 | 0 | 6000 | 0 | 765408 | 510.81 | 287.7601
8584 | 12 | 0 | 0.66635 | 0.29249 | 204.4047 | 0 | 0 | 0 | 0 | 0 | 0 | 6000 | 0 | 765408 | 510.81 | 204.4047
8585 | 12 | 0 | 0.3317 | 0.33994 | 109.6986 | 0 | 0 | 0 | 0 | 0 | 0 | 6000 | 0 | 765408 | 510.81 | 109.6986
8586 | 12 | 0 | 0.047298 | 0.28033 | 25.1251 | 0 | 0 | 0 | 0 | 0 | 0 | 6000 | 0 | 765408 | 510.81 | 25.1251
8587 | 12 | 0 | 0 | 0.15009 | 6.1388 | 0 | 0 | 0 | 0 | 0 | 0 | 6000 | 0 | 765408 | 510.81 | 6.1388
8588 | 12 | 1 | 0 | 0.09968 | 4.0769 | 200 | 4.0769 | 180 | 184.0769 | 0 | 0 | 5800 | 184.0769 | 765592.0769 | 330.81 | 0
8589 | 12 | 1 | 0 | 0.18334 | 7.4988 | 200 | 7.4988 | 180 | 187.4988 | 0 | 0 | 5600 | 187.4988 | 765779.5757 | 150.81 | 0
8590 | 12 | 0 | 0 | 0.22945 | 9.3846 | 0 | 0 | 0 | 0 | 9.3846 | 0 | 5600 | 0 | 765779.5757 | 158.9446 | 0
8591 | 12 | 0 | 0 | 0.34266 | 14.0149 | 0 | 0 | 0 | 0 | 14.0149 | 0 | 5600 | 0 | 765779.5757 | 171.0927 | 0
8592 | 12 | 0 | 0 | 0.30177 | 12.3424 | 0 | 0 | 0 | 0 | 12.3424 | 0 | 5600 | 0 | 765779.5757 | 181.7911 | 0
8593 | 12 | 0 | 0 | 0.24531 | 10.0332 | 0 | 0 | 0 | 0 | 10.0332 | 0 | 5600 | 0 | 765779.5757 | 190.4878 | 0
8594 | 12 | 0 | 0 | 0.193 | 7.8937 | 0 | 0 | 0 | 0 | 7.8937 | 0 | 5600 | 0 | 765779.5757 | 197.3301 | 0
8595 | 12 | 0 | 0 | 0.11801 | 4.8267 | 0 | 0 | 0 | 0 | 4.8267 | 0 | 5600 | 0 | 765779.5757 | 201.5138 | 0
8596 | 12 | 0 | 0 | 0.18057 | 7.3851 | 0 | 0 | 0 | 0 | 7.3851 | 0 | 5600 | 0 | 765779.5757 | 207.9153 | 0
8597 | 12 | 0 | 0 | 0.20021 | 8.1888 | 0 | 0 | 0 | 0 | 8.1888 | 0 | 5600 | 0 | 765779.5757 | 215.0133 | 0
8598 | 12 | 0 | 0 | 0.2048 | 8.3763 | 0 | 0 | 0 | 0 | 8.3763 | 0 | 5600 | 0 | 765779.5757 | 222.2739 | 0
8599 | 12 | 0 | 0 | 0.15611 | 6.385 | 0 | 0 | 0 | 0 | 6.385 | 0 | 5600 | 0 | 765779.5757 | 227.8084 | 0
8600 | 12 | 1 | 0.049659 | 0.17541 | 21.5159 | 200 | 21.5159 | 178.4841 | 200 | 0 | 0 | 5400 | 200 | 765979.5757 | 49.3242 | 0
8601 | 12 | 1 | 0.34826 | 0.20783 | 109.0766 | 200 | 109.0766 | 49.3242 | 158.4008 | 0 | 0 | 5200 | 158.4008 | 766137.9765 | 0 | 0
8602 | 12 | 0 | 0.69961 | 0.22714 | 211.3369 | 0 | 0 | 0 | 0 | 180 | 31.3369 | 5200 | 31.3369 | 766169.3134 | 156.024 | 0
8603 | 12 | 0 | 1 | 0.18462 | 296.351 | 0 | 0 | 0 | 0 | 180 | 38.6866 | 5200 | 38.6866 | 766208 | 312.048 | 77.6645
8604 | 12 | 0 | 1 | 0.30308 | 301.1961 | 0 | 0 | 0 | 0 | 180 | 0 | 5200 | 0 | 766208 | 468.072 | 121.1961
8605 | 12 | 0 | 1 | 0.56861 | 312.0562 | 0 | 0 | 0 | 0 | 49.3055 | 0 | 5200 | 0 | 766208 | 510.81 | 262.7507
8606 | 12 | 0 | 1 | 0.69425 | 317.1949 | 0 | 0 | 0 | 0 | 0 | 0 | 5200 | 0 | 766208 | 510.81 | 317.1949
8607 | 12 | 0 | 1 | 0.78611 | 320.9518 | 0 | 0 | 0 | 0 | 0 | 0 | 5200 | 0 | 766208 | 510.81 | 320.9518
8608 | 12 | 0 | 0.69961 | 0.64677 | 228.4998 | 0 | 0 | 0 | 0 | 0 | 0 | 5200 | 0 | 766208 | 510.81 | 228.4998
8609 | 12 | 0 | 0.34826 | 0.79957 | 133.2787 | 0 | 0 | 0 | 0 | 0 | 0 | 5200 | 0 | 766208 | 510.81 | 133.2787
8610 | 12 | 0 | 0.049659 | 0.6043 | 39.0572 | 0 | 0 | 0 | 0 | 0 | 0 | 5200 | 0 | 766208 | 510.81 | 39.0572
8611 | 12 | 0 | 0 | 0.58468 | 23.9133 | 0 | 0 | 0 | 0 | 0 | 0 | 5200 | 0 | 766208 | 510.81 | 23.9133
8612 | 12 | 1 | 0 | 0.46172 | 18.8843 | 200 | 18.8843 | 180 | 198.8843 | 0 | 0 | 5000 | 198.8843 | 766406.8843 | 330.81 | 0
8613 | 12 | 1 | 0 | 0.28552 | 11.6778 | 200 | 11.6778 | 180 | 191.6778 | 0 | 0 | 4800 | 191.6778 | 766598.5621 | 150.81 | 0
8614 | 12 | 0 | 0 | 0.21743 | 8.8931 | 0 | 0 | 0 | 0 | 8.8931 | 0 | 4800 | 0 | 766598.5621 | 158.5185 | 0
8615 | 12 | 0 | 0 | 0.14197 | 5.8065 | 0 | 0 | 0 | 0 | 5.8065 | 0 | 4800 | 0 | 766598.5621 | 163.5515 | 0
8616 | 12 | 0 | 0 | 0.16521 | 6.757 | 0 | 0 | 0 | 0 | 6.757 | 0 | 4800 | 0 | 766598.5621 | 169.4085 | 0
8617 | 12 | 0 | 0 | 0.11887 | 4.862 | 0 | 0 | 0 | 0 | 4.862 | 0 | 4800 | 0 | 766598.5621 | 173.6228 | 0
8618 | 12 | 0 | 0 | 0.12855 | 5.2575 | 0 | 0 | 0 | 0 | 5.2575 | 0 | 4800 | 0 | 766598.5621 | 178.1801 | 0
8619 | 12 | 0 | 0 | 0.13989 | 5.7216 | 0 | 0 | 0 | 0 | 5.7216 | 0 | 4800 | 0 | 766598.5621 | 183.1396 | 0
8620 | 12 | 0 | 0 | 0.12337 | 5.0457 | 0 | 0 | 0 | 0 | 5.0457 | 0 | 4800 | 0 | 766598.5621 | 187.5132 | 0
8621 | 12 | 0 | 0 | 0.18207 | 7.4466 | 0 | 0 | 0 | 0 | 7.4466 | 0 | 4800 | 0 | 766598.5621 | 193.9679 | 0
8622 | 12 | 0 | 0 | 0.18023 | 7.3715 | 0 | 0 | 0 | 0 | 7.3715 | 0 | 4800 | 0 | 766598.5621 | 200.3575 | 0
8623 | 12 | 0 | 0 | 0.12593 | 5.1505 | 0 | 0 | 0 | 0 | 5.1505 | 0 | 4800 | 0 | 766598.5621 | 204.822 | 0
8624 | 12 | 1 | 0.04719 | 0.10645 | 17.9824 | 200 | 17.9824 | 180 | 197.9824 | 0 | 0 | 4600 | 197.9824 | 766796.5444 | 24.822 | 0
8625 | 12 | 1 | 0.33094 | 0.11725 | 100.3724 | 200 | 100.3724 | 24.822 | 125.1944 | 0 | 0 | 4400 | 125.1944 | 766921.7388 | 0 | 0
8626 | 12 | 0 | 0.66483 | 0.10253 | 196.1974 | 0 | 0 | 0 | 0 | 180 | 16.1974 | 4400 | 16.1974 | 766937.9362 | 156.024 | 0
8627 | 12 | 0 | 0.96351 | 0.08744 | 281.8386 | 0 | 0 | 0 | 0 | 180 | 70.0638 | 4400 | 70.0638 | 767008 | 312.048 | 31.7748
8628 | 12 | 0 | 1 | 0.12708 | 293.9977 | 0 | 0 | 0 | 0 | 180 | 0 | 4400 | 0 | 767008 | 468.072 | 113.9977
8629 | 12 | 0 | 1 | 0.11587 | 293.5392 | 0 | 0 | 0 | 0 | 49.3055 | 0 | 4400 | 0 | 767008 | 510.81 | 244.2337
8630 | 12 | 0 | 1 | 0.13821 | 294.4527 | 0 | 0 | 0 | 0 | 0 | 0 | 4400 | 0 | 767008 | 510.81 | 294.4527
8631 | 12 | 0 | 0.96351 | 0.14209 | 284.0739 | 0 | 0 | 0 | 0 | 0 | 0 | 4400 | 0 | 767008 | 510.81 | 284.0739
8632 | 12 | 0 | 0.66483 | 0.13133 | 197.3753 | 0 | 0 | 0 | 0 | 0 | 0 | 4400 | 0 | 767008 | 510.81 | 197.3753
8633 | 12 | 0 | 0.33094 | 0.13531 | 101.1112 | 0 | 0 | 0 | 0 | 0 | 0 | 4400 | 0 | 767008 | 510.81 | 101.1112
8634 | 12 | 0 | 0.04719 | 0.1844 | 21.1703 | 0 | 0 | 0 | 0 | 0 | 0 | 4400 | 0 | 767008 | 510.81 | 21.1703
8635 | 12 | 0 | 0 | 0.17471 | 7.1458 | 0 | 0 | 0 | 0 | 0 | 0 | 4400 | 0 | 767008 | 510.81 | 7.1458
8636 | 12 | 1 | 0 | 0.177 | 7.2392 | 200 | 7.2392 | 180 | 187.2392 | 0 | 0 | 4200 | 187.2392 | 767195.2392 | 330.81 | 0
8637 | 12 | 1 | 0 | 0.20231 | 8.2743 | 200 | 8.2743 | 180 | 188.2743 | 0 | 0 | 4000 | 188.2743 | 767383.5135 | 150.81 | 0
8638 | 12 | 0 | 0 | 0.17422 | 7.1257 | 0 | 0 | 0 | 0 | 7.1257 | 0 | 4000 | 0 | 767383.5135 | 156.9866 | 0
8639 | 12 | 0 | 0 | 0.1675 | 6.8507 | 0 | 0 | 0 | 0 | 6.8507 | 0 | 4000 | 0 | 767383.5135 | 162.9247 | 0
8640 | 12 | 0 | 0 | 0.30304 | 12.3944 | 0 | 0 | 0 | 0 | 12.3944 | 0 | 4000 | 0 | 767383.5135 | 173.6682 | 0
8641 | 12 | 0 | 0 | 0.24112 | 9.8618 | 0 | 0 | 0 | 0 | 9.8618 | 0 | 4000 | 0 | 767383.5135 | 182.2164 | 0
8642 | 12 | 0 | 0 | 0.28027 | 11.463 | 0 | 0 | 0 | 0 | 11.463 | 0 | 4000 | 0 | 767383.5135 | 192.1525 | 0
8643 | 12 | 0 | 0 | 0.29697 | 12.1462 | 0 | 0 | 0 | 0 | 12.1462 | 0 | 4000 | 0 | 767383.5135 | 202.6808 | 0
8644 | 12 | 0 | 0 | 0.40456 | 16.5467 | 0 | 0 | 0 | 0 | 16.5467 | 0 | 4000 | 0 | 767383.5135 | 217.0235 | 0
8645 | 12 | 0 | 0 | 0.22659 | 9.2676 | 0 | 0 | 0 | 0 | 9.2676 | 0 | 4000 | 0 | 767383.5135 | 225.0566 | 0
8646 | 12 | 0 | 0 | 0.1898 | 7.7628 | 0 | 0 | 0 | 0 | 7.7628 | 0 | 4000 | 0 | 767383.5135 | 231.7854 | 0
8647 | 12 | 0 | 0 | 0.25191 | 10.3032 | 0 | 0 | 0 | 0 | 10.3032 | 0 | 4000 | 0 | 767383.5135 | 240.7162 | 0
8648 | 12 | 1 | 0.050948 | 0.32499 | 28.0059 | 200 | 28.0059 | 171.9941 | 200 | 0 | 0 | 3800 | 200 | 767583.5135 | 68.7221 | 0
8649 | 12 | 1 | 0.3573 | 0.44539 | 121.4046 | 200 | 121.4046 | 68.7221 | 190.1267 | 0 | 0 | 3600 | 190.1267 | 767773.6402 | 0 | 0
8650 | 12 | 0 | 0.71778 | 0.39405 | 223.4102 | 0 | 0 | 0 | 0 | 180 | 34.3598 | 3600 | 34.3598 | 767808 | 156.024 | 9.0504
8651 | 12 | 0 | 1 | 0.36091 | 303.5613 | 0 | 0 | 0 | 0 | 180 | 0 | 3600 | 0 | 767808 | 312.048 | 123.5613
8652 | 12 | 0 | 1 | 0.32468 | 302.0794 | 0 | 0 | 0 | 0 | 180 | 0 | 3600 | 0 | 767808 | 468.072 | 122.0794
8653 | 12 | 0 | 1 | 0.44458 | 306.9833 | 0 | 0 | 0 | 0 | 49.3055 | 0 | 3600 | 0 | 767808 | 510.81 | 257.6778
8654 | 12 | 0 | 1 | 0.43339 | 306.5258 | 0 | 0 | 0 | 0 | 0 | 0 | 3600 | 0 | 767808 | 510.81 | 306.5258
8655 | 12 | 0 | 1 | 0.33848 | 302.6437 | 0 | 0 | 0 | 0 | 0 | 0 | 3600 | 0 | 767808 | 510.81 | 302.6437
8656 | 12 | 0 | 0.71778 | 0.2452 | 217.3225 | 0 | 0 | 0 | 0 | 0 | 0 | 3600 | 0 | 767808 | 510.81 | 217.3225
8657 | 12 | 0 | 0.3573 | 0.37716 | 118.6138 | 0 | 0 | 0 | 0 | 0 | 0 | 3600 | 0 | 767808 | 510.81 | 118.6138
8658 | 12 | 0 | 0.050948 | 0.60783 | 39.5742 | 0 | 0 | 0 | 0 | 0 | 0 | 3600 | 0 | 767808 | 510.81 | 39.5742
8659 | 12 | 0 | 0 | 0.46564 | 19.0445 | 0 | 0 | 0 | 0 | 0 | 0 | 3600 | 0 | 767808 | 510.81 | 19.0445
8660 | 12 | 1 | 0 | 0.48796 | 19.9574 | 200 | 19.9574 | 180 | 199.9574 | 0 | 0 | 3400 | 199.9574 | 768007.9574 | 330.81 | 0
8661 | 12 | 1 | 0 | 0.40214 | 16.4475 | 200 | 16.4475 | 180 | 196.4475 | 0 | 0 | 3200 | 196.4475 | 768204.4048 | 150.81 | 0
8662 | 12 | 0 | 0 | 0.3513 | 14.368 | 0 | 0 | 0 | 0 | 14.368 | 0 | 3200 | 0 | 768204.4048 | 163.2642 | 0
8663 | 12 | 0 | 0 | 0.25943 | 10.6107 | 0 | 0 | 0 | 0 | 10.6107 | 0 | 3200 | 0 | 768204.4048 | 172.4616 | 0
8664 | 12 | 0 | 0 | 0.30845 | 12.6156 | 0 | 0 | 0 | 0 | 12.6156 | 0 | 3200 | 0 | 768204.4048 | 183.3968 | 0
8665 | 12 | 0 | 0 | 0.19444 | 7.9526 | 0 | 0 | 0 | 0 | 7.9526 | 0 | 3200 | 0 | 768204.4048 | 190.2902 | 0
8666 | 12 | 0 | 0 | 0.17387 | 7.1113 | 0 | 0 | 0 | 0 | 7.1113 | 0 | 3200 | 0 | 768204.4048 | 196.4542 | 0
8667 | 12 | 0 | 0 | 0.18154 | 7.4251 | 0 | 0 | 0 | 0 | 7.4251 | 0 | 3200 | 0 | 768204.4048 | 202.8904 | 0
8668 | 12 | 0 | 0 | 0.17173 | 7.0236 | 0 | 0 | 0 | 0 | 7.0236 | 0 | 3200 | 0 | 768204.4048 | 208.9784 | 0
8669 | 12 | 0 | 0 | 0.18614 | 7.613 | 0 | 0 | 0 | 0 | 7.613 | 0 | 3200 | 0 | 768204.4048 | 215.5774 | 0
8670 | 12 | 0 | 0 | 0.25829 | 10.564 | 0 | 0 | 0 | 0 | 10.564 | 0 | 3200 | 0 | 768204.4048 | 224.7342 | 0
8671 | 12 | 0 | 0 | 0.40399 | 16.5233 | 0 | 0 | 0 | 0 | 16.5233 | 0 | 3200 | 0 | 768204.4048 | 239.0566 | 0
8672 | 12 | 1 | 0.048409 | 0.51305 | 34.9642 | 200 | 34.9642 | 165.0358 | 200 | 0 | 0 | 3000 | 200 | 768404.4048 | 74.0209 | 0
8673 | 12 | 1 | 0.33949 | 0.45846 | 116.7953 | 200 | 116.7953 | 74.0209 | 190.8161 | 0 | 0 | 2800 | 190.8161 | 768595.221 | 0 | 0
8674 | 12 | 0 | 0.682 | 0.59146 | 221.1519 | 0 | 0 | 0 | 0 | 180 | 12.779 | 2800 | 12.779 | 768608 | 156.024 | 28.3729
8675 | 12 | 0 | 0.98839 | 0.64711 | 311.9128 | 0 | 0 | 0 | 0 | 180 | 0 | 2800 | 0 | 768608 | 312.048 | 131.9128
8676 | 12 | 0 | 1 | 0.35403 | 303.2799 | 0 | 0 | 0 | 0 | 180 | 0 | 2800 | 0 | 768608 | 468.072 | 123.2799
8677 | 12 | 0 | 1 | 0.24984 | 299.0184 | 0 | 0 | 0 | 0 | 49.3055 | 0 | 2800 | 0 | 768608 | 510.81 | 249.7129
8678 | 12 | 0 | 1 | 0.14531 | 294.7433 | 0 | 0 | 0 | 0 | 0 | 0 | 2800 | 0 | 768608 | 510.81 | 294.7433
8679 | 12 | 0 | 0.98839 | 0.17979 | 292.7995 | 0 | 0 | 0 | 0 | 0 | 0 | 2800 | 0 | 768608 | 510.81 | 292.7995
8680 | 12 | 0 | 0.682 | 0.13472 | 202.4711 | 0 | 0 | 0 | 0 | 0 | 0 | 2800 | 0 | 768608 | 510.81 | 202.4711
8681 | 12 | 0 | 0.33949 | 0.12603 | 103.199 | 0 | 0 | 0 | 0 | 0 | 0 | 2800 | 0 | 768608 | 510.81 | 103.199
8682 | 12 | 0 | 0.048409 | 0.10127 | 18.1224 | 0 | 0 | 0 | 0 | 0 | 0 | 2800 | 0 | 768608 | 510.81 | 18.1224
8683 | 12 | 0 | 0 | 0.088117 | 3.604 | 0 | 0 | 0 | 0 | 0 | 0 | 2800 | 0 | 768608 | 510.81 | 3.604
8684 | 12 | 1 | 0 | 0.074527 | 3.0482 | 200 | 3.0482 | 180 | 183.0482 | 0 | 0 | 2600 | 183.0482 | 768791.0482 | 330.81 | 0
8685 | 12 | 1 | 0 | 0.09577 | 3.917 | 200 | 3.917 | 180 | 183.917 | 0 | 0 | 2400 | 183.917 | 768974.9651 | 150.81 | 0
8686 | 12 | 0 | 0 | 0.089516 | 3.6612 | 0 | 0 | 0 | 0 | 3.6612 | 0 | 2400 | 0 | 768974.9651 | 153.9835 | 0
8687 | 12 | 0 | 0 | 0.11774 | 4.8156 | 0 | 0 | 0 | 0 | 4.8156 | 0 | 2400 | 0 | 768974.9651 | 158.1577 | 0
8688 | 12 | 0 | 0 | 0.11252 | 4.6019 | 0 | 0 | 0 | 0 | 4.6019 | 0 | 2400 | 0 | 768974.9651 | 162.1467 | 0
8689 | 12 | 0 | 0 | 0.11683 | 4.7784 | 0 | 0 | 0 | 0 | 4.7784 | 0 | 2400 | 0 | 768974.9651 | 166.2886 | 0
8690 | 12 | 0 | 0 | 0.15321 | 6.2665 | 0 | 0 | 0 | 0 | 6.2665 | 0 | 2400 | 0 | 768974.9651 | 171.7204 | 0
8691 | 12 | 0 | 0 | 0.20074 | 8.2103 | 0 | 0 | 0 | 0 | 8.2103 | 0 | 2400 | 0 | 768974.9651 | 178.8371 | 0
8692 | 12 | 0 | 0 | 0.29053 | 11.8828 | 0 | 0 | 0 | 0 | 11.8828 | 0 | 2400 | 0 | 768974.9651 | 189.137 | 0
8693 | 12 | 0 | 0 | 0.21358 | 8.7356 | 0 | 0 | 0 | 0 | 8.7356 | 0 | 2400 | 0 | 768974.9651 | 196.709 | 0
8694 | 12 | 0 | 0 | 0.18831 | 7.702 | 0 | 0 | 0 | 0 | 7.702 | 0 | 2400 | 0 | 768974.9651 | 203.3852 | 0
8695 | 12 | 0 | 0 | 0.13836 | 5.659 | 0 | 0 | 0 | 0 | 5.659 | 0 | 2400 | 0 | 768974.9651 | 208.2904 | 0
8696 | 12 | 1 | 0.050409 | 0.1145 | 19.2413 | 200 | 19.2413 | 180 | 199.2413 | 0 | 0 | 2200 | 199.2413 | 769174.2065 | 28.2904 | 0
8697 | 12 | 1 | 0.35352 | 0.11737 | 106.8961 | 200 | 106.8961 | 28.2904 | 135.1865 | 0 | 0 | 2000 | 135.1865 | 769309.3929 | 0 | 0
8698 | 12 | 0 | 0.71018 | 0.15257 | 211.3391 | 0 | 0 | 0 | 0 | 180 | 31.3391 | 2000 | 31.3391 | 769340.732 | 156.024 | 0
8699 | 12 | 0 | 1 | 0.14379 | 294.6811 | 0 | 0 | 0 | 0 | 180 | 67.268 | 2000 | 67.268 | 769408 | 312.048 | 47.4131
8700 | 12 | 0 | 1 | 0.15339 | 295.0736 | 0 | 0 | 0 | 0 | 180 | 0 | 2000 | 0 | 769408 | 468.072 | 115.0736
8701 | 12 | 0 | 1 | 0.19476 | 296.7656 | 0 | 0 | 0 | 0 | 49.3055 | 0 | 2000 | 0 | 769408 | 510.81 | 247.4602
8702 | 12 | 0 | 1 | 0.24349 | 298.7585 | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 0 | 769408 | 510.81 | 298.7585
8703 | 12 | 0 | 1 | 0.27309 | 299.9695 | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 0 | 769408 | 510.81 | 299.9695
8704 | 12 | 0 | 0.71018 | 0.28055 | 216.5734 | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 0 | 769408 | 510.81 | 216.5734
8705 | 12 | 0 | 0.35352 | 0.2246 | 111.2819 | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 0 | 769408 | 510.81 | 111.2819
8706 | 12 | 0 | 0.050409 | 0.12801 | 19.7939 | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 0 | 769408 | 510.81 | 19.7939
8707 | 12 | 0 | 0 | 0.19898 | 8.1384 | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 0 | 769408 | 510.81 | 8.1384
8708 | 12 | 1 | 0 | 0.16925 | 6.9221 | 200 | 6.9221 | 180 | 186.9221 | 0 | 0 | 1800 | 186.9221 | 769594.9221 | 330.81 | 0
8709 | 12 | 1 | 0 | 0.24308 | 9.9422 | 200 | 9.9422 | 180 | 189.9422 | 0 | 0 | 1600 | 189.9422 | 769784.8643 | 150.81 | 0
8710 | 12 | 0 | 0 | 0.27155 | 11.1065 | 0 | 0 | 0 | 0 | 11.1065 | 0 | 1600 | 0 | 769784.8643 | 160.4371 | 0
8711 | 12 | 0 | 0 | 0.24222 | 9.9067 | 0 | 0 | 0 | 0 | 9.9067 | 0 | 1600 | 0 | 769784.8643 | 169.0242 | 0
8712 | 12 | 0 | 0 | 0.26469 | 10.8259 | 0 | 0 | 0 | 0 | 10.8259 | 0 | 1600 | 0 | 769784.8643 | 178.4081 | 0
8713 | 12 | 0 | 0 | 0.23332 | 9.5429 | 0 | 0 | 0 | 0 | 9.5429 | 0 | 1600 | 0 | 769784.8643 | 186.6799 | 0
8714 | 12 | 0 | 0 | 0.28435 | 11.6299 | 0 | 0 | 0 | 0 | 11.6299 | 0 | 1600 | 0 | 769784.8643 | 196.7607 | 0
8715 | 12 | 0 | 0 | 0.33746 | 13.8022 | 0 | 0 | 0 | 0 | 13.8022 | 0 | 1600 | 0 | 769784.8643 | 208.7245 | 0
8716 | 12 | 0 | 0 | 0.22421 | 9.1704 | 0 | 0 | 0 | 0 | 9.1704 | 0 | 1600 | 0 | 769784.8643 | 216.6734 | 0
8717 | 12 | 0 | 0 | 0.22037 | 9.0131 | 0 | 0 | 0 | 0 | 9.0131 | 0 | 1600 | 0 | 769784.8643 | 224.4859 | 0
8718 | 12 | 0 | 0 | 0.12846 | 5.2541 | 0 | 0 | 0 | 0 | 5.2541 | 0 | 1600 | 0 | 769784.8643 | 229.0402 | 0
8719 | 12 | 0 | 0 | 0.086746 | 3.5479 | 0 | 0 | 0 | 0 | 3.5479 | 0 | 1600 | 0 | 769784.8643 | 232.1155 | 0
8720 | 12 | 1 | 0.049427 | 0.098033 | 18.2841 | 200 | 18.2841 | 180 | 198.2841 | 0 | 0 | 1400 | 198.2841 | 769983.1484 | 52.1155 | 0
8721 | 12 | 1 | 0.34663 | 0.15279 | 106.3562 | 200 | 106.3562 | 52.1155 | 158.4717 | 0 | 0 | 1200 | 158.4717 | 770141.6201 | 0 | 0
8722 | 12 | 0 | 0.69635 | 0.15406 | 207.4059 | 0 | 0 | 0 | 0 | 180 | 27.4059 | 1200 | 27.4059 | 770169.026 | 156.024 | 0
8723 | 12 | 0 | 1 | 0.14887 | 294.8887 | 0 | 0 | 0 | 0 | 180 | 38.974 | 1200 | 38.974 | 770208 | 312.048 | 75.9148
8724 | 12 | 0 | 1 | 0.20443 | 297.1612 | 0 | 0 | 0 | 0 | 180 | 0 | 1200 | 0 | 770208 | 468.072 | 117.1612
8725 | 12 | 0 | 1 | 0.17883 | 296.1139 | 0 | 0 | 0 | 0 | 49.3055 | 0 | 1200 | 0 | 770208 | 510.81 | 246.8085
8726 | 12 | 0 | 1 | 0.25997 | 299.4327 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 0 | 770208 | 510.81 | 299.4327
8727 | 12 | 0 | 1 | 0.34544 | 302.9286 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 0 | 770208 | 510.81 | 302.9286
8728 | 12 | 0 | 0.69635 | 0.24843 | 211.2654 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 0 | 770208 | 510.81 | 211.2654
8729 | 12 | 0 | 0.34663 | 0.2235 | 109.2483 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 0 | 770208 | 510.81 | 109.2483
8730 | 12 | 0 | 0.049427 | 0.21833 | 23.2043 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 0 | 770208 | 510.81 | 23.2043
8731 | 12 | 0 | 0 | 0.21695 | 8.8733 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 0 | 770208 | 510.81 | 8.8733
8732 | 12 | 1 | 0 | 0.2398 | 9.808 | 200 | 9.808 | 180 | 189.808 | 0 | 0 | 1000 | 189.808 | 770397.808 | 330.81 | 0
8733 | 12 | 1 | 0 | 0.16043 | 6.5618 | 200 | 6.5618 | 180 | 186.5618 | 0 | 0 | 800 | 186.5618 | 770584.3698 | 150.81 | 0
8734 | 12 | 0 | 0 | 0.19434 | 7.9486 | 0 | 0 | 0 | 0 | 7.9486 | 0 | 800 | 0 | 770584.3698 | 157.6999 | 0
8735 | 12 | 0 | 0 | 0.12651 | 5.1743 | 0 | 0 | 0 | 0 | 5.1743 | 0 | 800 | 0 | 770584.3698 | 162.185 | 0
8736 | 12 | 0 | 0 | 0.10202 | 4.1726 | 0 | 0 | 0 | 0 | 4.1726 | 0 | 800 | 0 | 770584.3698 | 165.8017 | 0
8737 | 12 | 0 | 0 | 0.15772 | 6.4508 | 0 | 0 | 0 | 0 | 6.4508 | 0 | 800 | 0 | 770584.3698 | 171.3933 | 0
8738 | 12 | 0 | 0 | 0.15724 | 6.4313 | 0 | 0 | 0 | 0 | 6.4313 | 0 | 800 | 0 | 770584.3698 | 176.9679 | 0
8739 | 12 | 0 | 0 | 0.16304 | 6.6683 | 0 | 0 | 0 | 0 | 6.6683 | 0 | 800 | 0 | 770584.3698 | 182.748 | 0
8740 | 12 | 0 | 0 | 0.13335 | 5.4542 | 0 | 0 | 0 | 0 | 5.4542 | 0 | 800 | 0 | 770584.3698 | 187.4757 | 0
8741 | 12 | 0 | 0 | 0.10872 | 4.4468 | 0 | 0 | 0 | 0 | 4.4468 | 0 | 800 | 0 | 770584.3698 | 191.3302 | 0
8742 | 12 | 0 | 0 | 0.077065 | 3.152 | 0 | 0 | 0 | 0 | 3.152 | 0 | 800 | 0 | 770584.3698 | 194.0623 | 0
8743 | 12 | 0 | 0 | 0.12951 | 5.2968 | 0 | 0 | 0 | 0 | 5.2968 | 0 | 800 | 0 | 770584.3698 | 198.6535 | 0
8744 | 12 | 1 | 0.048842 | 0.14157 | 19.8959 | 200 | 19.8959 | 180 | 199.8959 | 0 | 0 | 600 | 199.8959 | 770784.2657 | 18.6535 | 0
8745 | 12 | 1 | 0.34253 | 0.178 | 106.2022 | 200 | 106.2022 | 18.6535 | 124.8558 | 0 | 0 | 400 | 124.8558 | 770909.1215 | 0 | 0
8746 | 12 | 0 | 0.6881 | 0.14668 | 204.7226 | 0 | 0 | 0 | 0 | 180 | 24.7226 | 400 | 24.7226 | 770933.8441 | 156.024 | 0
8747 | 12 | 0 | 0.99723 | 0.22571 | 297.232 | 0 | 0 | 0 | 0 | 180 | 74.1559 | 400 | 74.1559 | 771008 | 312.048 | 43.0761
8748 | 12 | 0 | 1 | 0.40257 | 305.2652 | 0 | 0 | 0 | 0 | 180 | 0 | 400 | 0 | 771008 | 468.072 | 125.2652
8749 | 12 | 0 | 1 | 0.57929 | 312.4928 | 0 | 0 | 0 | 0 | 49.3055 | 0 | 400 | 0 | 771008 | 510.81 | 263.1873
8750 | 12 | 0 | 1 | 0.34419 | 302.8772 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 771008 | 510.81 | 302.8772
8751 | 12 | 0 | 0.99723 | 0.38695 | 303.8269 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 771008 | 510.81 | 303.8269
8752 | 12 | 0 | 0.6881 | 0.26571 | 209.5912 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 771008 | 510.81 | 209.5912
8753 | 12 | 0 | 0.34253 | 0.29403 | 110.9477 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 771008 | 510.81 | 110.9477
8754 | 12 | 0 | 0.048842 | 0.32129 | 27.2465 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 771008 | 510.81 | 27.2465
8755 | 12 | 0 | 0 | 0.45891 | 18.7695 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 771008 | 510.81 | 18.7695
8756 | 12 | 1 | 0 | 0.45656 | 18.6734 | 200 | 18.6734 | 180 | 198.6734 | 0 | 0 | 200 | 198.6734 | 771206.6734 | 330.81 | 0
8757 | 12 | 1 | 0 | 0.72592 | 29.69 | 200 | 29.69 | 170.31 | 200 | 0 | 0 | 0 | 200 | 771406.6734 | 160.5 | 0
8758 | 12 | 0 | 0 | 0.73267 | 29.9661 | 0 | 0 | 0 | 0 | 29.9661 | 0 | 0 | 0 | 771406.6734 | 186.4746 | 0
8759 | 12 | 0 | 0 | 0.90682 | 37.089 | 0 | 0 | 0 | 0 | 37.089 | 0 | 0 | 0 | 771406.6734 | 218.6233 | 0
8760 | 12 | 0 | 0 | 0.85764 | 35.0775 | 0 | 0 | 0 | 0 | 35.0775 | 0 | 0 | 0 | 771406.6734 | 249.0285 | 0