PROJECT CONFIGURATION

| Project | Site Name | Total Capacity | Connectivity | GSS |
| --- | --- | --- | --- | --- |
| Wind | Barmer, Rajasthan. | 31.5 MW | 30 MW | Fatehgarh 4S2 |
| Solar | Bikaner, Rajasthan | 240 MW/360 MWp/ 1.5 DC TO AC | 150 MW | Bikaner III |
| BESS |  | 540 MWh/135 MW/ C/4 |  |  |
| Solar | Bikaner, Rajasthan. | 60 MW/90 MWp/ 1.5 DC TO AC | 100 MW | Bikaner II |
| BESS |  | 200 MWh/50 MW/ C/4 |  |  |

- WTG Co-Ordinates

| Turbine | Easting (m) | Northing (m) | Elevation (m) |
| --- | --- | --- | --- |
|  | 705571 | 2893056 | 294 |
|  | 705987 | 2892654 | 299 |
|  | 706311 | 2892162 | 297 |
|  | 706670 | 2891708 | 295 |
|  | 707837 | 2891271 | 295 |
|  | 708468 | 2889046 | 286 |
|  | 707760 | 2889149 | 290 |
|  | 707460 | 2889663 | 290 |
|  | 708568 | 2891165 | 287 |
|  | 708976 | 2890775 | 282 |

- WTG Configuration:

| 1 | WTG Model |  | S144_3.15MW |
| --- | --- | --- | --- |
| 2 | Rotor Diameter (m) |  | 144 |
| 3 | Hub Height (m) |  | 140 |
| 4 | WTG Capacity (MW) |  | 3.15 |
| 5 | No of WTGs |  | 10 |
| 6 | Project Capacity (MW) |  | 31.50 |
| 7 | Free LT WS (m/s) of wind farm |  | 7.34 |
| 8 | Losses/Availability Considered |  |  |
| 8.1 | Wake loss | Array Efficiency | 84.30% |
| 8.2 | Other Loss Efficiency | Machine Availability* | 97.50% |
|  |  | BOP Availability | 99.50% |
|  |  | Grid Availability (CTU) | 99.50% |
|  |  | Transmission Efficiency | 97.00% |
|  |  | Wind farm self-Consumption | 99.50% |
|  |  | Turbine Performance | 98.00% |
|  |  | Turbine Degradation | 99.00% |
|  |  | Curtailment | 100.00% |
|  |  | Environmental | 99.30% |
|  |  | Additional future wake loss | 100.00% |
| 8.3 | Total Loss without wake |  | 10.25% |
| 8.4 | Total Loss with wake |  | 24.35% |
| 9 | Uncertainty |  | 9.47% |

- Solar Specification

| Particulars | Details |
| --- | --- |
| Location | Bikaner II |
| Project Capacity | 90MWp/ 60MWac |
| DC:AC Ratio | 1.50 |
| Location | District Bikaner, Rajasthan |
| Latitude & Longitude | 28.16°N, 72.96°E |
| Altitude | 178 m |
| Location | Bikaner III |
| Project Capacity | 360MWp/ 240MWac |
| DC:AC Ratio | 1.50 |
| Location | Bikaner, Rajasthan. |
| Latitude & Longitude | 28.38°N, 73.16°E |
| Altitude | 191 m |
| Technology |  |
| SPV Technology | TOPCon Bifacial |
| Solar PV Module Make | Waaree Energies |
| PV Module Rating | 605 Wp |
| Inverter Manufacturer | Sungrow |
| Inverter Nominal Power | 4400 KWac |

- BESS Specification

| Sr. | Input Parameters | Unit | Value |
| --- | --- | --- | --- |
| 1 | BESS Name plate Capacity | MWh/MW | - Name Plate – 600 MWh - DC Usable– 560 MWh - PoI- 500 MWh |
|  | BESS Name plate Capacity | MWh/MW | - Name Plate – 234.82 MWh - DC Usable– 217.94 MWh - PoI- 200 MWh/50MW |
| 2 | No. of Container |  | 58 |
| 3 | Each container capacity (MWh) |  | 10.0505 |
| 4 | Charge Rate | CPCV | 0.25 |
| 5 | Discharge Rate | CP | 0.25 |
| 6 | Cycle per Day | Nos | 1 |
| 7 | DOD1 of usable capacity |  | 100% |
| 8 | Battery Augmentation | Year | 100% 11th year |

| Yr | DC Usable | SOH | RTE |
| --- | --- | --- | --- |
| 1 | 217.94 | 100.000% | 86.68% |
| 2 | 208.46 | 95.650% | 86.68% |
| 3 | 203.60 | 93.420% | 86.12% |
| 4 | 199.44 | 91.510% | 86.12% |
| 5 | 195.71 | 89.800% | 86.12% |
| 6 | 192.24 | 88.210% | 86.12% |
| 7 | 189.02 | 86.730% | 85.57% |
| 8 | 185.97 | 85.330% | 85.57% |
| 9 | 183.07 | 84.000% | 85.57% |
| 10 | 180.28 | 82.720% | 85.57% |
| 11 | 217.94 | 100.000% | 86.68% |
| 12 | 208.46 | 95.650% | 86.68% |
| 13 | 203.60 | 93.420% | 86.12% |
| 14 | 199.44 | 91.510% | 86.12% |
| 15 | 195.71 | 89.800% | 86.12% |
| 16 | 192.24 | 88.210% | 86.12% |
| 17 | 189.02 | 86.730% | 85.57% |
| 18 | 185.97 | 85.330% | 85.57% |
| 19 | 183.07 | 84.000% | 85.57% |
| 20 | 180.28 | 82.720% | 85.57% |